## BuildingSummary
Building Summary Supermarket pre-1980 construction
|  | Value | Data Source
Program
| Building Name | Benchmark Super Market
| Available Fuel Types | gas, electricity
| Principal Building Activity | Food Sales
Form
| Total Floor Area (m2) | 4181 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 1.5
| Number of Floors | 1
| Window Fraction (Window to Wall Ratio) | South: 0.362 East: 0.00 North: 0.00 West: 0.00 Total: 0.109
Skylight/TDD Percentage
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | Office, DryStorage, Deli, Sales, Produce, Bakery
| Floor to Ceiling Height (m) | 6.1
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Mass wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1609.58
| Net Dimensions - Total Area (m2) | 1434.88
| Wall to Skin Ratio | 0.28
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 4181
| Net Dimensions - Total Area (m2) | 4181
| Roof to Skin Ratio | 0.72
Window
| Dimensions - Total Area (m2) | South: 174.7 East: 0.00 North: 0.00 West: 0.00 Total: 174.7
| Operable area (m2) | 0
Skylights/TDD
Dimensions - Total Area (m2)
Operable area (m2)
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab-on-grade
| Dimensions - Total Area (m2) | 4181
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 46.47
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.93 | See Benchmark Technical Report
HVAC
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | Unitary DX | 2003 CBECS
| Fan Control | Constant volume | 2003 CBECS
Service Water Heating
| SWH Type | N/A
| Fuel | N/A
| Thermal Efficiency (%) | N/A
| Temperature Setpoint (ºC ) | N/A
| Water Consumption (m3 ) | N/A

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Office | Yes | 1 | 88.84 | 541.72 | 6.0977 | 115.0801 | 0 | 18.5806 | 4.7813 | 21.3644 | 8.0729 |  |  | 10 |  | 47.8132 |  | 1.5364
DryStorage | Yes | 1 | 621.89 | 3792.03 | 6.0976 | 477.2404 | 0 | 27.8709 | 22.3132 | 11.9085 | 8.0729 |  |  |  | 0.75 | 466.4175 |  | 1.183
Deli | Yes | 1 | 224.72 | 1370.24 | 6.0975 | 138.4301 | 0 | 11.6129 | 19.3509 | 29.9486 | 53.8195 | 26.9097 | 18.927 |  | 1.5 | 337.08 | 1415.841 | 1.0817
Sales | Yes | 1 | 2324.94 | 14176.6 | 6.0976 | 323.5203 | 174.7002 | 11.6129 | 200.2034 | 29.9486 | 5.3819 |  |  |  | 1.5 | 3487.41 |  | 0.76248
Produce | Yes | 1 | 711.36 | 4337.61 | 6.0976 | 366.1803 | 0 | 11.6129 | 61.2561 | 29.9486 | 5.3819 |  |  |  | 1.5 | 1067.04 |  | 1.0139
Bakery | Yes | 1 | 209.04 | 1274.65 | 6.0976 | 189.1302 | 0 | 11.6129 | 18.0007 | 29.9486 | 53.8195 | 26.9097 | 18.927 |  | 1.5 | 313.56 | 353.9603 | 1.2749
Total Conditioned Zones |  |  | 4180.79 | 25492.85 |  | 1609.5815 | 174.7002 |  | 325.9056 | [6 empty] | 5719.3207 | 1769.8013
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric
Exterior walls
| Construction Type | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall
| R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
| SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
| Visible transmittance | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade
| R-value (m2·K / W) | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC:1_COOLC DXCOIL | 12.6185 | 15.5909 | 11.9495 | 17.7423 | 8.9362 | 12.6649 | 9.0959 | 20.0593 | 15.2987 | 11.915 | 25.754 | 18.992 | 28.3995 | 21.8346 | 28.9088 | 27.5018
| PSZ-AC:2_COOLC DXCOIL | 63.5493 | 89.4259 | 69.2065 | 104.9118 | 52.9926 | 74.775 | 53.0336 | 115.1212 | 81.2934 | 68.9074 | 144.4971 | 109.7654 | 160.4994 | 115.1149 | 171.7379 | 146.5394
| PSZ-AC:3_COOLC DXCOIL | 56.6448 | 62.983 | 64.6187 | 63.4605 | 55.4678 | 63.7674 | 37.908 | 58.3592 | 59.2327 | 46.3862 | 53.537 | 55.6906 | 54.548 | 39.2268 | 41.1496 | 49.6249
| PSZ-AC:4_COOLC DXCOIL | 173.995 | 260.5745 | 252.1055 | 324.2034 | 209.5274 | 299.6237 | 190.3545 | 343.2696 | 354.2772 | 267.7259 | 407.8273 | 404.9059 | 446.5259 | 323.3556 | 477.0681 | 386.9396
| PSZ-AC:5_COOLC DXCOIL | 57.5905 | 91.9205 | 80.6357 | 108.8149 | 60.0417 | 101.6314 | 50.8953 | 115.8451 | 103.8543 | 64.5076 | 144.4504 | 100.7091 | 160.0379 | 115.0806 | 171.4155 | 146.0071
| PSZ-AC:6_COOLC DXCOIL | 54.241 | 55.0739 | 51.4547 | 51.6447 | 39.508 | 44.9831 | 30.2609 | 50.1251 | 42.5846 | 35.4093 | 37.4569 | 40.1136 | 41.1426 | 42.0402 | 41.7712 | 53.2928
Heating (kW)
| PSZ-AC:1_HEATC | 13.5876 | 17.2807 | 14.6775 | 20.2606 | 11.7997 | 16.9143 | 13.7919 | 22.2648 | 19.1151 | 17.9025 | 27.5078 | 23.8067 | 30.3638 | 29.0527 | 31.7011 | 41.692
| PSZ-AC:2_HEATC | 68.1151 | 97.0301 | 80.1274 | 113.3758 | 66.7805 | 94.2749 | 79.4333 | 125.8873 | 107.7027 | 101.4017 | 155.3141 | 133.8576 | 171.6459 | 163.9383 | 179.6821 | 238.0172
| PSZ-AC:3_HEATC | 88.3145 | 129.6324 | 112.2107 | 140.9003 | 89.9421 | 119.7047 | 85.4178 | 144.239 | 124.7684 | 110.1137 | 154.5778 | 139.5827 | 170.2077 | 167.3185 | 186.4373 | 294.4344
| PSZ-AC:4_HEATC | 215.8631 | 343.4815 | 297.6171 | 404.3137 | 253.8406 | 344.8531 | 295.0315 | 450.5333 | 389.2323 | 373.8712 | 541.0633 | 469.1376 | 593.8021 | 566.3643 | 620.2887 | 798.1824
| PSZ-AC:5_HEATC | 70.0995 | 116.7154 | 95.5891 | 133.6865 | 79.971 | 114.5283 | 94.9878 | 149.389 | 126.4974 | 122.7375 | 185.4785 | 158.7555 | 204.1831 | 194.1661 | 213.7312 | 282.4826
| PSZ-AC:6_HEATC | 63.5976 | 68.2213 | 66.7128 | 68.3957 | 58.4154 | 64.5315 | 49.8077 | 67.587 | 58.882 | 58.8285 | 63.7459 | 58.5856 | 70.5698 | 67.0945 | 73.7638 | 97.4048
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC:1_COOLC DXCOIL | 3.36 | 3.37 | 3.47 | 3.41 | 3.49 | 3.58 | 3.62 | 3.35 | 3.61 | 3.62 | 3.33 | 3.61 | 3.34 | 3.6 | 3.36 | 3.6
| PSZ-AC:2_COOLC DXCOIL | 3.1 | 3.33 | 3.16 | 3.35 | 3.18 | 3.62 | 3.29 | 3.33 | 3.91 | 3.96 | 3.31 | 3.71 | 3.31 | 3.89 | 3.31 | 3.89
| PSZ-AC:3_COOLC DXCOIL | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.41 | 3.1 | 3.14 | 3.15 | 3.1 | 3.13 | 3.1 | 3.56 | 3.31 | 3.35
| PSZ-AC:4_COOLC DXCOIL | 3.31 | 3.1 | 3.1 | 3.09 | 3.31 | 3.09 | 3.45 | 3.09 | 3.13 | 3.17 | 3.09 | 3.15 | 3.09 | 3.52 | 3.09 | 3.52
| PSZ-AC:5_COOLC DXCOIL | 3.1 | 3.33 | 2.97 | 3.33 | 3.14 | 3.33 | 3.35 | 3.33 | 3.51 | 4.17 | 3.31 | 3.89 | 3.31 | 3.89 | 3.31 | 3.89
| PSZ-AC:6_COOLC DXCOIL | 3.17 | 3.17 | 3.24 | 3.22 | 3.51 | 3.32 | 3.56 | 3.19 | 3.35 | 3.56 | 3.5 | 3.35 | 3.31 | 3.35 | 3.35 | 3.35
Heating Efficiency (%)
| PSZ-AC:1_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:2_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:3_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:4_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:5_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:6_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
HVAC Control - Economizer
| DELI EXHAUST FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| SALES EXHAUST FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC:1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC:2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC:3_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC:4_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| BAKERY EXHAUST FAN | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
| DELI EXHAUST FAN | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34
| SALES EXHAUST FAN | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08
| PSZ-AC:1_FAN | 0.54 | 0.68 | 0.61 | 0.83 | 0.47 | 0.73 | 0.55 | 0.88 | 0.92 | 0.71 | 1.11 | 1.15 | 1.23 | 1.32 | 1.31 | 1.66
| PSZ-AC:2_FAN | 2.56 | 3.6 | 3.1 | 4.35 | 2.5 | 3.82 | 2.95 | 4.64 | 4.87 | 3.78 | 5.82 | 6.05 | 6.46 | 6.95 | 6.92 | 8.85
| PSZ-AC:3_FAN | 2.28 | 2.54 | 2.6 | 2.56 | 2.23 | 2.57 | 1.92 | 2.35 | 2.56 | 2.07 | 2.16 | 2.4 | 2.2 | 2.37 | 2.35 | 3
| PSZ-AC:4_FAN | 7.01 | 10.49 | 10.15 | 13.06 | 8.44 | 12.07 | 9.57 | 13.82 | 15.07 | 11.81 | 16.42 | 17.58 | 17.98 | 19.53 | 19.21 | 23.38
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.081069 | 0.1041 | 0.077398 | 0.09853 | 0.12341 | 0.09348 | 0.14444 | 0.070281 | 0.037027 | 0.071158 | 0.095974 | 0.037027 | 0.055327 | 0.070139 | 0.054868 | 0.088425
| Total Cost ($/m2) | 44.24 | 55.59 | 38.11 | 49.25 | 55.66 | 44.28 | 61.75 | 33.93 | 17.13 | 31.17 | 46.02 | 17.13 | 26.67 | 32.57 | 25.71 | 42.94
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.01144 | 0.0080763 | 0.0082701 | 0.0097125 | 0.0085497 | 0.0077422 | 0.0085041 | 0.0097111 | 0.0069296 | 0.008383 | 0.0083854 | 0.006958 | 0.0078673 | 0.0082122 | 0.0078698 | 0.004136
| Total Cost ($/m2) | 0.88 | 2.44 | 2.5 | 5.1 | 2.66 | 3.3 | 5.21 | 7.97 | 4.42 | 7.06 | 8.61 | 5.77 | 9.87 | 8.94 | 12.19 | 9.81
Total Utility Costs
| Cost Intensity ($/m2) | 45.12 | 58.03 | 40.62 | 54.35 | 58.32 | 47.58 | 66.96 | 41.9 | 21.56 | 38.23 | 54.63 | 22.9 | 36.54 | 41.51 | 37.9 | 52.75
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 228125 | 194044.4444 | 195930.5556 | 116750 | 21613.8889 | 136425 | 5208.3333 | 86008.3333 | 61255.5556 | 8700 | 53116.6667 | 33547.2222 | 43347.2222 | 17475 | 12125 | 3600
| Interior Lighting | 420180.5556 | 420180.5556 | 420180.5556 | 420180.5556 | 420180.5556 | 420180.5556 | 420180.5556 | 420180.5556 | 420180.5556 | 420180.5556 | 420180.5556 | 420180.5556 | 420180.5556 | 420180.5556 | 420180.5556 | 420180.5556
| Exterior Lighting | 21494.4444 | 21458.3333 | 21450 | 21486.1111 | 21483.3333 | 21461.1111 | 21438.8889 | 21461.1111 | 21458.3333 | 21425 | 21430.5556 | 21436.1111 | 21447.2222 | 21422.2222 | 21416.6667 | 21288.8889
| Interior Equipment | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 142844.4444 | 230352.7778 | 185461.1111 | 281080.5556 | 158400 | 261827.7778 | 167297.2222 | 307619.4444 | 329888.8889 | 256061.1111 | 367433.3333 | 390972.2222 | 407155.5556 | 442266.6667 | 447633.3333 | 575438.8889
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 1250386.1111 | 1148313.8889 | 1017541.6667 | 1031833.3333 | 1045602.7778 | 922094.4444 | 954991.6667 | 964811.1111 | 883475 | 906691.6667 | 924325 | 849358.3333 | 904916.6667 | 821713.8889 | 839511.1111 | 791333.3333
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 2281277.7778 | 2232591.6667 | 2058811.1111 | 2089577.7778 | 1885525 | 1980233.3333 | 1787361.1111 | 2018325 | 1934500 | 1831302.7778 | 2004733.3333 | 1933738.8889 | 2015294.4444 | 1941302.7778 | 1959111.1111 | 2030088.8889
Gas (MJ)
| Heating | 108270 | 1043770 | 1049130 | 1978320 | 1082020 | 1566600 | 2341130 | 3210660 | 2448180 | 3301680 | 4068950 | 3246400 | 5022630 | 4327970 | 6250540 | 9689170
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 15860 | 17830 | 16700 | 19720 | 19360 | 18060 | 20980 | 21210 | 20930 | 21990 | 22520 | 22450 | 23650 | 23850 | 25510 | 27770
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 323260 | 1260730 | 1264950 | 2197170 | 1300510 | 1783790 | 2561230 | 3431000 | 2668240 | 3522790 | 4290600 | 3467980 | 5245410 | 4550950 | 6475180 | 9916060
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 8535860 | 9298050 | 8676670 | 9719650 | 8088400 | 8912630 | 8995730 | 10696970 | 9632440 | 10115480 | 11507640 | 10429440 | 12500470 | 11539640 | 13527980 | 17224380
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 196.4342 | 167.088 | 168.7121 | 100.5312 | 18.6113 | 117.473 | 4.4848 | 74.0602 | 52.746 | 7.4914 | 45.7378 | 28.8869 | 37.3255 | 15.0474 | 10.4406 | 3.0999
| Interior Lighting (elec) | 361.8096 | 361.8096 | 361.8096 | 361.8096 | 361.8096 | 361.8096 | 361.8096 | 361.8096 | 361.8096 | 361.8096 | 361.8096 | 361.8096 | 361.8096 | 361.8096 | 361.8096 | 361.8096
| Exterior Lighting (elec) | 18.5085 | 18.4774 | 18.4702 | 18.5013 | 18.4989 | 18.4798 | 18.4606 | 18.4798 | 18.4774 | 18.4487 | 18.4535 | 18.4582 | 18.4678 | 18.4463 | 18.4415 | 18.3315
| Interior Equipment (elec) | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 123.0007 | 198.3525 | 159.6971 | 242.0332 | 136.3953 | 225.455 | 144.0565 | 264.8853 | 284.0611 | 220.4894 | 316.39 | 336.6589 | 350.594 | 380.8275 | 385.4487 | 495.4997
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 1076.6841 | 988.7916 | 876.1861 | 888.4924 | 900.349 | 793.9983 | 822.3254 | 830.7808 | 760.7438 | 780.7352 | 795.919 | 731.3666 | 779.2068 | 707.5624 | 722.8873 | 681.4023
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1964.3656 | 1922.4429 | 1772.8037 | 1799.2963 | 1623.5903 | 1705.1419 | 1539.0632 | 1737.9419 | 1665.7617 | 1576.9005 | 1726.2383 | 1665.1064 | 1735.3323 | 1671.6195 | 1686.9539 | 1748.0715
Gas (MJ/m2)
| Heating (gas) | 25.897 | 249.6586 | 250.9406 | 473.1929 | 258.8075 | 374.7139 | 559.9731 | 767.9553 | 585.5783 | 789.7263 | 973.2491 | 776.504 | 1201.3591 | 1035.2039 | 1495.0619 | 2317.5452
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 3.7935 | 4.2647 | 3.9945 | 4.7168 | 4.6307 | 4.3198 | 5.0182 | 5.0732 | 5.0062 | 5.2598 | 5.3865 | 5.3698 | 5.6568 | 5.7047 | 6.1017 | 6.6423
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 77.3203 | 301.5531 | 302.5624 | 525.5394 | 311.068 | 426.6634 | 612.6187 | 820.6583 | 638.2143 | 842.6135 | 1026.2654 | 829.5035 | 1254.6457 | 1088.5383 | 1548.7934 | 2371.8149
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 2041.6859 | 2223.9936 | 2075.3661 | 2324.8357 | 1934.6583 | 2131.8052 | 2151.6819 | 2558.6002 | 2303.976 | 2419.514 | 2752.5037 | 2494.6099 | 2989.978 | 2760.1578 | 3235.7473 | 4119.8864
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 424.2356 | 411.4446 | 348.0586 | 378.4301 | 351.7972 | 353.2406 | 350.147 | 371.1211 | 354.7873 | 359.4935 | 360.9464 | 365.63 | 362.7642 | 368.3852 | 363.8005 | 381.7349
| Feb | 442.0923 | 406.7049 | 354.7216 | 377.2511 | 365.5655 | 363.2475 | 349.9335 | 360.4806 | 356.4107 | 350.3706 | 362.5624 | 361.6747 | 362.4686 | 373.3518 | 368.8276 | 379.7576
| Mar | 436.3793 | 418.5505 | 396.5172 | 381.9744 | 360.7456 | 353.4947 | 348.2743 | 391.9926 | 360.0477 | 360.0673 | 375.3771 | 369.3078 | 372.8996 | 370.3719 | 370.1456 | 383.0221
| Apr | 442.0856 | 468.6556 | 402.0586 | 422.1674 | 364.2384 | 416.2454 | 360.057 | 392.2705 | 378.0308 | 365.2555 | 389.6977 | 387.4695 | 383.6377 | 376.5669 | 376.8303 | 382.2921
| May | 469.4881 | 496.5411 | 447.1809 | 472.7533 | 389.8088 | 435.336 | 362.8988 | 434.7117 | 409.3492 | 378.3354 | 439.9392 | 410.6685 | 486.6852 | 389.8963 | 387.5902 | 400.236
| Jun | 489.9175 | 501.1496 | 518.6228 | 496.041 | 387.9049 | 497.5759 | 379.0696 | 518.6775 | 443.6992 | 391.9494 | 504.0907 | 439.0462 | 504.24 | 444.322 | 453.1573 | 428.4272
| Jul | 485.4731 | 520.1684 | 526.0523 | 522.746 | 414.0768 | 509.9921 | 402.2683 | 551.8195 | 453.5846 | 410.6843 | 531.9795 | 465.5526 | 506.0765 | 445.6561 | 489.7778 | 432.3754
| Aug | 474.9967 | 525.623 | 518.9191 | 502.5297 | 432.3224 | 528.0028 | 388.4256 | 522.9688 | 471.3701 | 405.4738 | 508.8836 | 465.4306 | 503.581 | 439.3127 | 466.9099 | 428.4321
| Sep | 476.0699 | 517.7422 | 489.649 | 471.1843 | 427.5974 | 481.3177 | 408.8339 | 465.1604 | 417.1182 | 425.2844 | 467.1672 | 421.0826 | 431.9548 | 417.743 | 406.4596 | 393.0276
| Oct | 476.3828 | 464.8273 | 425.1857 | 418.7511 | 392.7281 | 431.7262 | 358.7573 | 424.9521 | 393.7894 | 365.3972 | 405.7605 | 389.4073 | 389.8727 | 380.551 | 384.734 | 389.1625
| Nov | 447.5757 | 431.843 | 382.7652 | 388.4342 | 376.692 | 356.43 | 353.5226 | 407.4899 | 362.5101 | 366.6026 | 405.0162 | 364.7933 | 373.1504 | 369.7022 | 386.3485 | 380.1163
| Dec | 426.1422 | 421.9007 | 357.3547 | 381.881 | 361.4445 | 351.9286 | 347.6256 | 371.2742 | 353.6676 | 353.6296 | 365.004 | 359.8347 | 366.3307 | 366.6125 | 367.5796 | 385.0613
Time of Peak Electrical Demand
| Jan | 06-JAN-11:00 | 03-JAN-11:00 | 28-JAN-11:45 | 24-JAN-18:15 | 28-JAN-11:45 | 23-JAN-11:15 | 05-JAN-11:15 | 09-JAN-11:15 | 02-JAN-11:15 | 14-JAN-11:15 | 18-JAN-11:15 | 23-JAN-11:15 | 30-JAN-11:15 | 23-JAN-11:15 | 13-JAN-11:15 | 21-JAN-11:15
| Feb | 23-FEB-11:00 | 23-FEB-13:00 | 28-FEB-11:45 | 21-FEB-11:15 | 13-FEB-11:45 | 11-FEB-11:15 | 15-FEB-18:15 | 13-FEB-11:15 | 17-FEB-11:15 | 21-FEB-11:15 | 28-FEB-11:15 | 11-FEB-11:15 | 21-FEB-11:15 | 02-FEB-11:15 | 21-FEB-11:15 | 27-FEB-11:15
| Mar | 04-MAR-11:00 | 25-MAR-12:30 | 17-MAR-17:15 | 29-MAR-17:15 | 04-MAR-11:45 | 11-MAR-11:15 | 30-MAR-10:15 | 09-MAR-18:15 | 08-MAR-11:15 | 30-MAR-10:15 | 14-MAR-17:15 | 27-MAR-10:45 | 29-MAR-10:15 | 31-MAR-10:15 | 30-MAR-10:15 | 09-MAR-11:15
| Apr | 03-APR-10:45 | 29-APR-10:00 | 26-APR-17:15 | 14-APR-17:15 | 08-APR-10:45 | 21-APR-17:15 | 29-APR-10:45 | 04-APR-17:15 | 21-APR-17:15 | 29-APR-10:15 | 10-APR-10:15 | 26-APR-10:45 | 01-APR-17:15 | 24-APR-10:15 | 14-APR-10:15 | 14-APR-10:15
| May | 24-MAY-10:00 | 26-MAY-17:15 | 30-MAY-17:15 | 31-MAY-17:15 | 30-MAY-10:45 | 31-MAY-17:15 | 17-MAY-10:45 | 15-MAY-17:15 | 31-MAY-17:15 | 05-MAY-17:15 | 30-MAY-17:15 | 24-MAY-10:45 | 27-MAY-14:00 | 25-MAY-17:15 | 27-MAY-10:15 | 31-MAY-10:15
| Jun | 26-JUN-10:00 | 30-JUN-10:45 | 28-JUN-17:15 | 19-JUN-10:45 | 28-JUN-10:45 | 28-JUN-10:45 | 16-JUN-10:45 | 30-JUN-17:15 | 29-JUN-10:45 | 28-JUN-10:45 | 08-JUN-12:00 | 28-JUN-10:45 | 29-JUN-17:15 | 30-JUN-10:45 | 14-JUN-17:15 | 21-JUN-17:15
| Jul | 11-JUL-10:00 | 31-JUL-10:00 | 19-JUL-17:15 | 03-JUL-17:15 | 29-JUL-10:45 | 11-JUL-10:45 | 03-JUL-10:45 | 25-JUL-10:00 | 03-JUL-10:45 | 31-JUL-17:15 | 14-JUL-10:00 | 19-JUL-10:45 | 13-JUL-17:15 | 21-JUL-17:15 | 08-JUL-10:00 | 21-JUL-17:15
| Aug | 30-AUG-10:00 | 31-AUG-10:00 | 01-AUG-17:15 | 17-AUG-10:00 | 08-AUG-10:45 | 05-AUG-10:45 | 15-AUG-10:45 | 17-AUG-10:00 | 01-AUG-10:45 | 18-AUG-17:15 | 04-AUG-17:15 | 30-AUG-10:45 | 25-AUG-17:15 | 11-AUG-17:15 | 12-AUG-10:00 | 15-AUG-17:15
| Sep | 26-SEP-10:00 | 16-SEP-10:00 | 08-SEP-17:15 | 11-SEP-10:00 | 09-SEP-10:45 | 01-SEP-10:45 | 29-SEP-10:45 | 09-SEP-10:45 | 12-SEP-10:45 | 02-SEP-14:00 | 06-SEP-10:45 | 09-SEP-10:45 | 14-SEP-17:15 | 01-SEP-17:15 | 08-SEP-17:15 | 01-SEP-10:15
| Oct | 07-OCT-10:00 | 30-OCT-10:00 | 13-OCT-17:15 | 12-OCT-15:00 | 05-OCT-10:45 | 06-OCT-10:45 | 21-OCT-10:15 | 03-OCT-10:00 | 03-OCT-10:45 | 05-OCT-10:15 | 31-OCT-10:45 | 05-OCT-10:45 | 14-OCT-10:15 | 06-OCT-17:15 | 07-OCT-10:15 | 02-OCT-10:15
| Nov | 01-NOV-10:00 | 21-NOV-11:45 | 13-NOV-11:45 | 22-NOV-11:45 | 20-NOV-11:45 | 01-NOV-10:15 | 24-NOV-11:15 | 04-NOV-10:45 | 10-NOV-11:15 | 03-NOV-10:15 | 02-NOV-10:45 | 16-NOV-11:15 | 03-NOV-10:15 | 01-NOV-10:15 | 09-NOV-11:15 | 14-NOV-11:15
| Dec | 16-DEC-11:00 | 02-DEC-11:00 | 13-DEC-11:45 | 26-DEC-11:15 | 04-DEC-11:45 | 05-DEC-11:45 | 04-DEC-11:15 | 23-DEC-11:15 | 22-DEC-11:15 | 05-DEC-11:15 | 12-DEC-11:15 | 30-DEC-11:15 | 02-DEC-11:15 | 29-DEC-11:15 | 02-DEC-11:15 | 18-DEC-11:15
Source Energy
| Total Source Energy (GJ) | 27594.2 | 30568.28 | 24824.6 | 27704.93 | 22428.68 | 27447.77 | 22711.65 | 29729.75 | 26020.94 | 15331.35 | 30276.95 | 26885.15 | 30663.62 | 29262.33 | 31311.37 | 36933.64
| Total Source Energy (MJ/m2) | 6600.23 | 7311.6 | 5937.77 | 6626.72 | 5364.69 | 6565.2 | 5432.38 | 7111.03 | 6223.92 | 3667.09 | 7241.91 | 6430.63 | 7334.4 | 6999.23 | 7489.34 | 8834.12
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12
| Total Building | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12
Emissions
| Carbon Equivalent (kg) | 631469.2352 | 767439.413 | 644315.0926 | 683287.5178 | 243805.1834 | 700049.982 | 255067.4599 | 606525.9507 | 838355.2144 | 196906.7782 | 1146190 | 852465.1446 | 784409.9121 | 791490.8575 | 787355.1212 | 750054.4125
| CO2 (kg) | 1465540 | 1934360 | 1527500 | 1575340 | 656063.1392 | 1674830 | 691118.5401 | 1400160 | 1980350 | 500382.0985 | 2689600 | 2021290 | 1863590 | 1887130 | 1883330 | 1947600
| NOX (kg) | 2570.2308 | 2515.8395 | 2530.1586 | 2924.8563 | 564.972 | 2678.5588 | 598.3933 | 2604.3775 | 3356.9011 | 675.7155 | 4693.3863 | 3393.4551 | 3150.1312 | 3144.2204 | 3127.3964 | 2261.7595
| SO2 (kg) | 9764.8715 | 10649.7963 | 8279.2302 | 7335.0078 | 5487.0026 | 10893.3485 | 5201.6966 | 7368.6088 | 8448.2922 | 1416.3946 | 13511.4445 | 8445.1761 | 4757.8222 | 5184.7319 | 4625.5515 | 10336.6156
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0445 | 0.0301 | 0.0226 | 0.027 | 0.0026 | 0.0206 | 0.0026 | 0.03 | 0.0332 | 0.0059 | 0.0412 | 0.0333 | 0.0352 | 0.0364 | 0.0344 | 0.036
| Water for Electricity (m3) | 1208.53 | 3632.69 | 61155.7 | 13046.5 | 33105.6 | 54325.7 | 31382.1 | 458.2354 | 8784.18 | 18710.1 | 3110.22 | 8780.71 | 3126.61 | 122970 | 3039.44 | 2074.1

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 8535.86 | 2041.68 | 2041.68
Net Site Energy | 8535.86 | 2041.68 | 2041.68
Total Source Energy | 27594.2 | 6600.23 | 6600.23
Net Source Energy | 27594.2 | 6600.23 | 6600.23
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 108.27 | 0 | 0 | 0 | 0
Cooling | 821.25 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1512.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 77.38 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 514.24 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 15.86 | 0 | 0 | 0 | 87.12
Refrigeration | 4501.39 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8212.6 | 323.26 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 29.94 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 29.94 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 11.9 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 21.36 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 29.94 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 29.94 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 174.7 | 174.7 | 5.835 | 0.54 | 0.384 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12618.49 | 8747.81 | 3870.68 | 0.69 | 3.36
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 63549.3 | 42964.62 | 20584.69 | 0.68 | 3.1
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 56644.85 | 38296.63 | 18348.22 | 0.68 | 3.1
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 173994.96 | 117635.07 | 56359.89 | 0.68 | 3.31
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 57590.49 | 38935.97 | 18654.53 | 0.68 | 3.1
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 54241.02 | 38529.12 | 15711.9 | 0.71 | 3.17
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 13587.63 | 0.78
PSZ-AC:2_HEATC | Coil:Heating:Gas | 68115.11 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 88314.46 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 215863.07 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 70099.5 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 63597.59 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.54 | 630.7 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.56 | 2798.73 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.28 | 2494.66 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.01 | 13144.64 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.32 | 2536.3 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.49 | 2722.61 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.72 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 113463.5214 | 197.5395 | 744.594 | 0 | 0.0034 | 92151.7691 | 48743.5466
February | 103188.0805 | 180.2005 | 681.4949 | 0 | 0.0031 | 84342.983 | 44384.4093
March | 116220.5544 | 203.2691 | 770.0033 | 0 | 0.0035 | 95297.1691 | 50021.1046
April | 118000.1199 | 207.1421 | 787.7799 | 0 | 0.0036 | 97497.8163 | 50863.2374
May | 129076.3152 | 226.8024 | 863.4313 | 0 | 0.0039 | 106860.7952 | 55659.278
June | 129962.0964 | 228.4049 | 869.7193 | 0 | 0.004 | 107639.0553 | 56045.856
July | 136154.4111 | 239.3183 | 911.3993 | 0 | 0.0042 | 112797.5195 | 58719.3381
August | 137005.9418 | 240.8008 | 916.9873 | 0 | 0.0042 | 113489.1004 | 59085.1521
September | 128701.447 | 226.1912 | 861.2974 | 0 | 0.0039 | 106596.7386 | 55502.3884
October | 126458.4281 | 222.1719 | 845.6791 | 0 | 0.0039 | 104663.718 | 54527.3545
November | 115342.1371 | 202.4098 | 769.5126 | 0 | 0.0035 | 95236.9571 | 49710.8802
December | 111971.7761 | 195.9802 | 742.973 | 0 | 0.0034 | 91951.957 | 48206.6899
Annual Sum or Average | 1465540 | 2570.2308 | 9764.8715 | 0 | 0.0445 | 1208530 | 631469.2352
Minimum of Months | 103188.0805 | 180.2005 | 681.4949 | 0 | 0.0031 | 84342.983 | 44384.4093
Maximum of Months | 137005.9418 | 240.8008 | 916.9873 | 0 | 0.0042 | 113489.1004 | 59085.1521
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 626222000000 | 424235.611 | 06-JAN-11:00 | 101872.638 | 41401.92 | 24458.559 | 0 | 49382.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207120.383 | 0 | 0
February | 573157000000 | 442092.288 | 23-FEB-11:00 | 101872.638 | 41401.92 | 24458.559 | 0 | 66580.013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207779.157 | 0 | 0
March | 647597000000 | 436379.297 | 04-MAR-11:00 | 101872.638 | 41401.92 | 24458.559 | 0 | 60784.169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207862.011 | 0 | 0
April | 662552000000 | 442085.611 | 03-APR-10:45 | 101872.638 | 41401.92 | 24458.559 | 0 | 62830.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211521.583 | 0 | 0
May | 726178000000 | 469488.083 | 24-MAY-10:00 | 101872.638 | 41401.92 | 24458.559 | 0 | 86684.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215070.846 | 0 | 0
June | 731467000000 | 489917.515 | 26-JUN-10:00 | 101872.638 | 41401.92 | 24458.559 | 0 | 103222.293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218962.105 | 0 | 0
July | 766522000000 | 485473.07 | 11-JUL-10:00 | 101872.638 | 41401.92 | 24458.559 | 0 | 99092.391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218647.562 | 0 | 0
August | 771222000000 | 474996.697 | 30-AUG-10:00 | 101872.638 | 41401.92 | 24458.559 | 0 | 90281.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216982.56 | 0 | 0
September | 724384000000 | 476069.928 | 26-SEP-10:00 | 101872.638 | 41401.92 | 24458.559 | 0 | 91645.513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216691.298 | 0 | 0
October | 711248000000 | 476382.795 | 07-OCT-10:00 | 101872.638 | 41401.92 | 24458.559 | 0 | 92889.401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215760.277 | 0 | 0
November | 647188000000 | 447575.664 | 01-NOV-10:00 | 101872.638 | 41401.92 | 24458.559 | 0 | 69032.646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210809.901 | 0 | 0
December | 624865000000 | 426142.157 | 16-DEC-11:00 | 101872.638 | 41401.92 | 24458.559 | 0 | 54011.714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204397.325 | 0 | 0
Annual Sum or Average | 8212600000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 573157000000 | 424235.611 |  | 101872.638 | 41401.92 | 24458.559 | 0 | 49382.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204397.325 | 0 | 0
Maximum of Months | 771222000000 | 489917.515 |  | 101872.638 | 41401.92 | 24458.559 | 0 | 103222.293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218962.105 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 184939.91 | 3697.96 | 0 | 188637.87
Cost per Total Building Area ($/m2) | 44.24 | 0.88 | 0 | 45.12
Cost per Net Conditioned Building Area ($/m2) | 44.24 | 0.88 | 0 | 45.12

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 9298.05 | 2223.99 | 2223.99
Net Site Energy | 9298.05 | 2223.99 | 2223.99
Total Source Energy | 30568.28 | 7311.6 | 7311.6
Net Source Energy | 30568.28 | 7311.6 | 7311.6
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1043.77 | 0 | 0 | 0 | 0
Cooling | 698.56 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1512.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 77.25 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 829.27 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 17.83 | 0 | 0 | 0 | 87.12
Refrigeration | 4133.93 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8037.33 | 1260.73 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 29.94 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 29.94 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 11.9 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 21.36 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 29.94 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 29.94 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 174.7 | 174.7 | 5.835 | 0.54 | 0.384 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 15590.89 | 10875.48 | 4715.41 | 0.7 | 3.37
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 89425.92 | 60459.37 | 28966.56 | 0.68 | 3.33
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 62982.96 | 42581.72 | 20401.24 | 0.68 | 3.1
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 260574.47 | 176170.03 | 84404.44 | 0.68 | 3.1
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 91920.51 | 62145.92 | 29774.6 | 0.68 | 3.33
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 55073.91 | 39248.95 | 15824.96 | 0.71 | 3.17
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 17280.66 | 0.78
PSZ-AC:2_HEATC | Coil:Heating:Gas | 97030.07 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 129632.38 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 343481.51 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 116715.39 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 68221.28 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.68 | 792.04 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.6 | 6869.01 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.54 | 2773.79 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.59 | 1017.59 | 10.49 | 18052.3 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.7 | 7060.62 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.55 | 2787.45 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.72 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 148957.9374 | 189.7253 | 763.9388 | 0 | 0.0022 | 260564.6016 | 58580.7301
February | 133641.3103 | 169.9843 | 682.131 | 0 | 0.0019 | 232660.4276 | 52527.1922
March | 147535.5288 | 191.0985 | 801.2493 | 0 | 0.0023 | 273305.7333 | 58431.8606
April | 151668.2868 | 198.42 | 851.2639 | 0 | 0.0024 | 290374.6091 | 60322.3899
May | 170555.5764 | 223.6558 | 964.6457 | 0 | 0.0027 | 329052.5695 | 67902.2151
June | 179080.0505 | 234.9985 | 1015.1591 | 0 | 0.0029 | 346284.0512 | 71317.1769
July | 189928.5775 | 249.2578 | 1076.9832 | 0 | 0.003 | 367373.1705 | 75640.5205
August | 188760.0414 | 247.6992 | 1070.006 | 0 | 0.003 | 364993.0202 | 75171.9104
September | 170416.2978 | 223.5996 | 965.6284 | 0 | 0.0027 | 329388.3284 | 67863.0591
October | 161772.5216 | 211.7495 | 909.5249 | 0 | 0.0026 | 310248.4979 | 64355.3632
November | 144228.2499 | 187.4572 | 792.2877 | 0 | 0.0022 | 270251.848 | 57204.8332
December | 147817.97 | 188.1938 | 756.9784 | 0 | 0.0022 | 258190.1512 | 58122.1617
Annual Sum or Average | 1934360 | 2515.8395 | 10649.7963 | 0 | 0.0301 | 3632690 | 767439.413
Minimum of Months | 133641.3103 | 169.9843 | 682.131 | 0 | 0.0019 | 232660.4276 | 52527.1922
Maximum of Months | 189928.5775 | 249.2578 | 1076.9832 | 0 | 0.003 | 367373.1705 | 75640.5205
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 576500000000 | 411444.603 | 03-JAN-11:00 | 101872.638 | 41401.92 | 38466.123 | 0 | 25336.337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204367.586 | 0 | 0
February | 514762000000 | 406704.934 | 23-FEB-13:00 | 101872.638 | 41401.92 | 38466.123 | 0 | 50841.104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174123.148 | 0 | 0
March | 604689000000 | 418550.525 | 25-MAR-12:30 | 101872.638 | 41401.92 | 38466.123 | 0 | 55973.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180836.811 | 0 | 0
April | 642454000000 | 468655.566 | 29-APR-10:00 | 101872.638 | 41401.92 | 38466.123 | 0 | 76074.934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210839.951 | 0 | 0
May | 728029000000 | 496541.092 | 26-MAY-17:15 | 67915.092 | 36859.929 | 38466.123 | 0 | 109903.267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243396.681 | 0 | 0
June | 766154000000 | 501149.633 | 30-JUN-10:45 | 101872.638 | 41401.92 | 38466.123 | 0 | 100518.978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218889.974 | 0 | 0
July | 812814000000 | 520168.354 | 31-JUL-10:00 | 101872.638 | 41401.92 | 38466.123 | 0 | 118213.734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220213.939 | 0 | 0
August | 807548000000 | 525623.023 | 31-AUG-10:00 | 101872.638 | 41401.92 | 38466.123 | 0 | 122739.648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221142.695 | 0 | 0
September | 728772000000 | 517742.162 | 16-SEP-10:00 | 101872.638 | 41401.92 | 38466.123 | 0 | 117988.636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218012.845 | 0 | 0
October | 686425000000 | 464827.256 | 30-OCT-10:00 | 101872.638 | 41401.92 | 38466.123 | 0 | 73128.491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209958.084 | 0 | 0
November | 597933000000 | 431842.994 | 21-NOV-11:45 | 101872.638 | 41401.92 | 38466.123 | 0 | 42896.216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207206.097 | 0 | 0
December | 571246000000 | 421900.707 | 02-DEC-11:00 | 101872.638 | 41401.92 | 38466.123 | 0 | 31513.827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208646.198 | 0 | 0
Annual Sum or Average | 8037330000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 514762000000 | 406704.934 |  | 67915.092 | 36859.929 | 38466.123 | 0 | 25336.337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174123.148 | 0 | 0
Maximum of Months | 812814000000 | 525623.023 |  | 101872.638 | 41401.92 | 38466.123 | 0 | 122739.648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243396.681 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 232411.41 | 10182.06 | 0 | 242593.48
Cost per Total Building Area ($/m2) | 55.59 | 2.44 | 0 | 58.03
Cost per Net Conditioned Building Area ($/m2) | 55.59 | 2.44 | 0 | 58.03

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 8676.67 | 2075.37 | 2075.37
Net Site Energy | 8676.67 | 2075.37 | 2075.37
Total Source Energy | 24824.6 | 5937.77 | 5937.77
Net Source Energy | 24824.6 | 5937.77 | 5937.77
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1049.13 | 0 | 0 | 0 | 0
Cooling | 705.35 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1512.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 77.22 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 667.66 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 16.7 | 0 | 0 | 0 | 87.12
Refrigeration | 3663.15 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7411.72 | 1264.95 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 29.94 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 29.94 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 11.9 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 21.36 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 29.94 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 29.94 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 174.7 | 174.7 | 5.835 | 0.54 | 0.384 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11949.5 | 8851.7 | 3097.8 | 0.74 | 3.47
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 69206.54 | 48723.84 | 20482.69 | 0.7 | 3.16
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 64618.68 | 43687.61 | 20931.08 | 0.68 | 3.1
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 252105.47 | 170444.28 | 81661.19 | 0.68 | 3.1
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 80635.7 | 54516.45 | 26119.26 | 0.68 | 2.97
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 51454.67 | 38314.1 | 13140.57 | 0.74 | 3.24
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 14677.52 | 0.78
PSZ-AC:2_HEATC | Coil:Heating:Gas | 80127.42 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 112210.65 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 297617.06 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 95589.1 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 66712.79 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.61 | 705.45 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.1 | 3395.49 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.6 | 2845.83 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.59 | 1017.59 | 10.15 | 17465.57 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.25 | 3551.22 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.65 | 2899.77 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.72 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 115894.1571 | 184.7374 | 575.8534 | 0 | 0.0016 | 4253260 | 48154.288
February | 103720.9834 | 166.0378 | 520.4651 | 0 | 0.0014 | 3844200 | 43167.5633
March | 116639.2429 | 192.5146 | 627.2245 | 0 | 0.0017 | 4633050 | 49130.2185
April | 114781.8447 | 191.4052 | 631.3886 | 0 | 0.0017 | 4663910 | 48545.6824
May | 126715.238 | 212.7047 | 707.1583 | 0 | 0.0019 | 5223670 | 53734.3356
June | 140180.5288 | 236.0897 | 787.9618 | 0 | 0.0021 | 5820590 | 59523.4608
July | 158626.2567 | 267.3551 | 893.0886 | 0 | 0.0024 | 6597160 | 67376.0492
August | 156385.0315 | 263.5636 | 880.3679 | 0 | 0.0024 | 6503200 | 66422.6664
September | 141790.9501 | 238.8487 | 797.3521 | 0 | 0.0022 | 5889960 | 60212.0029
October | 123895.1257 | 207.2523 | 686.2219 | 0 | 0.0019 | 5068980 | 52465.7867
November | 111628.3966 | 184.0484 | 598.8633 | 0 | 0.0016 | 4423550 | 46999.7883
December | 117237.5271 | 185.601 | 573.2849 | 0 | 0.0016 | 4234220 | 48583.2507
Annual Sum or Average | 1527500 | 2530.1586 | 8279.2302 | 0 | 0.0226 | 61155700 | 644315.0926
Minimum of Months | 103720.9834 | 166.0378 | 520.4651 | 0 | 0.0014 | 3844200 | 43167.5633
Maximum of Months | 158626.2567 | 267.3551 | 893.0886 | 0 | 0.0024 | 6597160 | 67376.0492
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 515470000000 | 348058.553 | 28-JAN-11:45 | 101872.638 | 41401.92 | 30994.253 | 0 | 4877.287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168912.456 | 0 | 0
February | 465894000000 | 354721.605 | 28-FEB-11:45 | 101872.638 | 41401.92 | 30994.253 | 0 | 5875.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174577.17 | 0 | 0
March | 561499000000 | 396517.151 | 17-MAR-17:15 | 67915.092 | 36859.929 | 30994.253 | 0 | 51264.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209483.85 | 0 | 0
April | 565239000000 | 402058.593 | 26-APR-17:15 | 67915.092 | 36859.929 | 30994.253 | 0 | 58648.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207641.18 | 0 | 0
May | 633078000000 | 447180.882 | 30-MAY-17:15 | 67915.092 | 36859.929 | 30994.253 | 0 | 96080.762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215330.846 | 0 | 0
June | 705422000000 | 518622.821 | 28-JUN-17:15 | 67915.092 | 36859.929 | 30994.253 | 0 | 160157.144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222696.403 | 0 | 0
July | 799538000000 | 526052.3 | 19-JUL-17:15 | 67915.092 | 36859.929 | 30994.253 | 0 | 157233.996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233049.031 | 0 | 0
August | 788149000000 | 518919.12 | 01-AUG-17:15 | 67915.092 | 36859.929 | 30994.253 | 0 | 156447.592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226702.255 | 0 | 0
September | 713829000000 | 489648.98 | 08-SEP-17:15 | 67915.092 | 36859.929 | 30994.253 | 0 | 122233.289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231646.417 | 0 | 0
October | 614331000000 | 425185.695 | 13-OCT-17:15 | 67915.092 | 36859.929 | 30994.253 | 0 | 67237.796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222178.625 | 0 | 0
November | 536108000000 | 382765.242 | 13-NOV-11:45 | 101872.638 | 41401.92 | 30994.253 | 0 | 23211.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185284.671 | 0 | 0
December | 513162000000 | 357354.712 | 13-DEC-11:45 | 101872.638 | 41401.92 | 30994.253 | 0 | 52.081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183033.82 | 0 | 0
Annual Sum or Average | 7411720000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 465894000000 | 348058.553 |  | 67915.092 | 36859.929 | 30994.253 | 0 | 52.081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168912.456 | 0 | 0
Maximum of Months | 799538000000 | 526052.3 |  | 101872.638 | 41401.92 | 30994.253 | 0 | 160157.144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233049.031 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 159348.03 | 10461.25 | 0 | 169809.28
Cost per Total Building Area ($/m2) | 38.11 | 2.5 | 0 | 40.62
Cost per Net Conditioned Building Area ($/m2) | 38.11 | 2.5 | 0 | 40.62

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 9719.65 | 2324.83 | 2324.83
Net Site Energy | 9719.65 | 2324.83 | 2324.83
Total Source Energy | 27704.93 | 6626.72 | 6626.72
Net Source Energy | 27704.93 | 6626.72 | 6626.72
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1978.32 | 0 | 0 | 0 | 0
Cooling | 420.3 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1512.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 77.35 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1011.89 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 19.72 | 0 | 0 | 0 | 87.12
Refrigeration | 3714.6 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7522.48 | 2197.17 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 29.94 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 29.94 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 11.9 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 21.36 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 29.94 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 29.94 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 174.7 | 174.7 | 5.835 | 0.54 | 0.384 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 17742.34 | 12720.08 | 5022.26 | 0.72 | 3.41
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 104911.84 | 71673.65 | 33238.2 | 0.68 | 3.35
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 63460.52 | 42904.59 | 20555.93 | 0.68 | 3.1
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 324203.4 | 219188.48 | 105014.92 | 0.68 | 3.09
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 108814.93 | 73567.95 | 35246.98 | 0.68 | 3.33
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 51644.71 | 37933.26 | 13711.45 | 0.73 | 3.22
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 20260.59 | 0.78
PSZ-AC:2_HEATC | Coil:Heating:Gas | 113375.8 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 140900.27 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 404313.72 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 133686.53 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 68395.67 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.83 | 966.87 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.35 | 8291.85 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.56 | 2794.82 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 13.06 | 22120.12 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.38 | 8358.32 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.58 | 2816.62 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.72 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 131908.1246 | 227.1471 | 527.1203 | 0 | 0.002 | 937396.592 | 55573.6211
February | 116906.0329 | 204.722 | 483.8797 | 0 | 0.0018 | 860538.7618 | 49567.9583
March | 122681.9015 | 223.8874 | 552.1547 | 0 | 0.002 | 982058.0666 | 52852.7962
April | 120764.1082 | 226.4911 | 573.4429 | 0 | 0.0021 | 1019980 | 52590.2616
May | 133258.9584 | 255.2418 | 658.838 | 0 | 0.0024 | 1171920 | 58522.5403
June | 139573.236 | 268.3949 | 695.2463 | 0 | 0.0025 | 1236700 | 61393.3252
July | 149813.5863 | 288.2611 | 747.1108 | 0 | 0.0027 | 1328950 | 65913.8
August | 149672.7995 | 287.9617 | 746.2685 | 0 | 0.0027 | 1327460 | 65849.2172
September | 137266.6084 | 263.911 | 683.5199 | 0 | 0.0025 | 1215840 | 60374.2647
October | 124790.134 | 235.6136 | 600.2654 | 0 | 0.0022 | 1067710 | 54488.6725
November | 119539.0914 | 217.0157 | 532.4396 | 0 | 0.002 | 946981.6552 | 51393.8964
December | 129163.5879 | 226.2089 | 534.7218 | 0 | 0.002 | 950957.207 | 54767.1644
Annual Sum or Average | 1575340 | 2924.8563 | 7335.0078 | 0 | 0.027 | 13046500 | 683287.5178
Minimum of Months | 116906.0329 | 204.722 | 483.8797 | 0 | 0.0018 | 860538.7618 | 49567.9583
Maximum of Months | 149813.5863 | 288.2611 | 747.1108 | 0 | 0.0027 | 1328950 | 65913.8
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 540494000000 | 378430.12 | 24-JAN-18:15 | 67915.092 | 36859.929 | 45479.519 | 0 | 3948.735 | 4916 | 0 | 0 | 0 | 0 | 0 | 0 | 219310.846 | 0 | 0
February | 496179000000 | 377251.064 | 21-FEB-11:15 | 101872.638 | 41401.92 | 45479.519 | 0 | 3000.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185496.517 | 0 | 0
March | 566245000000 | 381974.404 | 29-MAR-17:15 | 67915.092 | 36859.929 | 45479.519 | 0 | 9078.381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222641.483 | 0 | 0
April | 588112000000 | 422167.365 | 14-APR-17:15 | 67915.092 | 36859.929 | 45479.519 | 0 | 43813.231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228099.594 | 0 | 0
May | 675721000000 | 472753.349 | 31-MAY-17:15 | 67915.092 | 36859.929 | 45479.519 | 0 | 83000.652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239498.156 | 0 | 0
June | 713067000000 | 496041.013 | 19-JUN-10:45 | 101872.638 | 41401.92 | 45479.519 | 0 | 89826.535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 217460.401 | 0 | 0
July | 766262000000 | 522745.955 | 03-JUL-17:15 | 67915.092 | 36859.929 | 45479.519 | 0 | 130826.399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241665.015 | 0 | 0
August | 765398000000 | 502529.716 | 17-AUG-10:00 | 101872.638 | 41401.92 | 45479.519 | 0 | 98081.405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215694.234 | 0 | 0
September | 701040000000 | 471184.269 | 11-SEP-10:00 | 101872.638 | 41401.92 | 45479.519 | 0 | 75420.178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207010.014 | 0 | 0
October | 615629000000 | 418751.136 | 12-OCT-15:00 | 101872.638 | 41401.92 | 45479.519 | 0 | 73120.548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156876.511 | 0 | 0
November | 546021000000 | 388434.206 | 22-NOV-11:45 | 101872.638 | 41401.92 | 45479.519 | 0 | 10206.923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189473.205 | 0 | 0
December | 548313000000 | 381881.005 | 26-DEC-11:15 | 101872.638 | 41401.92 | 45479.519 | 0 | 4182.182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188944.746 | 0 | 0
Annual Sum or Average | 7522480000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 496179000000 | 377251.064 |  | 67915.092 | 36859.929 | 45479.519 | 0 | 3000.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156876.511 | 0 | 0
Maximum of Months | 766262000000 | 522745.955 |  | 101872.638 | 41401.92 | 45479.519 | 0 | 130826.399 | 4916 | 0 | 0 | 0 | 0 | 0 | 0 | 241665.015 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 205885.57 | 21340.02 | 0 | 227225.59
Cost per Total Building Area ($/m2) | 49.25 | 5.1 | 0 | 54.35
Cost per Net Conditioned Building Area ($/m2) | 49.25 | 5.1 | 0 | 54.35

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 8088.4 | 1934.66 | 1934.66
Net Site Energy | 8088.4 | 1934.66 | 1934.66
Total Source Energy | 22428.68 | 5364.69 | 5364.69
Net Source Energy | 22428.68 | 5364.69 | 5364.69
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1082.02 | 0 | 0 | 0 | 0
Cooling | 77.81 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1512.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 77.34 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 570.24 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 19.36 | 0 | 0 | 0 | 87.12
Refrigeration | 3764.17 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6787.89 | 1300.51 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 29.94 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 29.94 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 11.9 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 21.36 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 29.94 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 29.94 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 174.7 | 174.7 | 5.835 | 0.54 | 0.384 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8936.22 | 6689.28 | 2246.94 | 0.75 | 3.49
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 52992.56 | 38069.26 | 14923.3 | 0.72 | 3.18
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 55467.75 | 37500.81 | 17966.93 | 0.68 | 3.1
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 209527.35 | 141657.92 | 67869.42 | 0.68 | 3.31
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 60041.68 | 41927.06 | 18114.62 | 0.7 | 3.14
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 39508.02 | 30754.01 | 8754.02 | 0.78 | 3.51
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 11799.71 | 0.78
PSZ-AC:2_HEATC | Coil:Heating:Gas | 66780.45 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 89942.12 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 253840.64 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 79971.02 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 58415.43 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.47 | 540.84 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.5 | 2736.67 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.23 | 2442.82 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 8.44 | 15828.98 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.64 | 2883.95 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.26 | 2466.51 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.72 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 56940.0051 | 49.3274 | 423.7445 | 0 | 0.0002 | 2556450 | 20999.8593
February | 51525.1867 | 44.5974 | 390.4532 | 0 | 0.0002 | 2355630 | 19024.2111
March | 56214.1818 | 48.553 | 444.4033 | 0 | 0.0002 | 2681190 | 20811.6796
April | 53681.6565 | 46.2962 | 436.7993 | 0 | 0.0002 | 2635370 | 19911.9689
May | 54994.8696 | 47.2905 | 472.2219 | 0 | 0.0002 | 2849180 | 20474.5473
June | 53543.626 | 45.9873 | 469.6448 | 0 | 0.0002 | 2833660 | 19964.4067
July | 55386.2493 | 47.485 | 500.9995 | 0 | 0.0002 | 3022900 | 20697.8036
August | 57042.0861 | 48.8942 | 517.846 | 0 | 0.0002 | 3124550 | 21322.2895
September | 53586.6572 | 45.9409 | 484.9527 | 0 | 0.0002 | 2926080 | 20026.0036
October | 54014.8882 | 46.3791 | 476.0984 | 0 | 0.0002 | 2872610 | 20147.2011
November | 53246.6823 | 45.8927 | 438.3454 | 0 | 0.0002 | 2644710 | 19766.1406
December | 55887.0505 | 48.3282 | 431.4936 | 0 | 0.0002 | 2603270 | 20659.0721
Annual Sum or Average | 656063.1392 | 564.972 | 5487.0026 | 0 | 0.0026 | 33105600 | 243805.1834
Minimum of Months | 51525.1867 | 44.5974 | 390.4532 | 0 | 0.0002 | 2355630 | 19024.2111
Maximum of Months | 57042.0861 | 49.3274 | 517.846 | 0 | 0.0002 | 3124550 | 21322.2895
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 524168000000 | 351797.222 | 28-JAN-11:45 | 101872.638 | 41401.92 | 27030.675 | 0 | 5825.502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175666.487 | 0 | 0
February | 482993000000 | 365565.476 | 13-FEB-11:45 | 101872.638 | 41401.92 | 27030.675 | 0 | 10960.452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184299.791 | 0 | 0
March | 549745000000 | 360745.587 | 04-MAR-11:45 | 101872.638 | 41401.92 | 27030.675 | 0 | 8525.865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181914.49 | 0 | 0
April | 540349000000 | 364238.351 | 08-APR-10:45 | 101872.638 | 41401.92 | 27030.675 | 0 | 11370.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182562.747 | 0 | 0
May | 584188000000 | 389808.819 | 30-MAY-10:45 | 101872.638 | 41401.92 | 27030.675 | 0 | 18631.908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200871.678 | 0 | 0
June | 581008000000 | 387904.916 | 28-JUN-10:45 | 101872.638 | 41401.92 | 27030.675 | 0 | 18133.146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199466.537 | 0 | 0
July | 619808000000 | 414076.849 | 29-JUL-10:45 | 101872.638 | 41401.92 | 27030.675 | 0 | 37271.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206500.495 | 0 | 0
August | 640651000000 | 432322.423 | 08-AUG-10:45 | 101872.638 | 41401.92 | 27030.675 | 0 | 54017.909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207999.281 | 0 | 0
September | 599956000000 | 427597.442 | 09-SEP-10:45 | 101872.638 | 41401.92 | 27030.675 | 0 | 48878.651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208413.558 | 0 | 0
October | 588993000000 | 392728.06 | 05-OCT-10:45 | 101872.638 | 41401.92 | 27030.675 | 0 | 21271.503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201151.324 | 0 | 0
November | 542266000000 | 376691.997 | 20-NOV-11:45 | 101872.638 | 41401.92 | 27030.675 | 0 | 15118.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191268.717 | 0 | 0
December | 533767000000 | 361444.471 | 04-DEC-11:45 | 101872.638 | 41401.92 | 27030.675 | 0 | 5731.764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185407.475 | 0 | 0
Annual Sum or Average | 6787890000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 482993000000 | 351797.222 |  | 101872.638 | 41401.92 | 27030.675 | 0 | 5731.764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175666.487 | 0 | 0
Maximum of Months | 640651000000 | 432322.423 |  | 101872.638 | 41401.92 | 27030.675 | 0 | 54017.909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208413.558 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 232697.12 | 11118.97 | 0 | 243816.09
Cost per Total Building Area ($/m2) | 55.66 | 2.66 | 0 | 58.32
Cost per Net Conditioned Building Area ($/m2) | 55.66 | 2.66 | 0 | 58.32

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 8912.63 | 2131.8 | 2131.8
Net Site Energy | 8912.63 | 2131.8 | 2131.8
Total Source Energy | 27447.77 | 6565.2 | 6565.2
Net Source Energy | 27447.77 | 6565.2 | 6565.2
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1566.6 | 0 | 0 | 0 | 0
Cooling | 491.13 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1512.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 77.26 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 942.58 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 18.06 | 0 | 0 | 0 | 87.12
Refrigeration | 3319.54 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7128.84 | 1783.79 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 29.94 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 29.94 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 11.9 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 21.36 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 29.94 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 29.94 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 174.7 | 174.7 | 5.835 | 0.54 | 0.384 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12664.85 | 9873.92 | 2790.94 | 0.78 | 3.58
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 74774.97 | 55453.37 | 19321.6 | 0.74 | 3.62
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 63767.44 | 43112.1 | 20655.35 | 0.68 | 3.1
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 299623.69 | 202570.55 | 97053.14 | 0.68 | 3.09
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 101631.42 | 68852.26 | 32779.15 | 0.68 | 3.33
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 44983.05 | 35322.47 | 9660.59 | 0.79 | 3.32
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 16914.34 | 0.78
PSZ-AC:2_HEATC | Coil:Heating:Gas | 94274.92 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 119704.71 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 344853.06 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 114528.31 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 64531.52 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.73 | 841.51 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.82 | 7279.13 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.57 | 2808.34 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 12.07 | 20443.07 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.12 | 7850.72 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.62 | 2863.41 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.72 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 138298.1264 | 210.5528 | 799.6164 | 0 | 0.0015 | 3987340 | 56701.7064
February | 118660.1256 | 185.7104 | 733.5921 | 0 | 0.0014 | 3658310 | 49175.6705
March | 131364.4474 | 206.1639 | 817.4952 | 0 | 0.0016 | 4076750 | 54499.9382
April | 125578.5081 | 202.9588 | 836.7133 | 0 | 0.0016 | 4172810 | 52710.1682
May | 136845.6098 | 222.3918 | 923.2816 | 0 | 0.0017 | 4604590 | 57566.542
June | 150030.1945 | 245.2172 | 1025.3837 | 0 | 0.0019 | 5113840 | 63258.2548
July | 166842.1579 | 272.9045 | 1142.2497 | 0 | 0.0021 | 5696690 | 70368.5201
August | 168330.9794 | 275.2898 | 1151.9728 | 0 | 0.0022 | 5745180 | 70991.261
September | 145669.3905 | 237.9139 | 993.9284 | 0 | 0.0019 | 4956960 | 61401.3187
October | 132424.7595 | 214.2982 | 884.9093 | 0 | 0.0017 | 4413180 | 55612.3383
November | 125097.3118 | 197.1503 | 786.221 | 0 | 0.0015 | 3920820 | 51985.2985
December | 135683.8418 | 208.0073 | 797.985 | 0 | 0.0015 | 3979260 | 55778.9653
Annual Sum or Average | 1674830 | 2678.5588 | 10893.3485 | 0 | 0.0206 | 54325700 | 700049.982
Minimum of Months | 118660.1256 | 185.7104 | 733.5921 | 0 | 0.0014 | 3658310 | 49175.6705
Maximum of Months | 168330.9794 | 275.2898 | 1151.9728 | 0 | 0.0022 | 5745180 | 70991.261
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 523234000000 | 353240.599 | 23-JAN-11:15 | 101872.638 | 41401.92 | 42217.086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167748.955 | 0 | 0
February | 480059000000 | 363247.472 | 11-FEB-11:15 | 101872.638 | 41401.92 | 42217.086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177755.829 | 0 | 0
March | 534967000000 | 353494.738 | 11-MAR-11:15 | 101872.638 | 41401.92 | 42217.086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168003.094 | 0 | 0
April | 547574000000 | 416245.366 | 21-APR-17:15 | 67915.092 | 36859.929 | 42217.086 | 0 | 55203.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214050.029 | 0 | 0
May | 604233000000 | 435336.001 | 31-MAY-17:15 | 67915.092 | 36859.929 | 42217.086 | 0 | 77274.046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211069.849 | 0 | 0
June | 671059000000 | 497575.93 | 28-JUN-10:45 | 101872.638 | 41401.92 | 42217.086 | 0 | 111849.365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200234.92 | 0 | 0
July | 747542000000 | 509992.093 | 11-JUL-10:45 | 101872.638 | 41401.92 | 42217.086 | 0 | 108179.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216321.328 | 0 | 0
August | 753905000000 | 528002.833 | 05-AUG-10:45 | 101872.638 | 41401.92 | 42217.086 | 0 | 119945.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222565.917 | 0 | 0
September | 650472000000 | 481317.71 | 01-SEP-10:45 | 101872.638 | 41401.92 | 42217.086 | 0 | 92423.211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203402.856 | 0 | 0
October | 579116000000 | 431726.161 | 06-OCT-10:45 | 101872.638 | 41401.92 | 42217.086 | 0 | 46210.725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200023.793 | 0 | 0
November | 514506000000 | 356429.989 | 01-NOV-10:15 | 101872.638 | 41401.92 | 42217.086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170938.345 | 0 | 0
December | 522175000000 | 351928.625 | 05-DEC-11:45 | 101872.638 | 41401.92 | 42217.086 | 0 | 1519.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164917.661 | 0 | 0
Annual Sum or Average | 7128840000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 480059000000 | 351928.625 |  | 67915.092 | 36859.929 | 42217.086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164917.661 | 0 | 0
Maximum of Months | 753905000000 | 528002.833 |  | 101872.638 | 41401.92 | 42217.086 | 0 | 119945.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222565.917 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 185112.09 | 13810.37 | 0 | 198922.46
Cost per Total Building Area ($/m2) | 44.28 | 3.3 | 0 | 47.58
Cost per Net Conditioned Building Area ($/m2) | 44.28 | 3.3 | 0 | 47.58

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 8995.73 | 2151.68 | 2151.68
Net Site Energy | 8995.73 | 2151.68 | 2151.68
Total Source Energy | 22711.65 | 5432.38 | 5432.38
Net Source Energy | 22711.65 | 5432.38 | 5432.38
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2341.13 | 0 | 0 | 0 | 0
Cooling | 18.75 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1512.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 77.18 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 602.27 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 20.98 | 0 | 0 | 0 | 87.12
Refrigeration | 3437.97 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6434.5 | 2561.23 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 29.94 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 29.94 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 11.9 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 21.36 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 29.94 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 29.94 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 174.7 | 174.7 | 5.835 | 0.54 | 0.384 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9095.92 | 7241.84 | 1854.08 | 0.8 | 3.62
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 53033.57 | 40784.59 | 12248.98 | 0.77 | 3.29
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 37908.01 | 28018.47 | 9889.54 | 0.74 | 3.41
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 190354.55 | 140284.39 | 50070.15 | 0.74 | 3.45
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 50895.34 | 40647.83 | 10247.51 | 0.8 | 3.35
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 30260.94 | 24168.06 | 6092.88 | 0.8 | 3.56
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 13791.94 | 0.78
PSZ-AC:2_HEATC | Coil:Heating:Gas | 79433.25 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 85417.79 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 295031.48 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 94987.82 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 49807.69 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.55 | 633.03 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.95 | 3221.42 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.92 | 2098.86 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.59 | 1017.59 | 9.57 | 16463.42 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.07 | 3362.45 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.83 | 1999.22 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.72 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 65284.8228 | 56.9363 | 417.9191 | 0 | 0.0002 | 2521020 | 23870.2418
February | 54533.1478 | 47.3484 | 386.8534 | 0 | 0.0002 | 2333810 | 20054.2888
March | 60636.5659 | 52.6759 | 425.1172 | 0 | 0.0002 | 2564620 | 22283.4333
April | 56405.0647 | 48.8859 | 415.8473 | 0 | 0.0002 | 2508790 | 20790.6214
May | 56831.5222 | 49.1139 | 444.3364 | 0 | 0.0002 | 2680770 | 21025.1383
June | 54280.7145 | 46.8263 | 439.2664 | 0 | 0.0002 | 2650240 | 20126.831
July | 54951.4896 | 47.3269 | 458.6708 | 0 | 0.0002 | 2767370 | 20418.1895
August | 56061.9227 | 48.2783 | 468.831 | 0 | 0.0002 | 2828670 | 20833.5106
September | 53927.0409 | 46.4286 | 452.973 | 0 | 0.0002 | 2733000 | 20046.2423
October | 56359.2147 | 48.6445 | 451.5989 | 0 | 0.0002 | 2724630 | 20883.8293
November | 57333.7939 | 49.7055 | 420.0625 | 0 | 0.0002 | 2534210 | 21124.9166
December | 64513.2405 | 56.2229 | 420.2205 | 0 | 0.0002 | 2534940 | 23610.2171
Annual Sum or Average | 691118.5401 | 598.3933 | 5201.6966 | 0 | 0.0026 | 31382100 | 255067.4599
Minimum of Months | 53927.0409 | 46.4286 | 386.8534 | 0 | 0.0002 | 2333810 | 20046.2423
Maximum of Months | 65284.8228 | 56.9363 | 468.831 | 0 | 0.0002 | 2828670 | 23870.2418
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 516904000000 | 350147.009 | 05-JAN-11:15 | 101872.638 | 41401.92 | 27909.326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178963.124 | 0 | 0
February | 478518000000 | 349933.46 | 15-FEB-18:15 | 67915.092 | 36859.929 | 27909.326 | 0 | 451.292 | 4916 | 0 | 0 | 0 | 0 | 0 | 0 | 211881.82 | 0 | 0
March | 525844000000 | 348274.285 | 30-MAR-10:15 | 101872.638 | 41401.92 | 27909.326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177090.4 | 0 | 0
April | 514396000000 | 360057.018 | 29-APR-10:45 | 101872.638 | 41401.92 | 27909.326 | 0 | 4933.728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183939.406 | 0 | 0
May | 549659000000 | 362898.755 | 17-MAY-10:45 | 101872.638 | 41401.92 | 27909.326 | 0 | 3756.999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187957.872 | 0 | 0
June | 543399000000 | 379069.643 | 16-JUN-10:45 | 101872.638 | 41401.92 | 27909.326 | 0 | 13110.173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194775.586 | 0 | 0
July | 567414000000 | 402268.29 | 03-JUL-10:45 | 101872.638 | 41401.92 | 27909.326 | 0 | 26739.299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204345.106 | 0 | 0
August | 579984000000 | 388425.573 | 15-AUG-10:45 | 101872.638 | 41401.92 | 27909.326 | 0 | 13856.515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203385.174 | 0 | 0
September | 560368000000 | 408833.912 | 29-SEP-10:45 | 101872.638 | 41401.92 | 27909.326 | 0 | 29836.883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207813.144 | 0 | 0
October | 558652000000 | 358757.251 | 21-OCT-10:15 | 101872.638 | 41401.92 | 27909.326 | 0 | 37.495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187535.871 | 0 | 0
November | 519608000000 | 353522.571 | 24-NOV-11:15 | 101872.638 | 41401.92 | 27909.326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182338.687 | 0 | 0
December | 519758000000 | 347625.63 | 04-DEC-11:15 | 101872.638 | 41401.92 | 27909.326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176441.746 | 0 | 0
Annual Sum or Average | 6434500000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 478518000000 | 347625.63 |  | 67915.092 | 36859.929 | 27909.326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176441.746 | 0 | 0
Maximum of Months | 579984000000 | 408833.912 |  | 101872.638 | 41401.92 | 27909.326 | 0 | 29836.883 | 4916 | 0 | 0 | 0 | 0 | 0 | 0 | 211881.82 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 258170.71 | 21780.89 | 0 | 279951.59
Cost per Total Building Area ($/m2) | 61.75 | 5.21 | 0 | 66.96
Cost per Net Conditioned Building Area ($/m2) | 61.75 | 5.21 | 0 | 66.96

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 10696.97 | 2558.6 | 2558.6
Net Site Energy | 10696.97 | 2558.6 | 2558.6
Total Source Energy | 29729.75 | 7111.03 | 7111.03
Net Source Energy | 29729.75 | 7111.03 | 7111.03
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 3210.66 | 0 | 0 | 0 | 0
Cooling | 309.63 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1512.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 77.26 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1107.43 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 21.21 | 0 | 0 | 0 | 87.12
Refrigeration | 3473.32 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7265.97 | 3431 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 29.94 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 29.94 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 11.9 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 21.36 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 29.94 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 29.94 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 174.7 | 174.7 | 5.835 | 0.54 | 0.384 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 20059.3 | 14016.28 | 6043.03 | 0.7 | 3.35
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 115121.24 | 77831.54 | 37289.7 | 0.68 | 3.33
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 58359.24 | 39455.7 | 18903.54 | 0.68 | 3.1
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 343269.61 | 232078.82 | 111190.79 | 0.68 | 3.09
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 115845.1 | 78320.93 | 37524.17 | 0.68 | 3.33
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 50125.07 | 36121.28 | 14003.79 | 0.72 | 3.19
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 22264.83 | 0.78
PSZ-AC:2_HEATC | Coil:Heating:Gas | 125887.3 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 144239.05 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 450533.26 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 149388.97 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 67586.98 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.88 | 1005.31 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.64 | 8842.72 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.35 | 2570.16 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 13.82 | 23421 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.67 | 8898.32 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.39 | 2608.71 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.72 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 130015.2947 | 216.4688 | 544.1662 | 0 | 0.0023 | 33831.8133 | 54000.8662
February | 113349.3052 | 191.894 | 491.9337 | 0 | 0.002 | 30585.7672 | 47368.9285
March | 114962.2255 | 206.2959 | 563.3777 | 0 | 0.0023 | 35032.5235 | 49110.1635
April | 103658.0777 | 193.2317 | 547.8505 | 0 | 0.0022 | 34069.5979 | 44941.4333
May | 109206.5971 | 212.8821 | 628.566 | 0 | 0.0025 | 39092.2302 | 48198.0484
June | 118741.2613 | 235.7808 | 707.2556 | 0 | 0.0029 | 43987.4724 | 52800.4479
July | 127518.3368 | 253.7511 | 762.5267 | 0 | 0.0031 | 47425.197 | 56752.8878
August | 128522.1779 | 255.6714 | 768.1028 | 0 | 0.0031 | 47771.9768 | 57192.5888
September | 111068.0617 | 219.5703 | 656.1739 | 0 | 0.0026 | 40810.1777 | 49299.3611
October | 108714.8914 | 207.432 | 600.9353 | 0 | 0.0024 | 37372.4179 | 47570.3371
November | 110134.2408 | 200.2416 | 554.1256 | 0 | 0.0023 | 34458.1402 | 47286.3103
December | 124273.5562 | 211.1579 | 543.5948 | 0 | 0.0023 | 33798.0848 | 52004.5779
Annual Sum or Average | 1400160 | 2604.3775 | 7368.6088 | 0 | 0.03 | 458235.3988 | 606525.9507
Minimum of Months | 103658.0777 | 191.894 | 491.9337 | 0 | 0.002 | 30585.7672 | 44941.4333
Maximum of Months | 130015.2947 | 255.6714 | 768.1028 | 0 | 0.0031 | 47771.9768 | 57192.5888
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 536451000000 | 371121.08 | 09-JAN-11:15 | 101872.638 | 41401.92 | 47477.127 | 0 | 2359.723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178009.671 | 0 | 0
February | 484980000000 | 360480.626 | 13-FEB-11:15 | 101872.638 | 41401.92 | 47477.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169728.941 | 0 | 0
March | 555490000000 | 391992.588 | 09-MAR-18:15 | 67915.092 | 36859.929 | 47477.127 | 0 | 10492.184 | 4916 | 0 | 0 | 0 | 0 | 0 | 0 | 224332.256 | 0 | 0
April | 540221000000 | 392270.46 | 04-APR-17:15 | 67915.092 | 36859.929 | 47477.127 | 0 | 16108.396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223909.916 | 0 | 0
May | 619862000000 | 434711.659 | 15-MAY-17:15 | 67915.092 | 36859.929 | 47477.127 | 0 | 45160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 237299.511 | 0 | 0
June | 697483000000 | 518677.533 | 30-JUN-17:15 | 67915.092 | 36859.929 | 47477.127 | 0 | 120600.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245824.646 | 0 | 0
July | 751993000000 | 551819.493 | 25-JUL-10:00 | 101872.638 | 41401.92 | 47477.127 | 0 | 137106.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223960.897 | 0 | 0
August | 757492000000 | 522968.792 | 17-AUG-10:00 | 101872.638 | 41401.92 | 47477.127 | 0 | 113548.752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218668.354 | 0 | 0
September | 647103000000 | 465160.372 | 09-SEP-10:45 | 101872.638 | 41401.92 | 47477.127 | 0 | 62541.795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211866.892 | 0 | 0
October | 592592000000 | 424952.07 | 03-OCT-10:00 | 101872.638 | 41401.92 | 47477.127 | 0 | 30843.687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203356.698 | 0 | 0
November | 546382000000 | 407489.884 | 04-NOV-10:45 | 101872.638 | 41401.92 | 47477.127 | 0 | 17183.272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199554.927 | 0 | 0
December | 535916000000 | 371274.222 | 23-DEC-11:15 | 101872.638 | 41401.92 | 47477.127 | 0 | 1377.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179145.465 | 0 | 0
Annual Sum or Average | 7265970000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 484980000000 | 360480.626 |  | 67915.092 | 36859.929 | 47477.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169728.941 | 0 | 0
Maximum of Months | 757492000000 | 551819.493 |  | 101872.638 | 41401.92 | 47477.127 | 0 | 137106.911 | 4916 | 0 | 0 | 0 | 0 | 0 | 0 | 245824.646 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 141850.69 | 33318.74 | 0 | 175169.43
Cost per Total Building Area ($/m2) | 33.93 | 7.97 | 0 | 41.9
Cost per Net Conditioned Building Area ($/m2) | 33.93 | 7.97 | 0 | 41.9

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 9632.44 | 2303.97 | 2303.97
Net Site Energy | 9632.44 | 2303.97 | 2303.97
Total Source Energy | 26020.94 | 6223.92 | 6223.92
Net Source Energy | 26020.94 | 6223.92 | 6223.92
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2448.18 | 0 | 0 | 0 | 0
Cooling | 220.52 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1512.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 77.25 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1187.6 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 20.93 | 0 | 0 | 0 | 87.12
Refrigeration | 3180.51 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6964.2 | 2668.24 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 29.94 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 29.94 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 11.9 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 21.36 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 29.94 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 29.94 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 174.7 | 174.7 | 5.835 | 0.54 | 0.384 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 15298.69 | 12218.38 | 3080.31 | 0.8 | 3.61
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 81293.39 | 64678.18 | 16615.21 | 0.8 | 3.91
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 59232.66 | 41100.43 | 18132.23 | 0.69 | 3.14
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 354277.19 | 244415.98 | 109861.2 | 0.69 | 3.13
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 103854.28 | 74755.24 | 29099.04 | 0.72 | 3.51
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 42584.59 | 34010.41 | 8574.18 | 0.8 | 3.35
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 19115.1 | 0.78
PSZ-AC:2_HEATC | Coil:Heating:Gas | 107702.7 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 124768.35 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 389232.3 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 126497.36 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 58882.02 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.92 | 1052.84 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.87 | 9289.79 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.56 | 2798.07 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 15.07 | 25534.79 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.93 | 9400.52 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.57 | 2813.39 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.72 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 169711.2193 | 274.8555 | 654.5946 | 0 | 0.0026 | 680532.7517 | 70587.2269
February | 148938.0796 | 244.5601 | 592.59 | 0 | 0.0023 | 616096.4 | 62275.5259
March | 161567.2849 | 268.834 | 661.9794 | 0 | 0.0026 | 688263.982 | 67903.0607
April | 149433.8279 | 254.2605 | 642.6599 | 0 | 0.0025 | 668217.1039 | 63354.4692
May | 159405.4572 | 276.0588 | 711.6956 | 0 | 0.0028 | 740030.837 | 68056.0107
June | 168771.7689 | 294.5586 | 765.8496 | 0 | 0.003 | 796355.6825 | 72278.3991
July | 186949.8535 | 327.0501 | 852.4788 | 0 | 0.0033 | 886440.5112 | 80138.4144
August | 185950.2674 | 325.1103 | 846.8868 | 0 | 0.0033 | 880624.4223 | 79691.1894
September | 166034.5689 | 289.5163 | 751.9942 | 0 | 0.0029 | 781946.6366 | 71080.1632
October | 157067.6106 | 268.2917 | 681.132 | 0 | 0.0027 | 708226.238 | 66693.1631
November | 156127.9443 | 258.4052 | 632.2335 | 0 | 0.0025 | 657327.2833 | 65481.8411
December | 170392.4274 | 275.4 | 654.1978 | 0 | 0.0026 | 680116.0565 | 70815.7507
Annual Sum or Average | 1980350 | 3356.9011 | 8448.2922 | 0 | 0.0332 | 8784180 | 838355.2144
Minimum of Months | 148938.0796 | 244.5601 | 592.59 | 0 | 0.0023 | 616096.4 | 62275.5259
Maximum of Months | 186949.8535 | 327.0501 | 852.4788 | 0 | 0.0033 | 886440.5112 | 80138.4144
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 539535000000 | 354787.275 | 02-JAN-11:15 | 101872.638 | 41401.92 | 51020.314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160492.402 | 0 | 0
February | 488449000000 | 356410.712 | 17-FEB-11:15 | 101872.638 | 41401.92 | 51020.314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162115.84 | 0 | 0
March | 545664000000 | 360047.719 | 08-MAR-11:15 | 101872.638 | 41401.92 | 51020.314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165752.847 | 0 | 0
April | 529771000000 | 378030.85 | 21-APR-17:15 | 67915.092 | 36859.929 | 51020.314 | 0 | 21025.858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201209.657 | 0 | 0
May | 586705000000 | 409349.2 | 31-MAY-17:15 | 67915.092 | 36859.929 | 51020.314 | 0 | 44634.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208919.702 | 0 | 0
June | 631360000000 | 443699.245 | 29-JUN-10:45 | 101872.638 | 41401.92 | 51020.314 | 0 | 49949.633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199454.739 | 0 | 0
July | 702781000000 | 453584.574 | 03-JUL-10:45 | 101872.638 | 41401.92 | 51020.314 | 0 | 56924.667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202365.035 | 0 | 0
August | 698170000000 | 471370.101 | 01-AUG-10:45 | 101872.638 | 41401.92 | 51020.314 | 0 | 66960.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210115.15 | 0 | 0
September | 619937000000 | 417118.195 | 12-SEP-10:45 | 101872.638 | 41401.92 | 51020.314 | 0 | 30454.829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192368.493 | 0 | 0
October | 561490000000 | 393789.364 | 03-OCT-10:45 | 101872.638 | 41401.92 | 51020.314 | 0 | 14802.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184691.581 | 0 | 0
November | 521137000000 | 362510.12 | 10-NOV-11:15 | 101872.638 | 41401.92 | 51020.314 | 0 | 32.654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168182.593 | 0 | 0
December | 539204000000 | 353667.629 | 22-DEC-11:15 | 101872.638 | 41401.92 | 51020.314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159372.756 | 0 | 0
Annual Sum or Average | 6964200000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 488449000000 | 353667.629 |  | 67915.092 | 36859.929 | 51020.314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159372.756 | 0 | 0
Maximum of Months | 702781000000 | 471370.101 |  | 101872.638 | 41401.92 | 51020.314 | 0 | 66960.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210115.15 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 71629.36 | 18489.95 | 0 | 90119.3
Cost per Total Building Area ($/m2) | 17.13 | 4.42 | 0 | 21.56
Cost per Net Conditioned Building Area ($/m2) | 17.13 | 4.42 | 0 | 21.56

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 10115.48 | 2419.51 | 2419.51
Net Site Energy | 10115.48 | 2419.51 | 2419.51
Total Source Energy | 15331.35 | 3667.09 | 3667.09
Net Source Energy | 15331.35 | 3667.09 | 3667.09
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 3301.68 | 0 | 0 | 0 | 0
Cooling | 31.32 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1512.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 77.13 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 921.82 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 21.99 | 0 | 0 | 0 | 87.12
Refrigeration | 3264.09 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6592.69 | 3522.79 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 29.94 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 29.94 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 11.9 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 21.36 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 29.94 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 29.94 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 174.7 | 174.7 | 5.835 | 0.54 | 0.384 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11914.98 | 9470.5 | 2444.47 | 0.79 | 3.62
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 68907.42 | 52725.83 | 16181.59 | 0.77 | 3.96
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 46386.19 | 32618.31 | 13767.89 | 0.7 | 3.15
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 267725.89 | 187280.8 | 80445.09 | 0.7 | 3.17
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 64507.58 | 51519.31 | 12988.26 | 0.8 | 4.17
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 35409.35 | 28279.86 | 7129.49 | 0.8 | 3.56
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 17902.45 | 0.78
PSZ-AC:2_HEATC | Coil:Heating:Gas | 101401.7 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 110113.68 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 373871.24 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 122737.47 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 58828.47 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.71 | 826.22 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.78 | 7216.87 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.07 | 2268.81 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 11.81 | 20013.85 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.9 | 7433.07 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.14 | 2339.35 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.72 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 54290.8359 | 67.0806 | 113.8761 | 0 | 0.0005 | 1503300 | 20696.5079
February | 44402.5473 | 56.3631 | 102.714 | 0 | 0.0004 | 1356260 | 17087.6159
March | 47686.6899 | 61.3621 | 115.6118 | 0 | 0.0005 | 1526720 | 18440.3832
April | 41307.3573 | 55.039 | 112.1858 | 0 | 0.0005 | 1481820 | 16175.4668
May | 36995.6036 | 52.4908 | 120.8871 | 0 | 0.0005 | 1597260 | 14829.425
June | 33416.0417 | 49.193 | 120.5618 | 0 | 0.0005 | 1593200 | 13585.3276
July | 33083.3748 | 50.1803 | 128.7925 | 0 | 0.0005 | 1702150 | 13608.2798
August | 33085.6657 | 50.8233 | 132.8847 | 0 | 0.0005 | 1756300 | 13677.7163
September | 34481.3263 | 50.4645 | 122.5105 | 0 | 0.0005 | 1618920 | 13986.6376
October | 40322.0155 | 55.342 | 119.8268 | 0 | 0.0005 | 1583000 | 15962.6805
November | 47285.3547 | 60.4079 | 111.8436 | 0 | 0.0005 | 1476880 | 18238.2996
December | 54025.2858 | 66.9688 | 114.6999 | 0 | 0.0005 | 1514220 | 20618.438
Annual Sum or Average | 500382.0985 | 675.7155 | 1416.3946 | 0 | 0.0059 | 18710100 | 196906.7782
Minimum of Months | 33083.3748 | 49.193 | 102.714 | 0 | 0.0004 | 1356260 | 13585.3276
Maximum of Months | 54290.8359 | 67.0806 | 132.8847 | 0 | 0.0005 | 1756300 | 20696.5079
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 529706000000 | 359493.454 | 14-JAN-11:15 | 101872.638 | 41401.92 | 40229.092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175989.804 | 0 | 0
February | 477893000000 | 350370.641 | 21-FEB-11:15 | 101872.638 | 41401.92 | 40229.092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166866.991 | 0 | 0
March | 537958000000 | 360067.349 | 30-MAR-10:15 | 101872.638 | 41401.92 | 40229.092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176563.699 | 0 | 0
April | 522135000000 | 365255.47 | 29-APR-10:15 | 101872.638 | 41401.92 | 40229.092 | 0 | 41.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181710.489 | 0 | 0
May | 562813000000 | 378335.357 | 05-MAY-17:15 | 67915.092 | 36859.929 | 40229.092 | 0 | 10346.126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222985.118 | 0 | 0
June | 561382000000 | 391949.39 | 28-JUN-10:45 | 101872.638 | 41401.92 | 40229.092 | 0 | 14667.782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193777.957 | 0 | 0
July | 599770000000 | 410684.27 | 31-JUL-17:15 | 67915.092 | 36859.929 | 40229.092 | 0 | 38061.448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227618.709 | 0 | 0
August | 618852000000 | 405473.78 | 18-AUG-17:15 | 67915.092 | 36859.929 | 40229.092 | 0 | 33653.317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226816.35 | 0 | 0
September | 570443000000 | 425284.449 | 02-SEP-14:00 | 101872.638 | 41401.92 | 40229.092 | 0 | 81728.347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160052.452 | 0 | 0
October | 557789000000 | 365397.205 | 05-OCT-10:15 | 101872.638 | 41401.92 | 40229.092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181893.554 | 0 | 0
November | 520396000000 | 366602.578 | 03-NOV-10:15 | 101872.638 | 41401.92 | 40229.092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183098.928 | 0 | 0
December | 533553000000 | 353629.649 | 05-DEC-11:15 | 101872.638 | 41401.92 | 40229.092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170125.999 | 0 | 0
Annual Sum or Average | 6592690000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 477893000000 | 350370.641 |  | 67915.092 | 36859.929 | 40229.092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160052.452 | 0 | 0
Maximum of Months | 618852000000 | 425284.449 |  | 101872.638 | 41401.92 | 40229.092 | 0 | 81728.347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227618.709 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 130311.75 | 29531.62 | 0 | 159843.37
Cost per Total Building Area ($/m2) | 31.17 | 7.06 | 0 | 38.23
Cost per Net Conditioned Building Area ($/m2) | 31.17 | 7.06 | 0 | 38.23

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 11507.64 | 2752.5 | 2752.5
Net Site Energy | 11507.64 | 2752.5 | 2752.5
Total Source Energy | 30276.95 | 7241.91 | 7241.91
Net Source Energy | 30276.95 | 7241.91 | 7241.91
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 4068.95 | 0 | 0 | 0 | 0
Cooling | 191.22 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1512.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 77.15 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1322.76 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 22.52 | 0 | 0 | 0 | 87.12
Refrigeration | 3327.57 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7217.04 | 4290.6 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 29.94 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 29.94 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 11.9 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 21.36 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 29.94 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 29.94 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 174.7 | 174.7 | 3.525 | 0.407 | 0.316 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 25753.97 | 17825.57 | 7928.4 | 0.69 | 3.33
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 144497.07 | 97692.04 | 46805.02 | 0.68 | 3.31
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 53537.03 | 36195.49 | 17341.54 | 0.68 | 3.1
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 407827.34 | 275725.22 | 132102.12 | 0.68 | 3.09
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 144450.43 | 97660.51 | 46789.92 | 0.68 | 3.31
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 37456.89 | 29080.95 | 8375.94 | 0.78 | 3.5
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 27507.77 | 0.78
PSZ-AC:2_HEATC | Coil:Heating:Gas | 155314.12 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 154577.79 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 541063.33 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 185478.47 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 63745.9 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.11 | 1258.92 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.82 | 10916.19 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.16 | 2357.79 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 16.42 | 27646.19 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.82 | 10912.67 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.13 | 2324.73 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.72 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 235381.0371 | 385.8144 | 1033.0188 | 0 | 0.0032 | 237757.1334 | 97925.8912
February | 206852.3645 | 343.4431 | 934.1328 | 0 | 0.0029 | 215004.8792 | 86476.8185
March | 221980.657 | 376.1537 | 1047.967 | 0 | 0.0032 | 241217.4833 | 93527.2958
April | 203412.5246 | 355.4365 | 1024.7336 | 0 | 0.0031 | 235885.8708 | 86731.5134
May | 215200.7562 | 385.8513 | 1142.9662 | 0 | 0.0035 | 263115.9751 | 92696.3642
June | 231367.0987 | 419.5289 | 1256.9529 | 0 | 0.0038 | 289362.4974 | 100108.4763
July | 253147.832 | 459.8561 | 1380.2755 | 0 | 0.0042 | 317753.6162 | 109612.2655
August | 247933.1233 | 450.2116 | 1350.8133 | 0 | 0.0041 | 310970.8888 | 107337.8959
September | 220170.0287 | 398.1504 | 1189.6767 | 0 | 0.0036 | 273873.4842 | 95160.8996
October | 211900.2246 | 374.8929 | 1095.2193 | 0 | 0.0033 | 252117.6869 | 90792.7434
November | 211334.1426 | 361.9247 | 1020.5565 | 0 | 0.0031 | 234913.9723 | 89406.0529
December | 230922.3542 | 382.1228 | 1035.1319 | 0 | 0.0032 | 238249.3242 | 96416.7307
Annual Sum or Average | 2689600 | 4693.3863 | 13511.4445 | 0 | 0.0412 | 3110220 | 1146190
Minimum of Months | 203412.5246 | 343.4431 | 934.1328 | 0 | 0.0029 | 215004.8792 | 86476.8185
Maximum of Months | 253147.832 | 459.8561 | 1380.2755 | 0 | 0.0042 | 317753.6162 | 109612.2655
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 551698000000 | 360946.42 | 18-JAN-11:15 | 101872.638 | 41401.92 | 55547.402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162124.46 | 0 | 0
February | 498903000000 | 362562.384 | 28-FEB-11:15 | 101872.638 | 41401.92 | 55547.402 | 0 | 334.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163405.513 | 0 | 0
March | 559727000000 | 375377.058 | 14-MAR-17:15 | 67915.092 | 36859.929 | 55547.402 | 0 | 2231.883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212822.752 | 0 | 0
April | 547355000000 | 389697.661 | 10-APR-10:15 | 101872.638 | 41401.92 | 55547.402 | 0 | 2463.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188412.576 | 0 | 0
May | 610541000000 | 439939.24 | 30-MAY-17:15 | 67915.092 | 36859.929 | 55547.402 | 0 | 41798.305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 237818.512 | 0 | 0
June | 671444000000 | 504090.736 | 08-JUN-12:00 | 101872.638 | 41401.92 | 55547.402 | 0 | 114273.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190995.641 | 0 | 0
July | 737323000000 | 531979.46 | 14-JUL-10:00 | 101872.638 | 41401.92 | 55547.402 | 0 | 112935.667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220221.834 | 0 | 0
August | 721585000000 | 508883.597 | 04-AUG-17:15 | 67915.092 | 36859.929 | 55547.402 | 0 | 104377.863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244183.311 | 0 | 0
September | 635503000000 | 467167.221 | 06-SEP-10:45 | 101872.638 | 41401.92 | 55547.402 | 0 | 55430.207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212915.055 | 0 | 0
October | 585020000000 | 405760.545 | 31-OCT-10:45 | 101872.638 | 41401.92 | 55547.402 | 0 | 11053.084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195885.501 | 0 | 0
November | 545100000000 | 405016.238 | 02-NOV-10:45 | 101872.638 | 41401.92 | 55547.402 | 0 | 10043.563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196150.715 | 0 | 0
December | 552840000000 | 365003.98 | 12-DEC-11:15 | 101872.638 | 41401.92 | 55547.402 | 0 | 258.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165923.979 | 0 | 0
Annual Sum or Average | 7217040000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 498903000000 | 360946.42 |  | 67915.092 | 36859.929 | 55547.402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162124.46 | 0 | 0
Maximum of Months | 737323000000 | 531979.46 |  | 101872.638 | 41401.92 | 55547.402 | 0 | 114273.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244183.311 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 192402.25 | 35978.52 | 0 | 228380.77
Cost per Total Building Area ($/m2) | 46.02 | 8.61 | 0 | 54.63
Cost per Net Conditioned Building Area ($/m2) | 46.02 | 8.61 | 0 | 54.63

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 10429.44 | 2494.61 | 2494.61
Net Site Energy | 10429.44 | 2494.61 | 2494.61
Total Source Energy | 26885.15 | 6430.63 | 6430.63
Net Source Energy | 26885.15 | 6430.63 | 6430.63
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 3246.4 | 0 | 0 | 0 | 0
Cooling | 120.77 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1512.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 77.17 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1407.5 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 22.45 | 0 | 0 | 0 | 87.12
Refrigeration | 3057.69 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6961.46 | 3467.98 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 29.94 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 29.94 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 11.9 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 21.36 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 29.94 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 29.94 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 174.7 | 174.7 | 3.525 | 0.407 | 0.316 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 18992.04 | 15168.1 | 3823.95 | 0.8 | 3.61
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 109765.4 | 84118.96 | 25646.44 | 0.77 | 3.71
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 55690.6 | 38595.77 | 17094.83 | 0.69 | 3.13
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 404905.86 | 281489.03 | 123416.83 | 0.7 | 3.15
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 100709.08 | 80431.83 | 20277.24 | 0.8 | 3.89
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 40113.63 | 32036.96 | 8076.67 | 0.8 | 3.35
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 23806.73 | 0.78
PSZ-AC:2_HEATC | Coil:Heating:Gas | 133857.56 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 139582.67 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 469137.6 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 158755.52 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 58585.61 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.15 | 1307.01 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.05 | 11346.59 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.4 | 2622.32 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 17.58 | 29588.72 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.08 | 11413.21 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.42 | 2650.15 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.72 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 179708.491 | 287.9484 | 676.3866 | 0 | 0.0027 | 703165.0047 | 74441.4556
February | 158821.1855 | 256.9312 | 611.0351 | 0 | 0.0024 | 635245.0623 | 66029.5949
March | 171367.0601 | 281.8818 | 684.4965 | 0 | 0.0027 | 711652.107 | 71702.0912
April | 157128.0282 | 264.4718 | 660.1603 | 0 | 0.0026 | 686394.0365 | 66334.0034
May | 163108.0043 | 279.1929 | 710.4845 | 0 | 0.0028 | 738750.1673 | 69315.2318
June | 164290.5711 | 285.1883 | 737.1295 | 0 | 0.0029 | 766481.722 | 70207.3104
July | 182200.2384 | 318.4787 | 829.4005 | 0 | 0.0032 | 862441.0441 | 78076.6893
August | 179520.9312 | 313.3801 | 814.9565 | 0 | 0.0032 | 847419.0469 | 76887.8203
September | 158597.0663 | 273.9936 | 704.486 | 0 | 0.0028 | 732529.8691 | 67645.6301
October | 161397.6397 | 273.4061 | 687.5586 | 0 | 0.0027 | 714893.182 | 68307.9246
November | 164985.3734 | 270.6513 | 655.0376 | 0 | 0.0026 | 681019.1609 | 68959.9972
December | 180166.2228 | 287.9308 | 674.0445 | 0 | 0.0027 | 700724.3529 | 74557.3959
Annual Sum or Average | 2021290 | 3393.4551 | 8445.1761 | 0 | 0.0333 | 8780710 | 852465.1446
Minimum of Months | 157128.0282 | 256.9312 | 611.0351 | 0 | 0.0024 | 635245.0623 | 66029.5949
Maximum of Months | 182200.2384 | 318.4787 | 829.4005 | 0 | 0.0032 | 862441.0441 | 78076.6893
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 557478000000 | 365629.951 | 23-JAN-11:15 | 101872.638 | 41401.92 | 59058.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163296.49 | 0 | 0
February | 503630000000 | 361674.746 | 11-FEB-11:15 | 101872.638 | 41401.92 | 59058.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159341.285 | 0 | 0
March | 564206000000 | 369307.811 | 27-MAR-10:45 | 101872.638 | 41401.92 | 59058.903 | 0 | 797.699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166176.651 | 0 | 0
April | 544181000000 | 387469.498 | 26-APR-10:45 | 101872.638 | 41401.92 | 59058.903 | 0 | 8988.699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176147.338 | 0 | 0
May | 585690000000 | 410668.52 | 24-MAY-10:45 | 101872.638 | 41401.92 | 59058.903 | 0 | 17067.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191268.022 | 0 | 0
June | 607676000000 | 439046.185 | 28-JUN-10:45 | 101872.638 | 41401.92 | 59058.903 | 0 | 38816.421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197896.304 | 0 | 0
July | 683754000000 | 465552.641 | 19-JUL-10:45 | 101872.638 | 41401.92 | 59058.903 | 0 | 56346.266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206872.914 | 0 | 0
August | 671844000000 | 465430.638 | 30-AUG-10:45 | 101872.638 | 41401.92 | 59058.903 | 0 | 56527.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206569.546 | 0 | 0
September | 580759000000 | 421082.573 | 09-SEP-10:45 | 101872.638 | 41401.92 | 59058.903 | 0 | 22591.494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196157.618 | 0 | 0
October | 566776000000 | 389407.316 | 05-OCT-10:45 | 101872.638 | 41401.92 | 59058.903 | 0 | 11121.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175952.105 | 0 | 0
November | 539920000000 | 364793.347 | 16-NOV-11:15 | 101872.638 | 41401.92 | 59058.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162459.886 | 0 | 0
December | 555543000000 | 359834.693 | 30-DEC-11:15 | 101872.638 | 41401.92 | 59058.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157501.233 | 0 | 0
Annual Sum or Average | 6961460000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 503630000000 | 359834.693 |  | 101872.638 | 41401.92 | 59058.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157501.233 | 0 | 0
Maximum of Months | 683754000000 | 465552.641 |  | 101872.638 | 41401.92 | 59058.903 | 0 | 56527.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206872.914 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 71601.19 | 24130.18 | 0 | 95731.37
Cost per Total Building Area ($/m2) | 17.13 | 5.77 | 0 | 22.9
Cost per Net Conditioned Building Area ($/m2) | 17.13 | 5.77 | 0 | 22.9

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 12500.47 | 2989.97 | 2989.97
Net Site Energy | 12500.47 | 2989.97 | 2989.97
Total Source Energy | 30663.62 | 7334.4 | 7334.4
Net Source Energy | 30663.62 | 7334.4 | 7334.4
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 5022.63 | 0 | 0 | 0 | 0
Cooling | 156.05 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1512.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 77.21 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1465.76 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 23.65 | 0 | 0 | 0 | 87.12
Refrigeration | 3257.7 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7255.06 | 5245.41 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 29.94 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 29.94 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 11.9 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 21.36 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 29.94 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 29.94 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 174.7 | 174.7 | 3.525 | 0.407 | 0.316 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 28399.54 | 19709.58 | 8689.96 | 0.69 | 3.34
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 160499.44 | 108510.98 | 51988.46 | 0.68 | 3.31
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 54548 | 36878.99 | 17669.01 | 0.68 | 3.1
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 446525.89 | 301888.66 | 144637.23 | 0.68 | 3.09
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 160037.88 | 108198.93 | 51838.96 | 0.68 | 3.31
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 41142.56 | 32103.21 | 9039.35 | 0.78 | 3.31
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 30363.84 | 0.78
PSZ-AC:2_HEATC | Coil:Heating:Gas | 171645.93 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 170207.7 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 593802.1 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 204183.06 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 70569.78 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.23 | 1398.14 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.46 | 12125.11 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.2 | 2402.31 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 17.98 | 30269.53 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.44 | 12090.24 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.36 | 2582.36 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.72 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 185920.2496 | 282.0481 | 369.739 | 0 | 0.0028 | 242835.1848 | 75176.0755
February | 158666.8025 | 246.2838 | 333.7101 | 0 | 0.0025 | 219203.2892 | 64689.6492
March | 158036.7311 | 258.4904 | 375.3163 | 0 | 0.0028 | 246602.1438 | 65693.04
April | 138165.3195 | 237.7185 | 366.3204 | 0 | 0.0027 | 240745.8825 | 58554.1209
May | 143804.3517 | 256.872 | 412.0465 | 0 | 0.003 | 270836.3646 | 61847.3529
June | 149701.3951 | 271.4331 | 442.0575 | 0 | 0.0032 | 290577.9793 | 64768.5239
July | 159539.4581 | 289.8307 | 472.9307 | 0 | 0.0034 | 310873.9751 | 69078.4651
August | 160175.8792 | 290.9976 | 474.8523 | 0 | 0.0035 | 312137.1492 | 69355.0552
September | 139160.5283 | 249.9094 | 403.0792 | 0 | 0.0029 | 264947.3637 | 59977.5072
October | 142147.5527 | 244.8323 | 377.7325 | 0 | 0.0028 | 248246.9755 | 60266.8475
November | 151564.1962 | 248.0992 | 360.5813 | 0 | 0.0027 | 236921.4094 | 63021.206
December | 176712.0801 | 273.6161 | 369.4566 | 0 | 0.0028 | 242680.4239 | 71982.0686
Annual Sum or Average | 1863590 | 3150.1312 | 4757.8222 | 0 | 0.0352 | 3126610 | 784409.9121
Minimum of Months | 138165.3195 | 237.7185 | 333.7101 | 0 | 0.0025 | 219203.2892 | 58554.1209
Maximum of Months | 185920.2496 | 290.9976 | 474.8523 | 0 | 0.0035 | 312137.1492 | 75176.0755
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 563481000000 | 362764.221 | 30-JAN-11:15 | 101872.638 | 41401.92 | 60998.605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158491.058 | 0 | 0
February | 508645000000 | 362468.642 | 21-FEB-11:15 | 101872.638 | 41401.92 | 60998.605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158195.478 | 0 | 0
March | 572222000000 | 372899.61 | 29-MAR-10:15 | 101872.638 | 41401.92 | 60998.605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168626.447 | 0 | 0
April | 558633000000 | 383637.676 | 01-APR-17:15 | 56595.91 | 32317.938 | 60998.605 | 0 | 7109.267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226615.956 | 0 | 0
May | 628455000000 | 486685.159 | 27-MAY-14:00 | 101872.638 | 41401.92 | 60998.605 | 0 | 106574.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175837.826 | 0 | 0
June | 674264000000 | 504239.969 | 29-JUN-17:15 | 67915.092 | 36859.929 | 60998.605 | 0 | 95895.552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242570.791 | 0 | 0
July | 721360000000 | 506076.505 | 13-JUL-17:15 | 67915.092 | 36859.929 | 60998.605 | 0 | 95981.421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244321.457 | 0 | 0
August | 724291000000 | 503581.04 | 25-AUG-17:15 | 67915.092 | 36859.929 | 60998.605 | 0 | 95100.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242706.965 | 0 | 0
September | 614790000000 | 431954.812 | 14-SEP-17:15 | 67915.092 | 36859.929 | 60998.605 | 0 | 35935.275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230245.91 | 0 | 0
October | 576038000000 | 389872.65 | 14-OCT-10:15 | 101872.638 | 41401.92 | 60998.605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185599.486 | 0 | 0
November | 549758000000 | 373150.375 | 03-NOV-10:15 | 101872.638 | 41401.92 | 60998.605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168877.211 | 0 | 0
December | 563122000000 | 366330.746 | 02-DEC-11:15 | 101872.638 | 41401.92 | 60998.605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162057.583 | 0 | 0
Annual Sum or Average | 7255060000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 508645000000 | 362468.642 |  | 56595.91 | 32317.938 | 60998.605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158195.478 | 0 | 0
Maximum of Months | 724291000000 | 506076.505 |  | 101872.638 | 41401.92 | 60998.605 | 0 | 106574.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244321.457 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 111499.62 | 41267.28 | 0 | 152766.9
Cost per Total Building Area ($/m2) | 26.67 | 9.87 | 0 | 36.54
Cost per Net Conditioned Building Area ($/m2) | 26.67 | 9.87 | 0 | 36.54

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 11539.64 | 2760.16 | 2760.16
Net Site Energy | 11539.64 | 2760.16 | 2760.16
Total Source Energy | 29262.33 | 6999.23 | 6999.23
Net Source Energy | 29262.33 | 6999.23 | 6999.23
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 4327.97 | 0 | 0 | 0 | 0
Cooling | 62.91 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1512.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 77.12 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1592.16 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 23.85 | 0 | 0 | 0 | 87.12
Refrigeration | 2958.17 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6988.69 | 4550.95 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 29.94 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 29.94 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 11.9 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 21.36 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 29.94 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 29.94 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 174.7 | 174.7 | 3.525 | 0.407 | 0.316 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 21834.59 | 17438.31 | 4396.28 | 0.8 | 3.6
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 115114.87 | 91937.1 | 23177.77 | 0.8 | 3.89
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 39226.76 | 31328.65 | 7898.1 | 0.8 | 3.56
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 323355.57 | 258249.63 | 65105.94 | 0.8 | 3.52
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 115080.63 | 91909.75 | 23170.88 | 0.8 | 3.89
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 42040.23 | 33575.65 | 8464.58 | 0.8 | 3.35
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 29052.73 | 0.78
PSZ-AC:2_HEATC | Coil:Heating:Gas | 163938.32 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 167318.47 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 566364.27 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 194166.09 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 67094.48 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.32 | 1502.63 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.95 | 13045.8 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.37 | 2591.55 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.53 | 32882.63 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.95 | 13041.92 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.54 | 2777.43 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.72 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 181844.6477 | 282.7455 | 426.432 | 0 | 0.0031 | 10110800 | 74312.4949
February | 158722.5967 | 250.754 | 386.5326 | 0 | 0.0028 | 9165480 | 65246.2762
March | 161482.8094 | 264.664 | 427.7897 | 0 | 0.003 | 10145500 | 67303.9963
April | 148252.0855 | 247.518 | 409.1538 | 0 | 0.0029 | 9704290 | 62228.3221
May | 148178.2245 | 253.6705 | 431.6466 | 0 | 0.003 | 10238800 | 62803.9672
June | 147949.3707 | 258.0737 | 448.3209 | 0 | 0.0031 | 10635000 | 63170.469
July | 155453.3975 | 273.9082 | 480.9867 | 0 | 0.0033 | 11410300 | 66639.8193
August | 156301.6928 | 274.8679 | 481.6768 | 0 | 0.0033 | 11426600 | 66951.7587
September | 144376.8373 | 250.4002 | 432.2809 | 0 | 0.003 | 10254300 | 61505.7185
October | 150355.7981 | 253.4358 | 423.6593 | 0 | 0.003 | 10048700 | 63343.8753
November | 157121.3693 | 256.0723 | 411.0154 | 0 | 0.0029 | 9747450 | 65346.6748
December | 177095.604 | 278.1103 | 425.2372 | 0 | 0.003 | 10082900 | 72637.4851
Annual Sum or Average | 1887130 | 3144.2204 | 5184.7319 | 0 | 0.0364 | 122970000 | 791490.8575
Minimum of Months | 144376.8373 | 247.518 | 386.5326 | 0 | 0.0028 | 9165480 | 61505.7185
Maximum of Months | 181844.6477 | 282.7455 | 481.6768 | 0 | 0.0033 | 11426600 | 74312.4949
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 574618000000 | 368385.156 | 23-JAN-11:15 | 101872.638 | 41401.92 | 65972.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159137.718 | 0 | 0
February | 520896000000 | 373351.785 | 02-FEB-11:15 | 101872.638 | 41401.92 | 65972.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164104.347 | 0 | 0
March | 576593000000 | 370371.939 | 31-MAR-10:15 | 101872.638 | 41401.92 | 65972.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161124.5 | 0 | 0
April | 551518000000 | 376566.931 | 24-APR-10:15 | 101872.638 | 41401.92 | 65972.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167319.493 | 0 | 0
May | 581894000000 | 389896.327 | 25-MAY-17:15 | 67915.092 | 36859.929 | 65972.88 | 0 | 14066.354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205082.072 | 0 | 0
June | 604414000000 | 444321.95 | 30-JUN-10:45 | 101872.638 | 41401.92 | 65972.88 | 0 | 31767.391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203307.121 | 0 | 0
July | 648476000000 | 445656.085 | 21-JUL-17:15 | 67915.092 | 36859.929 | 65972.88 | 0 | 58074.006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216834.178 | 0 | 0
August | 649402000000 | 439312.708 | 11-AUG-17:15 | 67915.092 | 36859.929 | 65972.88 | 0 | 45367.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223196.907 | 0 | 0
September | 582777000000 | 417742.996 | 01-SEP-17:15 | 67915.092 | 36859.929 | 65972.88 | 0 | 32302.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214692.183 | 0 | 0
October | 571093000000 | 380550.982 | 06-OCT-17:15 | 67915.092 | 36859.929 | 65972.88 | 0 | 8745.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201057.181 | 0 | 0
November | 553971000000 | 369702.239 | 01-NOV-10:15 | 101872.638 | 41401.92 | 65972.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160454.801 | 0 | 0
December | 573038000000 | 366612.456 | 29-DEC-11:15 | 101872.638 | 41401.92 | 65972.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157365.017 | 0 | 0
Annual Sum or Average | 6988690000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 520896000000 | 366612.456 |  | 67915.092 | 36859.929 | 65972.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157365.017 | 0 | 0
Maximum of Months | 649402000000 | 445656.085 |  | 101872.638 | 41401.92 | 65972.88 | 0 | 58074.006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223196.907 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 136160.49 | 37373.34 | 0 | 173533.83
Cost per Total Building Area ($/m2) | 32.57 | 8.94 | 0 | 41.51
Cost per Net Conditioned Building Area ($/m2) | 32.57 | 8.94 | 0 | 41.51

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 13527.98 | 3235.74 | 3235.74
Net Site Energy | 13527.98 | 3235.74 | 3235.74
Total Source Energy | 31311.37 | 7489.34 | 7489.34
Net Source Energy | 31311.37 | 7489.34 | 7489.34
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 6250.54 | 0 | 0 | 0 | 0
Cooling | 43.65 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1512.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 77.1 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1611.48 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 25.51 | 0 | 0 | 0 | 87.12
Refrigeration | 3022.24 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7052.8 | 6475.18 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 29.94 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 29.94 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 11.9 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 21.36 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 29.94 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 29.94 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 174.7 | 174.7 | 3.525 | 0.407 | 0.316 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 28908.77 | 20425.74 | 8483.03 | 0.71 | 3.36
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 171737.85 | 116109.08 | 55628.77 | 0.68 | 3.31
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 41149.64 | 32041.74 | 9107.89 | 0.78 | 3.31
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 477068.06 | 322537.71 | 154530.35 | 0.68 | 3.09
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 171415.51 | 115891.15 | 55524.36 | 0.68 | 3.31
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 41771.23 | 33360.81 | 8410.42 | 0.8 | 3.35
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 31701.09 | 0.78
PSZ-AC:2_HEATC | Coil:Heating:Gas | 179682.14 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 186437.29 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 620288.66 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 213731.16 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 73763.8 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.31 | 1491.11 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.92 | 12974.13 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.35 | 2570.77 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.21 | 32339.95 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.9 | 12949.77 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.52 | 2759.66 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.72 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 189366.9785 | 287.0729 | 375.929 | 0 | 0.0029 | 246899.515 | 76550.2404
February | 166420.4968 | 255.2519 | 340.0302 | 0 | 0.0026 | 223338.6827 | 67557.6978
March | 170311.6589 | 270.818 | 379.2332 | 0 | 0.0029 | 249139.7968 | 70054.7371
April | 146980.7172 | 245.0271 | 364.1042 | 0 | 0.0027 | 239256.6944 | 61538.8937
May | 141753.5661 | 245.8329 | 382.1532 | 0 | 0.0028 | 251159.2804 | 60260.3155
June | 138079.8721 | 247.3292 | 397.8666 | 0 | 0.0029 | 261518.6623 | 59450.6182
July | 151448.539 | 273.9757 | 445.1808 | 0 | 0.0032 | 292628.6747 | 65464.6629
August | 149474.3887 | 268.8547 | 434.3319 | 0 | 0.0032 | 285491.6186 | 64463.1978
September | 139160.9872 | 244.7578 | 386.3033 | 0 | 0.0028 | 253900.8111 | 59485.1992
October | 146997.54 | 249.3596 | 378.1616 | 0 | 0.0028 | 248513.1468 | 61957.3786
November | 159454.9434 | 257.0347 | 366.3911 | 0 | 0.0027 | 240720.3129 | 65921.6898
December | 183881.1636 | 282.0819 | 375.8663 | 0 | 0.0029 | 246876.7654 | 74650.4903
Annual Sum or Average | 1883330 | 3127.3964 | 4625.5515 | 0 | 0.0344 | 3039440 | 787355.1212
Minimum of Months | 138079.8721 | 244.7578 | 340.0302 | 0 | 0.0026 | 223338.6827 | 59450.6182
Maximum of Months | 189366.9785 | 287.0729 | 445.1808 | 0 | 0.0032 | 292628.6747 | 76550.2404
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 572912000000 | 363800.54 | 13-JAN-11:15 | 101872.638 | 41401.92 | 65216.303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155309.679 | 0 | 0
February | 518241000000 | 368827.628 | 21-FEB-11:15 | 101872.638 | 41401.92 | 65216.303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160336.766 | 0 | 0
March | 578110000000 | 370145.625 | 30-MAR-10:15 | 101872.638 | 41401.92 | 65216.303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161654.764 | 0 | 0
April | 555177000000 | 376830.294 | 14-APR-10:15 | 101872.638 | 41401.92 | 65216.303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168339.433 | 0 | 0
May | 582796000000 | 387590.222 | 27-MAY-10:15 | 101872.638 | 41401.92 | 65216.303 | 0 | 86.234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179013.127 | 0 | 0
June | 606834000000 | 453157.347 | 14-JUN-17:15 | 67915.092 | 36859.929 | 65216.303 | 0 | 45981.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 237184.583 | 0 | 0
July | 679023000000 | 489777.803 | 08-JUL-10:00 | 101872.638 | 41401.92 | 65216.303 | 0 | 69107.757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212179.185 | 0 | 0
August | 662462000000 | 466909.905 | 12-AUG-10:00 | 101872.638 | 41401.92 | 65216.303 | 0 | 51144.369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207274.674 | 0 | 0
September | 589158000000 | 406459.646 | 08-SEP-17:15 | 67915.092 | 36859.929 | 65216.303 | 0 | 7982.387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228485.935 | 0 | 0
October | 576656000000 | 384734.031 | 07-OCT-10:15 | 101872.638 | 41401.92 | 65216.303 | 0 | 78.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176164.23 | 0 | 0
November | 558573000000 | 386348.523 | 09-NOV-11:15 | 101872.638 | 41401.92 | 65216.303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177857.662 | 0 | 0
December | 572859000000 | 367579.638 | 02-DEC-11:15 | 101872.638 | 41401.92 | 65216.303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159088.777 | 0 | 0
Annual Sum or Average | 7052800000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 518241000000 | 363800.54 |  | 67915.092 | 36859.929 | 65216.303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155309.679 | 0 | 0
Maximum of Months | 679023000000 | 489777.803 |  | 101872.638 | 41401.92 | 65216.303 | 0 | 69107.757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 237184.583 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 107491.75 | 50958.59 | 0 | 158450.33
Cost per Total Building Area ($/m2) | 25.71 | 12.19 | 0 | 37.9
Cost per Net Conditioned Building Area ($/m2) | 25.71 | 12.19 | 0 | 37.9

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 17224.38 | 4119.88 | 4119.88
Net Site Energy | 17224.38 | 4119.88 | 4119.88
Total Source Energy | 36933.64 | 8834.12 | 8834.12
Net Source Energy | 36933.64 | 8834.12 | 8834.12
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 9689.17 | 0 | 0 | 0 | 0
Cooling | 12.96 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1512.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 76.64 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2071.58 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 27.77 | 0 | 0 | 0 | 87.12
Refrigeration | 2848.8 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7308.32 | 9916.06 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 29.94 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 29.94 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 11.9 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 21.36 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 29.94 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 29.94 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 174.7 | 174.7 | 3.525 | 0.407 | 0.316 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 27501.83 | 21964.48 | 5537.35 | 0.8 | 3.6
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 146539.38 | 117034.45 | 29504.93 | 0.8 | 3.89
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 49624.91 | 39633.2 | 9991.72 | 0.8 | 3.35
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 386939.6 | 309031.34 | 77908.25 | 0.8 | 3.52
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 146007.08 | 116609.32 | 29397.76 | 0.8 | 3.89
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 53292.76 | 42562.54 | 10730.22 | 0.8 | 3.35
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 41691.98 | 0.78
PSZ-AC:2_HEATC | Coil:Heating:Gas | 238017.21 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 294434.41 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 798182.44 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 282482.62 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 97404.77 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.66 | 1892.64 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 8.85 | 16607.1 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 3 | 3278.52 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 23.38 | 39348.61 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 8.82 | 16546.77 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.22 | 3520.84 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.72 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 214321.6545 | 235.9888 | 867.5016 | 0 | 0.0031 | 174016.5076 | 80553.302
February | 188361.9897 | 208.364 | 782.4958 | 0 | 0.0028 | 156969.8826 | 70943.9274
March | 183836.6857 | 208.543 | 872.1687 | 0 | 0.0031 | 174985.3927 | 70037.407
April | 150215.2702 | 175.8628 | 826.8816 | 0 | 0.0029 | 165924.1977 | 58068.6106
May | 131581.3811 | 160.0715 | 850.3406 | 0 | 0.0029 | 170655.2099 | 51792.3574
June | 127304.2192 | 157.3743 | 875.1293 | 0 | 0.003 | 175638.4384 | 50494.4536
July | 134164.3873 | 166.5295 | 936.401 | 0 | 0.0032 | 187937.78 | 53319.3049
August | 133894.6267 | 165.1276 | 912.1954 | 0 | 0.0031 | 183076.3614 | 53047.9007
September | 133989.7788 | 161.8983 | 842.8271 | 0 | 0.0029 | 169143.6197 | 52570.588
October | 159578.3535 | 186.1671 | 864.6682 | 0 | 0.003 | 173503.9744 | 61586.9239
November | 186125.6816 | 209.0311 | 838.915 | 0 | 0.003 | 168304.0062 | 70584.9818
December | 204221.0006 | 226.8016 | 867.0914 | 0 | 0.0031 | 173944.56 | 77054.6552
Annual Sum or Average | 1947600 | 2261.7595 | 10336.6156 | 0 | 0.036 | 2074100 | 750054.4125
Minimum of Months | 127304.2192 | 157.3743 | 782.4958 | 0 | 0.0028 | 156969.8826 | 50494.4536
Maximum of Months | 214321.6545 | 235.9888 | 936.401 | 0 | 0.0032 | 187937.78 | 80553.302
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 613166000000 | 381734.916 | 21-JAN-11:15 | 101872.638 | 41401.92 | 81325.389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157134.969 | 0 | 0
February | 553100000000 | 379757.573 | 27-FEB-11:15 | 101872.638 | 41401.92 | 81325.389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155157.626 | 0 | 0
March | 616580000000 | 383022.118 | 09-MAR-11:15 | 101872.638 | 41401.92 | 81325.389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158422.171 | 0 | 0
April | 584652000000 | 382292.137 | 14-APR-10:15 | 101872.638 | 41401.92 | 81325.389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157692.191 | 0 | 0
May | 601322000000 | 400236.049 | 31-MAY-10:15 | 101872.638 | 41401.92 | 81325.389 | 0 | 95.788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175540.314 | 0 | 0
June | 618881000000 | 428427.197 | 21-JUN-17:15 | 67915.092 | 36859.929 | 81325.389 | 0 | 22138.164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220188.623 | 0 | 0
July | 662219000000 | 432375.424 | 21-JUL-17:15 | 67915.092 | 36859.929 | 81325.389 | 0 | 32819.841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 213455.173 | 0 | 0
August | 645089000000 | 428432.055 | 15-AUG-17:15 | 67915.092 | 36859.929 | 81325.389 | 0 | 25452.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216878.965 | 0 | 0
September | 595996000000 | 393027.618 | 01-SEP-10:15 | 101872.638 | 41401.92 | 81325.389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168427.672 | 0 | 0
October | 611360000000 | 389162.478 | 02-OCT-10:15 | 101872.638 | 41401.92 | 81325.389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164562.531 | 0 | 0
November | 593037000000 | 380116.309 | 14-NOV-11:15 | 101872.638 | 41401.92 | 81325.389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155516.363 | 0 | 0
December | 612912000000 | 385061.331 | 18-DEC-11:15 | 101872.638 | 41401.92 | 81325.389 | 0 | 0 | 4916 | 0 | 0 | 0 | 0 | 0 | 0 | 155545.384 | 0 | 0
Annual Sum or Average | 7308320000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 553100000000 | 379757.573 |  | 67915.092 | 36859.929 | 81325.389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155157.626 | 0 | 0
Maximum of Months | 662219000000 | 432375.424 |  | 101872.638 | 41401.92 | 81325.389 | 0 | 32819.841 | 4916 | 0 | 0 | 0 | 0 | 0 | 0 | 220188.623 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 179510.4 | 41013.09 | 0 | 220523.48
Cost per Total Building Area ($/m2) | 42.94 | 9.81 | 0 | 52.75
Cost per Net Conditioned Building Area ($/m2) | 42.94 | 9.81 | 0 | 52.75

## Picture
DOE Commercial Building Benchmark - Super Market
Sales
Bakery
Deli
Produce
Office
DryStorage

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 112 | 5840
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 112 | 5840
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | 11.3 | 72.2 | 3764.71
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | 9.9
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 5.8
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0 | 0 | 7.6 | 49 | 2555
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | 7.6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 3.4
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | 13.9 | 91.6 | 4776.29
|  |  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15 | 12.3
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.15 | 0.15 | 9.8
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.22 | 0.64 | 0.74 | 0.68 | 0.68 | 0.71 | 0.72 | 0.72 | 0.73 | 0.68 | 0.68 | 0.58 | 0.54 | 0 | 0 | 0 | 8.44 | 52.69 | 2747.41
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.21 | 0.56 | 0.66 | 0.68 | 0.68 | 0.69 | 0.7 | 0.69 | 0.66 | 0.58 | 0.47 | 0.43 | 0.43 | 0.08 | 0 | 0 | 7.61
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.13 | 0.35 | 0.37 | 0.37 | 0.39 | 0.41 | 0.38 | 0.34 | 0.03 | 0 | 0 | 0 | 0 | 0 | 2.88
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0.23 | 0.13 | 0.08 | 6.62 | 44.59 | 2325.05
|  |  | Sat, WinterDesign | 0.11 | 0.1 | 0.08 | 0.06 | 0.06 | 0.06 | 0.07 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0.16 | 0.13 | 6.9
|  |  | Sun, Hol, Other | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07 | 0.1 | 0.12 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.1 | 0.06 | 4.59
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
INFIL_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8 | 56 | 2920
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16 | 115.5 | 6022.5
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19.5
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | WD, WinterDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8 | 3225.6 | 168192
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8
|  |  | Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624 | 4368 | 227760
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 112 | 5840
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
Deli Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Deli Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Deli Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Deli Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Deli_Case:1_ MULTIDECKDIARYANDDELICASE_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Deli_Case:1_ MULTIDECKDIARYANDDELICASE_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Deli_Case:1_ MULTIDECKDIARYANDDELICASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 595 | 31025
Deli_Case:1_ MULTIDECKDIARYANDDELICASE_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2 | 10.4 | 72.8 | 3796
Deli_Case:2_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Deli_Case:2_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Deli_Case:2_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Deli_Case:2_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Sales_Case:1_MEATDISPLAYCASE_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Sales_Case:1_MEATDISPLAYCASE_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Sales_Case:1_MEATDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 595 | 31025
Sales_Case:2_ MULTIDECKDIARYANDDELICASE_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Sales_Case:2_ MULTIDECKDIARYANDDELICASE_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Sales_Case:2_ MULTIDECKDIARYANDDELICASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 595 | 31025
Sales_Case:2_ MULTIDECKDIARYANDDELICASE_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2 | 10.4 | 72.8 | 3796
Sales_Case:3_GLASSDOORFROZENFOOD_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57 | 3.97 | 206.83
Sales_Case:3_GLASSDOORFROZENFOOD_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73 | 5.13 | 267.67
Sales_Case:3_GLASSDOORFROZENFOOD_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 595 | 31025
Sales_Case:3_GLASSDOORFROZENFOOD_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2 | 10.4 | 72.8 | 3796
Sales_Case:4_OPENWELLICECREAMDISPLAYCASE_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Sales_Case:4_OPENWELLICECREAMDISPLAYCASE_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Sales_Case:4_OPENWELLICECREAMDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 595 | 31025
Sales_Case:4_OPENWELLICECREAMDISPLAYCASE_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2 | 10.4 | 72.8 | 3796
Sales_Case:5_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Sales_Case:5_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Sales_Case:5_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Sales_Case:5_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Sales_Case:6_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Sales_Case:6_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Sales_Case:6_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Sales_Case:6_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Sales_Case:7_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Sales_Case:7_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Sales_Case:7_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Sales_Case:7_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Produce_Case:1_ MULTIDECKDIARYANDDELICASE_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Produce_Case:1_ MULTIDECKDIARYANDDELICASE_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Produce_Case:1_ MULTIDECKDIARYANDDELICASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 595 | 31025
Produce_Case:1_ MULTIDECKDIARYANDDELICASE_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2 | 10.4 | 72.8 | 3796
Bakery Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Bakery Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Bakery Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Bakery Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Bakery_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Bakery_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Bakery_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Bakery_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720