## BuildingSummary
Building Summary Full Service Restaurant pre-1980 construction
|  | Value | Data Source
Program
| Building Name | Full Service Restaurant
| Available Fuel Types | gas, electricity
| Principal Building Activity | Food Service
Form |  |  | Time Saver Standards; Restaurant studies (EPRI, MEOS, LBL) cited in Huang et al. 1991 for all Form parameters
| Total Floor Area (m2) | 511.15
| Building Shape | Rectangle
| Aspect Ratio | 1
| Number of Floors | 1
Window Fraction (Window to Wall Ratio)
| South | 0.28
| East | 0.224
| North | 0
| West | 0.224
| Total | 0.182
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | 2 zones
| Floor to Ceiling Height (m) | 3.048
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel frame wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 275.72
| Net Dimensions - Total Area (m2) | 225.54
| Wall to Skin Ratio | 0.35
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 569.52
| Net Dimensions - Total Area (m2) | 569.52
| Roof to Skin Ratio | 0.65
| Window Dimensions (m2) |  | Time Saver Standards; FF Restaurant studies (EPRI, MEOS, LBL) cited in Huang et al. 1991
| South | 19.3
| East | 15.44
| North | 0
| West | 15.44
| Total Area (m2) | 50.18
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 4in slab-on-grade
| Dimensions - Total Area (m2) | 511.15
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 68.93
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 1022.31
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 2.0608 | See Reference Buildings Technical Report
HVAC
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | Unitary DX | 2003 CBECS
| Fan Control | Constant volume | 2003 CBECS
Service Water Heating
| SWH Type | Storage Tank
| Fuel | Natural Gas
| Thermal Efficiency (%) | 80 | Winiarski and Halverson, 2008
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3) | 1377.36

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Dining | Yes | 1 | 371.75 | 1133.39 | 3.0488 | 169.1902 | 47.17 | 1.3935 | 266.7653 | 27.3936 | 60.2778 |  |  | 10 |  | 2667.6532 |  | 1.9479
Kitchen | Yes | 1 | 139.41 | 425.02 | 3.0487 | 106.5301 | 0 | 18.5806 | 7.503 | 16.3771 | 376.7365 | 1198.345 | 503.4582 | 8 |  | 60.0238 | 1887.788 | 2.3617
Total Conditioned Zones |  |  | 511.16 | 1558.41 |  | 275.7203 | 47.17 |  | 274.2683
Data Source | [7 empty] | 1 |  | 2 | 4, 5 | 4, 5 | 4, 5 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Commercial Reference Buildings Report
[5] Smith, V. A. and D.R. Fisher. (2001). Estimating Food Service Loads and Profiles. ASHRAE Transactions 2001. V. 107. Pt 2. Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric
Exterior walls
| Construction Type | Steel frame wall | Steel frame wall | Steel frame wall | Steel frame wall | Steel frame wall | Steel frame wall | Steel frame wall | Steel frame wall | Steel frame wall | Steel frame wall | Steel frame wall | Steel frame wall | Steel frame wall | Steel frame wall | Steel frame wall | Steel frame wall
| R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
| SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
| Visible transmittance | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade
| R-value (m2·K / W) | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC_1:1_COOLC DXCOIL | 101.7888 | 104.885 | 108.9322 | 106.1836 | 94.1844 | 108.7962 | 67.428 | 99.4679 | 89.3934 | 77.5185 | 90.4701 | 81.3397 | 86.907 | 65.3254 | 79.8101 | 67.6401
| PSZ-AC_2:2_COOLC DXCOIL | 24.4999 | 25.2895 | 26.7 | 25.5364 | 20.796 | 26.5342 | 13.7881 | 22.8859 | 24.3317 | 17.1486 | 23.9648 | 22.4186 | 27.0576 | 19.253 | 29.106 | 25.6275
Heating (kW)
| PSZ-AC_1:1_HEATC | 136.2995 | 172.2158 | 153.1645 | 182.9757 | 133.9845 | 160.9575 | 138.4728 | 194.6307 | 162.2912 | 165.0986 | 213.5755 | 178.9307 | 225.6783 | 206.7285 | 223.9235 | 294.6792
| PSZ-AC_2:2_HEATC | 38.1976 | 52.0513 | 46.3646 | 56.6981 | 33.7212 | 49.8103 | 31.1922 | 56.5642 | 51.7347 | 41.2568 | 69.1937 | 57.0218 | 84.4285 | 82.1221 | 92.9615 | 152.0531
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC_1:1_COOLC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.3 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.3 | 3.23 | 3.3
| PSZ-AC_2:2_COOLC DXCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.67 | 3.5 | 3.5 | 3.67 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Heating Efficiency (%)
| PSZ-AC_1:1_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_2:2_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
HVAC Control - Economizer
| PSZ-AC_1:1 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC_2:2 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
Fan Max Flow Rate (m3/s )
| DINING EXHAUST FAN | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83
| KITCHEN EXHAUST FAN | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06
| PSZ-AC_1:1_FAN | 4.1 | 4.22 | 4.39 | 4.28 | 3.82 | 4.38 | 3.52 | 4.01 | 4.36 | 3.69 | 3.64 | 3.9 | 3.5 | 3.57 | 3.21 | 4.09
| PSZ-AC_2:2_FAN | 0.99 | 1.02 | 1.08 | 1.03 | 0.84 | 1.07 | 0.7 | 0.92 | 1.06 | 0.78 | 0.97 | 0.98 | 1.09 | 1.16 | 1.17 | 1.55
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.077279 | 0.10745 | 0.094685 | 0.10288 | 0.12397 | 0.094182 | 0.14437 | 0.06629 | 0.037429 | 0.069705 | 0.051815 | 0.037452 | 0.052149 | 0.068023 | 0.050825 | 0.08646
| Total Cost ($/m2) | 69.34 | 90.73 | 81.96 | 80.04 | 86.9 | 77.52 | 97.42 | 49.56 | 28.16 | 47.68 | 37.19 | 26.9 | 34.69 | 47.35 | 32.56 | 60.88
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011467 | 0.0081839 | 0.008568 | 0.010545 | 0.0084183 | 0.0080956 | 0.0084371 | 0.0099602 | 0.007131 | 0.0083237 | 0.0087034 | 0.0071169 | 0.0079259 | 0.0085274 | 0.0079191 | 0.0041634
| Total Cost ($/m2) | 21.95 | 19.53 | 19.02 | 30.15 | 18.84 | 20.15 | 23.67 | 35.77 | 21.85 | 28.85 | 36.45 | 25.69 | 39.18 | 37 | 45.38 | 31.45
Total Utility Costs
| Cost Intensity ($/m2) | 91.28 | 110.26 | 100.98 | 110.19 | 105.74 | 97.67 | 121.09 | 85.33 | 50 | 76.53 | 73.63 | 52.59 | 73.87 | 84.35 | 77.94 | 92.33
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 106444.4444 | 77786.1111 | 86311.1111 | 43188.8889 | 11755.5556 | 64558.3333 | 4255.5556 | 31841.6667 | 28213.8889 | 5688.8889 | 20458.3333 | 17144.4444 | 16138.8889 | 9241.6667 | 5497.2222 | 2480.5556
| Interior Lighting | 80500 | 80500 | 80500 | 80500 | 80500 | 80500 | 80500 | 80500 | 80500 | 80500 | 80500 | 80500 | 80500 | 80500 | 80500 | 80500
| Exterior Lighting | 22216.6667 | 22177.7778 | 22172.2222 | 22208.3333 | 22202.7778 | 22183.3333 | 22158.3333 | 22180.5556 | 22177.7778 | 22144.4444 | 22150 | 22155.5556 | 22169.4444 | 22141.6667 | 22136.1111 | 22002.7778
| Interior Equipment | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 64338.8889 | 66772.2222 | 69227.7778 | 68186.1111 | 60183.3333 | 69741.6667 | 55047.2222 | 64519.4444 | 70616.6667 | 58675 | 61016.6667 | 64769.4444 | 38658.3333 | 61652.7778 | 37322.2222 | 73286.1111
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 18711.1111 | 17941.6667 | 17855.5556 | 17183.3333 | 17261.1111 | 17313.8889 | 16569.4444 | 16672.2222 | 16594.4444 | 16244.4444 | 16327.7778 | 16202.7778 | 16158.3333 | 15886.1111 | 15636.1111 | 15241.6667
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 458616.6667 | 431583.3333 | 442472.2222 | 397672.2222 | 358308.3333 | 420700 | 344933.3333 | 382122.2222 | 384511.1111 | 349655.5556 | 366858.3333 | 367177.7778 | 340030.5556 | 355827.7778 | 327494.4444 | 359916.6667
Gas (MJ)
| Heating | 15000 | 225450 | 158220 | 436910 | 125570 | 274510 | 389790 | 787850 | 522630 | 711350 | 1071950 | 777430 | 1440390 | 1128160 | 1813340 | 2709610
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 162420 | 193490 | 175620 | 223430 | 217630 | 197140 | 243250 | 246970 | 242510 | 259220 | 267630 | 266550 | 285480 | 288730 | 314930 | 350570
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 978340 | 1219860 | 1134760 | 1461260 | 1144110 | 1272570 | 1433960 | 1835740 | 1566050 | 1771490 | 2140500 | 1844910 | 2526800 | 2217810 | 2929190 | 3861100
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 2629350 | 2773550 | 2727660 | 2892880 | 2434020 | 2787090 | 2675720 | 3211380 | 2950290 | 3030250 | 3461200 | 3166750 | 3750910 | 3498790 | 4108170 | 5156790
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 749.6821 | 547.8431 | 607.8842 | 304.1769 | 82.7937 | 454.6806 | 29.9716 | 224.259 | 198.7088 | 40.0665 | 144.0869 | 120.7473 | 113.6653 | 65.0885 | 38.7166 | 17.4704
| Interior Lighting (elec) | 566.9569 | 566.9569 | 566.9569 | 566.9569 | 566.9569 | 566.9569 | 566.9569 | 566.9569 | 566.9569 | 566.9569 | 566.9569 | 566.9569 | 566.9569 | 566.9569 | 566.9569 | 566.9569
| Exterior Lighting (elec) | 156.4707 | 156.1968 | 156.1577 | 156.412 | 156.3729 | 156.2359 | 156.0599 | 156.2164 | 156.1968 | 155.962 | 156.0012 | 156.0403 | 156.1381 | 155.9425 | 155.9034 | 154.9643
| Interior Equipment (elec) | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 453.1351 | 470.2729 | 487.5673 | 480.2309 | 423.8677 | 491.1865 | 387.6944 | 454.4067 | 497.3491 | 413.2446 | 429.7369 | 456.1675 | 272.2684 | 434.217 | 262.8583 | 516.1499
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 131.7813 | 126.3621 | 125.7556 | 121.0212 | 121.569 | 121.9407 | 116.6976 | 117.4215 | 116.8737 | 114.4087 | 114.9956 | 114.1152 | 113.8022 | 111.885 | 110.1242 | 107.3462
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 3230.0108 | 3039.6166 | 3116.3064 | 2800.7825 | 2523.5449 | 2962.9659 | 2429.3456 | 2691.2648 | 2708.0896 | 2462.6039 | 2583.7621 | 2586.0119 | 2394.8156 | 2506.0745 | 2306.5245 | 2534.8723
Gas (MJ/m2)
| Heating (gas) | 29.3456 | 441.0643 | 309.5373 | 854.7589 | 245.6617 | 537.0439 | 762.5746 | 1541.3284 | 1022.4592 | 1391.6659 | 2097.1339 | 1520.943 | 2817.9399 | 2207.1016 | 3547.5692 | 5301.0075
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 317.7541 | 378.5386 | 343.5782 | 437.1124 | 425.7654 | 385.6794 | 475.8877 | 483.1654 | 474.44 | 507.131 | 523.5841 | 521.4712 | 558.5053 | 564.8635 | 616.1205 | 685.8456
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1913.9978 | 2386.501 | 2220.0137 | 2858.7694 | 2238.3058 | 2489.6214 | 2805.3605 | 3591.392 | 3063.7778 | 3465.695 | 4187.6162 | 3609.3319 | 4943.363 | 4338.8633 | 5730.5879 | 7553.7513
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 5143.989 | 5426.098 | 5336.3201 | 5659.552 | 4761.8507 | 5452.5873 | 5234.7061 | 6282.6568 | 5771.8674 | 5928.2989 | 6771.3978 | 6195.3438 | 7338.1786 | 6844.9379 | 8037.1124 | 10088.6041
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 73.4107 | 69.1112 | 63.3482 | 56.0892 | 65.1993 | 54.5327 | 52.6313 | 53.7097 | 54.4421 | 53.0193 | 53.0708 | 53.6445 | 50.0217 | 53.0949 | 49.783 | 55.7873
| Feb | 75.7466 | 65.881 | 67.3952 | 57.4022 | 64.9003 | 55.3308 | 54.8039 | 53.6032 | 54.4849 | 53.0248 | 53.0327 | 53.591 | 49.9826 | 53.2061 | 49.797 | 54.2673
| Mar | 75.4894 | 71.6615 | 76.419 | 62.2054 | 62.207 | 61.9506 | 52.5983 | 61.8457 | 56.1566 | 52.996 | 53.933 | 61.1875 | 50.0509 | 53.1603 | 49.7656 | 54.3149
| Apr | 79.1048 | 78.3817 | 79.5269 | 68.5281 | 68.2144 | 76.5089 | 56.5371 | 60.6985 | 67.4674 | 53.4745 | 52.8711 | 59.6624 | 53.4715 | 51.5683 | 46.3794 | 54.2146
| May | 83.631 | 87.7187 | 96.6721 | 79.6586 | 64.958 | 86.1575 | 59.0017 | 71.0572 | 74.4099 | 58.7751 | 68.6836 | 68.2168 | 74.3139 | 61.3259 | 54.2047 | 53.2941
| Jun | 86.8194 | 88.1974 | 105.0749 | 83.0712 | 61.6552 | 102.1094 | 60.0803 | 86.7393 | 81.3395 | 63.2421 | 80.1714 | 77.1763 | 76.6459 | 73.2574 | 63.5067 | 65.5607
| Jul | 86.1392 | 90.6582 | 101.6043 | 91.0879 | 65.8609 | 99.7398 | 69.8701 | 87.8375 | 85.139 | 65.8107 | 83.016 | 77.3929 | 77.656 | 73.7394 | 70.8177 | 66.707
| Aug | 87.3659 | 89.9381 | 103.1994 | 86.2835 | 72.8737 | 96.7761 | 64.0157 | 86.9989 | 78.6265 | 64.6667 | 81.6066 | 77.6657 | 76.6035 | 71.7246 | 66.8214 | 62.7419
| Sep | 85.1737 | 87.86 | 94.5362 | 77.9829 | 79.1199 | 90.7106 | 71.4102 | 73.3714 | 72.4351 | 78.0804 | 70.3362 | 72.6493 | 59.9802 | 67.9891 | 54.7495 | 54.4481
| Oct | 83.7059 | 80.9672 | 79.2119 | 70.9451 | 70.0305 | 76.8604 | 60.0232 | 69.7593 | 67.7491 | 57.8575 | 62.0379 | 65.2588 | 57.0055 | 57.6429 | 54.6109 | 54.4087
| Nov | 79.2697 | 74.7022 | 72.9093 | 58.7496 | 64.9391 | 58.5527 | 52.8392 | 62.0599 | 54.5028 | 53.456 | 61.6851 | 53.6484 | 50.1917 | 53.1679 | 49.9048 | 54.3089
| Dec | 72.9448 | 72.5046 | 61.3529 | 55.2901 | 66.3271 | 57.2288 | 52.6399 | 53.6933 | 54.4135 | 52.9991 | 53.0906 | 53.5773 | 50.0208 | 53.094 | 49.7822 | 55.9114
Time of Peak Electrical Demand
| Jan | 06-JAN-12:00 | 03-JAN-12:15 | 28-JAN-18:15 | 23-JAN-18:15 | 26-JAN-12:00 | 19-JAN-16:00 | 15-JAN-17:15 | 09-JAN-07:30 | 25-JAN-17:30 | 14-JAN-07:45 | 18-JAN-07:15 | 27-JAN-17:15 | 16-JAN-07:45 | 10-JAN-07:00 | 16-JAN-07:45 | 01-JAN-11:15
| Feb | 23-FEB-12:15 | 22-FEB-18:15 | 28-FEB-18:30 | 18-FEB-18:30 | 12-FEB-12:00 | 08-FEB-12:00 | 14-FEB-12:00 | 15-FEB-17:45 | 14-FEB-17:45 | 21-FEB-17:45 | 27-FEB-18:45 | 11-FEB-17:30 | 18-FEB-07:15 | 02-FEB-17:30 | 28-FEB-17:00 | 27-FEB-08:15
| Mar | 13-MAR-11:00 | 25-MAR-17:15 | 17-MAR-16:15 | 28-MAR-17:15 | 30-MAR-11:00 | 31-MAR-15:00 | 22-MAR-06:15 | 09-MAR-18:30 | 25-MAR-15:45 | 13-MAR-06:30 | 14-MAR-17:00 | 26-MAR-16:30 | 23-MAR-06:15 | 09-MAR-18:30 | 18-MAR-06:15 | 09-MAR-07:30
| Apr | 01-APR-17:15 | 29-APR-15:15 | 01-APR-17:15 | 14-APR-17:15 | 11-APR-16:15 | 21-APR-16:15 | 29-APR-11:00 | 05-APR-17:15 | 21-APR-17:15 | 29-APR-15:15 | 28-APR-16:15 | 24-APR-11:00 | 16-APR-17:15 | 06-APR-17:15 | 14-APR-10:15 | 01-APR-06:15
| May | 23-MAY-11:00 | 26-MAY-17:30 | 28-MAY-16:00 | 31-MAY-17:30 | 29-MAY-11:00 | 31-MAY-16:15 | 09-MAY-11:00 | 31-MAY-16:15 | 31-MAY-17:15 | 15-MAY-16:00 | 30-MAY-17:15 | 23-MAY-17:15 | 27-MAY-15:15 | 16-MAY-17:15 | 31-MAY-17:15 | 30-MAY-17:15
| Jun | 26-JUN-10:00 | 13-JUN-17:30 | 08-JUN-15:00 | 19-JUN-17:15 | 28-JUN-11:00 | 27-JUN-15:00 | 16-JUN-11:00 | 30-JUN-16:00 | 19-JUN-17:15 | 27-JUN-17:15 | 08-JUN-11:00 | 28-JUN-11:00 | 29-JUN-17:30 | 30-JUN-15:00 | 14-JUN-17:30 | 20-JUN-17:00
| Jul | 13-JUL-11:00 | 30-JUL-15:30 | 19-JUL-16:00 | 03-JUL-16:30 | 29-JUL-10:15 | 24-JUL-16:15 | 02-JUL-15:15 | 25-JUL-10:00 | 31-JUL-17:30 | 24-JUL-17:00 | 14-JUL-11:00 | 17-JUL-16:15 | 13-JUL-17:00 | 21-JUL-16:00 | 06-JUL-17:30 | 29-JUL-17:00
| Aug | 21-AUG-15:30 | 27-AUG-16:15 | 01-AUG-16:00 | 17-AUG-11:00 | 08-AUG-11:00 | 04-AUG-16:15 | 15-AUG-11:00 | 17-AUG-15:15 | 01-AUG-17:15 | 18-AUG-17:30 | 04-AUG-16:30 | 30-AUG-11:00 | 25-AUG-17:15 | 09-AUG-17:15 | 11-AUG-17:30 | 15-AUG-17:15
| Sep | 06-SEP-11:00 | 16-SEP-11:00 | 12-SEP-17:15 | 11-SEP-11:00 | 24-SEP-10:00 | 01-SEP-11:00 | 28-SEP-15:30 | 05-SEP-11:00 | 20-SEP-16:00 | 02-SEP-15:00 | 06-SEP-11:15 | 02-SEP-15:15 | 14-SEP-11:00 | 01-SEP-17:15 | 08-SEP-17:00 | 19-SEP-06:30
| Oct | 07-OCT-17:00 | 29-OCT-15:15 | 24-OCT-17:45 | 12-OCT-15:00 | 19-OCT-10:00 | 03-OCT-17:30 | 16-OCT-17:30 | 20-OCT-17:30 | 12-OCT-17:45 | 17-OCT-17:30 | 31-OCT-17:15 | 05-OCT-16:15 | 08-OCT-17:45 | 05-OCT-17:00 | 07-OCT-17:45 | 04-OCT-06:00
| Nov | 01-NOV-17:45 | 27-NOV-18:15 | 12-NOV-17:30 | 19-NOV-17:30 | 20-NOV-12:00 | 10-NOV-12:00 | 02-NOV-17:30 | 04-NOV-17:15 | 09-NOV-17:15 | 04-NOV-17:30 | 02-NOV-17:30 | 04-NOV-16:00 | 03-NOV-06:30 | 21-NOV-18:00 | 08-NOV-18:45 | 14-NOV-07:00
| Dec | 15-DEC-18:15 | 02-DEC-18:30 | 11-DEC-17:30 | 26-DEC-17:45 | 19-DEC-12:00 | 05-DEC-12:00 | 03-DEC-17:45 | 23-DEC-07:15 | 08-DEC-16:00 | 31-DEC-07:45 | 12-DEC-16:45 | 21-DEC-16:45 | 02-DEC-07:15 | 29-DEC-08:15 | 26-DEC-07:30 | 18-DEC-11:15
Source Energy
| Total Source Energy (GJ) | 6544.76 | 6975.11 | 6277.51 | 6411.66 | 5241.64 | 6807.09 | 5409.15 | 6923.91 | 6303.02 | 4127.23 | 7020.61 | 6400.5 | 6966.54 | 6874.54 | 7250.83 | 8844.55
| Total Source Energy (MJ/m2) | 12803.91 | 13645.83 | 12281.07 | 12543.52 | 10254.55 | 13317.12 | 10582.24 | 13545.65 | 12330.99 | 8074.36 | 13734.84 | 12521.69 | 13629.06 | 13449.07 | 14185.23 | 17303.13
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36
| Total Building | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36
Emissions
| Carbon Equivalent (kg) | 143417.2118 | 165956.3603 | 154034.5689 | 148848.0627 | 62505.4708 | 164839.653 | 66169.2613 | 136220.9087 | 185311.7751 | 57411.7194 | 234189.8734 | 183260.0962 | 161955.4447 | 170026.0396 | 164920.2158 | 170901.8637
| CO2 (kg) | 342210.4495 | 424788.9982 | 373241.4556 | 354152.1473 | 171404.8216 | 402373.2683 | 182333.072 | 326886.6411 | 447583.3975 | 152790.8742 | 562801.2325 | 445614.2137 | 399971.8594 | 417987.4834 | 411043.0538 | 454860.7584
| NOX (kg) | 559.9062 | 532.5089 | 584.5888 | 605.9749 | 149.7892 | 611.327 | 159.928 | 549.182 | 716.2215 | 180.9933 | 922.9814 | 700.4658 | 609.1631 | 641.7616 | 610.1423 | 500.4645
| SO2 (kg) | 1963.3195 | 2058.9751 | 1779.5778 | 1396.2205 | 1042.9416 | 2314.5301 | 1004.1028 | 1395.3874 | 1679.4985 | 270.7313 | 2472.9123 | 1603.8866 | 803.2064 | 950.6984 | 773.7235 | 1833.1516
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0091 | 0.0059 | 0.0049 | 0.0053 | 0.0006 | 0.0045 | 0.0006 | 0.0058 | 0.0067 | 0.0012 | 0.0077 | 0.0064 | 0.0061 | 0.0068 | 0.006 | 0.0066
| Water for Electricity (m3) | 242.9552 | 702.2352 | 13143.4 | 2482.9 | 6291.1 | 11541.5 | 6056.28 | 86.7559 | 1745.98 | 3572.37 | 569.1603 | 1667.28 | 527.5389 | 22539.6 | 508.0875 | 367.7191

## Picture
DOE Commercial Building Benchmark - Full Service Restaurant

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
BLDG_EQUIP_SCH | Fraction | Through 12/31 | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9 | 23.6 | 1230.57
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9
|  |  | SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9
BLDG_LIGHT_SCH | Fraction | Through 12/31 | SummerDesign | [24 empty] | 24 | 35.4 | 1845.86 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Weekday, Sat, Sun, Hol, Other | 0.45 | 0.15 | 0.15 | 0.15 | 0.15 | 0.45 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 17.7
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2 | 8.4 | 56.8 | 2961.71
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35 | 8.25
|  |  | Sun, Hol, Other | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2 | 6.55
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
GAS_EQUIP_SCH | Fraction | Through 12/31 | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65 | 21.9 | 1141.93
|  |  | SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65
Kitchen_Exhaust_SCH | On/Off | Through 12/31 | All | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 140 | 7300
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 14.5 | 101.5 | 5292.5
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 14.5
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 14.5
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
CLGSETP_KITCHEN_SCH | Temperature | Through 12/31 | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 0 | 0
|  |  | Other | 26 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 640
HTGSETP_KITCHEN_SCH | Temperature | Through 12/31 | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4 | 0 | 0
|  |  | WinterDesign | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456
|  |  | Other | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 442.4
CLGSETP_SCH | Temperature | Through 12/31 | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 0 | 0
|  |  | Other | 24 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 600
HTGSETP_SCH | Temperature | Through 12/31 | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4 | 0 | 0
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Other | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 482.4
HVACOperationSchd | On/Off | Through 12/31 | All | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 140 | 7300
MinOA_Sched | Fraction | Through 12/31 | All | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 140 | 7300
Kitchen_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Kitchen_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Kitchen_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Kitchen_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | 7.75 | 52.65 | 2745.32
|  |  | Sat, WinterDesign | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3 | 7.45
|  |  | Sun, Hol, Other | 0.25 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2 | 6.45
Kitchen Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Kitchen Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Kitchen Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Kitchen Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600