## BuildingSummary
Building Summary Large Hotel new construction
|  | Value | Data Source
Program
| Building Name | Large Hotel new construction 90.1-2004
| Available Fuel Types | gas, electricity
| Principal Building Activity | Lodging
Form
| Total Floor Area (m2) | 11344.93 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 3.8 1st floor, 5.1 other floors
| Number of Floors | 6 plus basement
Window Fraction (Window to Wall Ratio)
| South | 0.3254
| East | 0.2112
| North | 0.2311
| West | 0.2112
| Total | 0.2663
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | See pictures
| Floor to Ceiling Height (m) | 3.96 1st floor, 3.05 other floors
| Floor to Floor Height (m) | 3.96 1st floor, 3.05 other floors
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Mass Wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 4462.84
| Net Dimensions - Total Area (m2) | 3248.53
| Wall to Skin Ratio | 0.75127
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1477.55
| Net Dimensions - Total Area (m2) | 1477.55
| Roof to Skin Ratio | 0.24873
Window Dimensions (m2)
| South | 609.46
| East | 85.84
| North | 432.93
| West | 85.84
| Total Area (m2) | 1214.07
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Basement
| Construction | 4 in slab w/carpet
| Dimensions - Total Area (m2) | 1978.83
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 15687.82
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 22690.58
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.15999 | See Reference Buildings Technical Report
HVAC
| System Type | FCU in rooms, CV ventilation, MZVAV in common areas | 2003 CBECS
| Heating Type | Gas boiler | 2003 CBECS
| Cooling Type | 2 air cooled chillers | 2003 CBECS
| Fan Control | Variable | 2003 CBECS
Service Water Heating
| SWH Type | gas boiler
| Fuel | gas
| Thermal Efficiency (%) | 80 | Standard 90.1-2004
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 44332.9

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Basement | Yes | 1 | 1978.83 | 4826.41 | 2.439 | 0 | 0 | 37.1613 | 53.2498 | 10.7639 | 5.3819 |  |  |  | 0.25 | 494.7075 |  | 0
Retail_1_Flr_1 | Yes | 1 | 67.07 | 265.76 | 3.9624 | 68.8401 | 23.3 | 6.1939 | 10.8285 | 16.1458 | 10.7639 |  |  |  | 1.5 | 100.605 |  | 0.28192
Retail_2_Flr_1 | Yes | 1 | 77.67 | 307.76 | 3.9624 | 26.57 | 0 | 6.1939 | 12.5399 | 16.1458 | 10.7639 |  |  |  | 1.5 | 116.505 |  | 0.093963
Mech_Flr_1 | Yes | 1 | 164.24 | 650.8 | 3.9625 | 62.8001 | 0 | 0 | 0 | 16.1458 | 5.3819 |  |  |  | 0.25 | 41.06 |  | 0.10502
Storage_Flr_1 | Yes | 1 | 94.76 | 375.47 | 3.9623 | 36.23 | 0 | 46.4516 | 2.04 | 9.6875 | 2.691 |  |  |  | 0.75 | 71.07 |  | 0.10502
Laundry_Flr_1 | Yes | 1 | 78.04 | 309.22 | 3.9623 | 85.7501 | 0 | 23.2258 | 3.3601 | 6.4583 | 61.6991 | 536.0463 | 592.7936 | 8 |  | 26.8805 | 235.9735 | 0.30182
Cafe_Flr_1 | Yes | 1 | 188.86 | 748.35 | 3.9625 | 152.1701 | 65.6201 | 1.3935 | 135.5247 | 13.9931 | 5.3819 |  |  | 10 |  | 1355.2468 |  | 0.22131
Lobby_Flr_1 | Yes | 1 | 1308.19 | 5183.56 | 3.9624 | 434.7904 | 85.2401 | 3.0965 | 422.479 | 11.8403 | 8.0729 |  |  | 10 |  | 4224.7904 |  | 0.091291
Room_1_Flr_3 | Yes | 4 | 39.02 | 118.94 | 3.0482 | 39.95 | 13.18 | 26.0133 | 1.5 | 11.8403 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 0.36556
Room_2_Flr_3 | Yes | 4 | 39.02 | 118.93 | 3.0479 | 39.95 | 13.18 | 26.0133 | 1.5 | 11.8403 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 0.3656
Room_3_Mult19_Flr_3 | Yes | 76 | 24.52 | 74.75 | 3.0485 | 11.15 | 3.68 | 16.3467 | 1.5 | 11.8403 | 14.3052 |  | 89.9032 |  |  | 14.1584 |  | 0.16235
Room_4_Mult19_Flr_3 | Yes | 76 | 24.53 | 74.77 | 3.0481 | 11.15 | 3.68 | 16.3533 | 1.5 | 11.8403 | 14.3052 |  | 89.9032 |  |  | 14.1584 |  | 0.1623
Room_5_Flr_3 | Yes | 4 | 39.02 | 118.94 | 3.0482 | 39.95 | 13.18 | 26.0133 | 1.5 | 11.8403 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 0.36556
Room_6_Flr_3 | Yes | 4 | 39.02 | 118.93 | 3.0479 | 39.95 | 13.18 | 26.0133 | 1.5 | 11.8403 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 0.3656
Corridor_Flr_3 | Yes | 4 | 389.4 | 1186.91 | 3.048 | 48.31 | 15.94 | 92.9031 | 4.1915 | 5.3819 |  |  |  |  | 0.25 | 97.35 |  | 0.044299
Room_1_Flr_6 | Yes | 1 | 39.02 | 118.94 | 3.0482 | 39.95 | 13.19 | 26.0133 | 1.5 | 11.8403 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 0.36556
Room_2_Flr_6 | Yes | 1 | 39.02 | 118.93 | 3.0479 | 39.95 | 13.19 | 26.0133 | 1.5 | 11.8403 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 0.3656
Room_3_Mult9_Flr_6 | Yes | 9 | 24.53 | 74.77 | 3.0481 | 63.1801 | 6.75 | 16.3533 | 1.5 | 11.8403 | 14.3052 |  | 42.5858 |  |  | 14.1584 |  | 0.91966
Banquet_Flr_6 | Yes | 1 | 331.66 | 1010.89 | 3.048 | 97.5501 | 32.21 | 1.3935 | 237.997 | 13.9931 | 67.8406 |  |  | 10 |  | 2379.97 |  | 0.10503
Dining_Flr_6 | Yes | 1 | 331.66 | 1010.89 | 3.048 | 97.5501 | 32.21 | 1.3935 | 237.997 | 13.9931 | 67.8406 |  |  | 10 |  | 2379.97 |  | 0.10503
Kitchen_Flr_6 | Yes | 1 | 103.3 | 314.87 | 3.0481 | 87.3301 | 26.38 | 18.5806 | 5.5596 | 12.9167 | 508.2285 | 1613.4237 | 503.4582 | 8 |  | 44.4764 | 1887.788 | 0.30186
Corridor_Flr_6 | Yes | 1 | 412.12 | 1256.16 | 3.048 | 137.5001 | 28.22 | 92.9031 | 4.436 | 5.3819 |  |  |  |  | 0.25 | 103.03 |  | 0.11913
Building Total Conditioned Zones |  |  | 11344.93 | 35185.06 |  | 4462.8441 | 1214.3111 |  | 1411.2773 |  |  |  | 15229.9891
Data Source | [7 empty] | 1 |  | 2 | 4, 5 | 4, 5 | 4, 5 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Commercial Reference Buildings Report
[5] Smith, V. A. and D.R. Fisher. (2001). Estimating Food Service Loads and Profiles. ASHRAE Transactions 2001. V. 107. Pt 2. Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 11.7809 | 67.2676 | 13.5344 | 68.8195 |  | 85.905 | 11.4406 | 103.8454 | 4.0102 | 13.276 | 99.5961 | 21.6382 | 24.5558 | 6.2509 | 4.15 | 0.38782
Fabric | [6 empty] | weighting factor is for all of 3B
Exterior walls - commercial space
| Construction Type | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall
| R-value (m2·K / W) | 0.4207 | 0.4207 | 0.4207 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.4327 | 1.4327 | 1.692 | 1.692 | 1.9569 | 2.2026
Exterior walls - residential space
| Construction Type | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall
| R-value (m2·K / W) | 1.1669 | 1.1669 | 1.1669 | 1.4327 | 1.4327 | 1.4327 | 1.4327 | 1.692 | 1.692 | 1.692 | 1.9569 | 1.9569 | 1.9569 | 1.9569 | 2.2026 | 2.4814
Underground walls
| Construction Type | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete
| R-value (m2·K / W) | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 1.6313 | 1.6313
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.849 | 2.849 | 2.849 | 2.849 | 2.7933 | 3.7175
Windows - fixed, commercial
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
| SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.296
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.162 | 0.162 | 0.162 | 0.223 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.212
Windows - operable, residential
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
| SHGC | 0.251 | 0.251 | 0.251 | 0.385 | 0.385 | 0.385 | 0.61 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.296
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.305 | 0.305 | 0.305 | 0.474 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.212
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement
| Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| COOLSYS1 CHILLER 1 | 721.7067 | 687.5958 | 559.4003 | 613.5664 | 417.3738 | 417.7608 | 300.8888 | 625.3148 | 295.0762 | 326.1265 | 619.3687 | 292.502 | 585.8576 | 272.7364 | 479.1796 | 240.5309
| COOLSYS1 CHILLER 2 | 721.7067 | 687.5958 | 559.4003 | 613.5664 | 417.3738 | 417.7608 | 300.8888 | 625.3148 | 295.0762 | 326.1265 | 619.3687 | 292.502 | 585.8576 | 272.7364 | 479.1796 | 240.5309
Heating (kW)
| HEATSYS1 BOILER | 2106.8007 | 2811.5062 | 2370.3824 | 3043.9012 | 2173.9682 | 2564.9428 | 2404.3016 | 3377.1861 | 2748.7006 | 2894.2612 | 3969.4165 | 3290.5072 | 4301.6083 | 3965.8732 | 4427.476 | 5422.9985
| CORRIDOR_FLR_6 UNIT HEATER COIL | 4.0479 | 9.8537 | 6.9689 | 10.7942 | 4.21 | 8.0817 | 6.6791 | 12.5042 | 10.9518 | 9.3651 | 16.6262 | 14.8857 | 19.0169 | 18.9434 | 20.2532 | 22.642
HVAC Efficiency
Air Conditioning (COP)
| COOLSYS1 CHILLER 1 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
| COOLSYS1 CHILLER 2 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
Heating Efficiency (%)
| HEATSYS1 BOILER | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| CORRIDOR_FLR_6 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HVAC Control - Economizer
| FLR_3_DOAS_FAN | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA
| FLR_6_DOAS_FAN | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA
| VAV WITH REHEAT_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| CORRIDOR_FLR_6 UNIT HEATERFAN | 0.1 | 0.26 | 0.19 | 0.28 | 0.1 | 0.22 | 0.17 | 0.31 | 0.34 | 0.23 | 0.42 | 0.47 | 0.48 | 0.56 | 0.53 | 0.53
| DINING_FLR_6 EXHAUST FAN | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84
| KITCHEN_FLR_6 EXHAUST FAN | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
| LAUNDRY_FLR_1 EXHAUST FAN | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
| ROOM_1_FLR_3 FAN COILFAN | 1.13 | 1.16 | 1.31 | 1.24 | 1.12 | 1.34 | 1.7 | 1.2 | 1.33 | 1.19 | 1.22 | 1.31 | 1.22 | 1.28 | 1.38 | 1
| ROOM_1_FLR_6 FAN COILFAN | 0.31 | 0.33 | 0.37 | 0.35 | 0.32 | 0.38 | 0.47 | 0.34 | 0.38 | 0.33 | 0.34 | 0.37 | 0.34 | 0.36 | 0.38 | 0.26
| ROOM_2_FLR_3 FAN COILFAN | 1.15 | 1.17 | 1.31 | 1.24 | 1.1 | 1.33 | 1.46 | 1.2 | 1.33 | 1.12 | 1.21 | 1.3 | 1.2 | 1.25 | 1.34 | 0.94
| ROOM_2_FLR_6 FAN COILFAN | 0.32 | 0.33 | 0.37 | 0.35 | 0.31 | 0.38 | 0.41 | 0.34 | 0.38 | 0.31 | 0.34 | 0.37 | 0.33 | 0.35 | 0.37 | 0.25
| ROOM_3_MULT19_FLR_3 FAN COILFAN | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45
| ROOM_3_MULT9_FLR_6 FAN COILFAN | 1.15 | 1.16 | 1.39 | 1.2 | 1.15 | 1.3 | 2.52 | 1.17 | 1.23 | 1.59 | 1.19 | 1.22 | 1.24 | 1.32 | 1.51 | 1.45
| ROOM_4_MULT19_FLR_3 FAN COILFAN | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45
| ROOM_5_FLR_3 FAN COILFAN | 0.98 | 0.98 | 1.12 | 1.07 | 0.94 | 1.12 | 1.4 | 1.03 | 1.09 | 0.99 | 1.04 | 1.07 | 1.05 | 1.06 | 1.16 | 0.88
| ROOM_6_FLR_3 FAN COILFAN | 1.02 | 1.02 | 1.15 | 1.1 | 0.96 | 1.14 | 1.2 | 1.06 | 1.12 | 0.97 | 1.06 | 1.09 | 1.07 | 1.08 | 1.17 | 0.88
| FLR_3_DOAS_FAN | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38
| FLR_6_DOAS_FAN | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16
| VAV WITH REHEAT_FAN | 33.5 | 33.38 | 34.13 | 34.04 | 32.39 | 34.14 | 31.21 | 33.21 | 37.4 | 32.32 | 33.56 | 37.15 | 33.74 | 35.59 | 34.59 | 32.5
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.073177 | 0.098654 | 0.069199 | 0.10514 | 0.11998 | 0.086047 | 0.14258 | 0.066366 | 0.037005 | 0.06578 | 0.097254 | 0.037008 | 0.052631 | 0.06901 | 0.052951 | 0.08908
| Total Cost ($/m2) | 26.54 | 30.96 | 20.36 | 29.41 | 30.32 | 22.04 | 31.01 | 17.28 | 8.13 | 13.79 | 23.66 | 7.85 | 12.37 | 13.95 | 11.28 | 16.47
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011451 | 0.0081755 | 0.0085451 | 0.010667 | 0.0084033 | 0.008082 | 0.0084137 | 0.010027 | 0.007167 | 0.0082999 | 0.0088354 | 0.0071664 | 0.0079652 | 0.0086709 | 0.0079624 | 0.0041874
| Total Cost ($/m2) | 5.23 | 4.89 | 4.47 | 7.8 | 5.33 | 4.92 | 6.28 | 8.8 | 5.8 | 7.37 | 8.98 | 6.78 | 9.17 | 9.61 | 10.54 | 6.98
Total Utility Costs
| Cost Intensity ($/m2) | 31.77 | 35.85 | 24.83 | 37.21 | 35.65 | 26.96 | 37.29 | 26.08 | 13.93 | 21.15 | 32.64 | 14.63 | 21.54 | 23.57 | 21.82 | 23.45
Energy - End Uses
Electricity (kWh)
| Heating | 13.8889 | 38.8889 | 838.8889 | 5.5556 | 0 | 483.3333 | 0 | 47.2222 | 2.7778 | 0 | 247.2222 | 183.3333 | 1072.2222 | 761.1111 | 1630.5556 | 3950
| Cooling | 2473577.7778 | 1922511.1111 | 1696519.4444 | 1539083.3333 | 1240972.2222 | 1267744.4444 | 829913.8889 | 1325252.7778 | 855319.4444 | 754883.3333 | 1132000 | 775008.3333 | 1037511.1111 | 664219.4444 | 784025 | 473508.3333
| Interior Lighting | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111
| Exterior Lighting | 73227.7778 | 73200 | 73186.1111 | 73175 | 73119.4444 | 73102.7778 | 73141.6667 | 73097.2222 | 73125 | 72977.7778 | 73108.3333 | 73066.6667 | 73061.1111 | 73044.4444 | 73000 | 72555.5556
| Interior Equipment | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222
| Exterior Equipment | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556
| Fans | 309716.6667 | 307955.5556 | 315072.2222 | 310077.7778 | 304750 | 314225 | 319327.7778 | 306825 | 315902.7778 | 305997.2222 | 306986.1111 | 313541.6667 | 307527.7778 | 311105.5556 | 312308.3333 | 301847.2222
| Pumps | 27263.8889 | 25947.2222 | 22369.4444 | 21572.2222 | 18236.1111 | 19922.2222 | 16083.3333 | 19786.1111 | 17569.4444 | 15366.6667 | 18391.6667 | 16661.1111 | 18725 | 16461.1111 | 17183.3333 | 17794.4444
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 21802.7778 | 21111.1111 | 21261.1111 | 20502.7778 | 20577.7778 | 20786.1111 | 20044.4444 | 20041.6667 | 20063.8889 | 19686.1111 | 19719.4444 | 19705.5556 | 19552.7778 | 19372.2222 | 19105.5556 | 18755.5556
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 4114788.8889 | 3559950 | 3338433.3333 | 3173602.7778 | 2866844.4444 | 2905452.7778 | 2467694.4444 | 2954238.8889 | 2491172.2222 | 2378100 | 2759638.8889 | 2407352.7778 | 2666638.8889 | 2294152.7778 | 2416441.6667 | 2097600
Gas (MJ)
| Heating | 163130 | 764610 | 488420 | 1309170 | 398120 | 771390 | 847750 | 2210560 | 1582800 | 1932820 | 3123500 | 2363710 | 4075290 | 3490640 | 5096210 | 7836740
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 3783270 | 4783250 | 4208800 | 5746390 | 5559180 | 4901120 | 6383390 | 6503480 | 6359940 | 6897280 | 7167980 | 7133270 | 7742140 | 7846380 | 8689130 | 9835500
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 5185050 | 6786510 | 5935860 | 8294210 | 7195950 | 6911160 | 8469800 | 9952690 | 9181400 | 10068750 | 11530130 | 10735640 | 13056070 | 12575670 | 15023990 | 18910900
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 19998290 | 19602330 | 17954220 | 19719180 | 17516590 | 17370780 | 17353500 | 20587950 | 18149620 | 18629910 | 21464830 | 19402110 | 22655970 | 20834620 | 23723180 | 26462260
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0.0044071 | 0.01234 | 0.26619 | 0.0017628 | 0 | 0.15337 | 0 | 0.014984 | 0.00088142 | 0 | 0.078447 | 0.058174 | 0.34023 | 0.24151 | 0.5174 | 1.2534
| Cooling (elec) | 784.8966 | 610.0364 | 538.3265 | 488.3701 | 393.7757 | 402.2709 | 263.3419 | 420.519 | 271.4034 | 239.5338 | 359.1975 | 245.9197 | 329.215 | 210.765 | 248.7808 | 150.25
| Interior Lighting (elec) | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025
| Exterior Lighting (elec) | 23.2361 | 23.2273 | 23.2229 | 23.2193 | 23.2017 | 23.1964 | 23.2088 | 23.1946 | 23.2035 | 23.1567 | 23.1982 | 23.185 | 23.1832 | 23.1779 | 23.1638 | 23.0228
| Interior Equipment (elec) | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696
| Exterior Equipment (elec) | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184
| Fans (elec) | 98.2769 | 97.7181 | 99.9763 | 98.3915 | 96.7009 | 99.7075 | 101.3266 | 97.3593 | 100.2398 | 97.0967 | 97.4105 | 99.4906 | 97.5823 | 98.7176 | 99.0993 | 95.7798
| Pumps (elec) | 8.6512 | 8.2334 | 7.0981 | 6.8451 | 5.7865 | 6.3216 | 5.1034 | 6.2784 | 5.575 | 4.876 | 5.8359 | 5.2868 | 5.9417 | 5.2233 | 5.4525 | 5.6464
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 6.9183 | 6.6988 | 6.7464 | 6.5058 | 6.5296 | 6.5957 | 6.3603 | 6.3595 | 6.3665 | 6.2466 | 6.2572 | 6.2528 | 6.2043 | 6.147 | 6.0624 | 5.9514
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1305.6731 | 1129.6159 | 1059.3259 | 1007.0232 | 909.685 | 921.9359 | 783.0298 | 937.4163 | 790.4796 | 754.6004 | 875.6673 | 763.8826 | 846.1573 | 727.9629 | 766.7666 | 665.5943
Gas (MJ/m2)
| Heating (gas) | 14.3787 | 67.3945 | 43.0505 | 115.3933 | 35.0912 | 67.9921 | 74.7226 | 194.8439 | 139.5116 | 170.3632 | 275.3125 | 208.3428 | 359.2055 | 307.6731 | 449.1917 | 690.7483
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 333.4661 | 421.6067 | 370.9733 | 506.5001 | 489.9989 | 431.996 | 562.6467 | 573.2317 | 560.5798 | 607.9422 | 631.8023 | 628.7429 | 682.4101 | 691.598 | 765.8799 | 866.9236
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 457.0223 | 598.1786 | 523.2004 | 731.0708 | 634.2676 | 609.1656 | 746.5477 | 877.253 | 809.2697 | 887.4828 | 1016.2922 | 946.264 | 1150.7921 | 1108.4485 | 1324.2491 | 1666.8503
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 1762.6954 | 1727.7945 | 1582.5263 | 1738.094 | 1543.9526 | 1531.1006 | 1529.5775 | 1814.6693 | 1599.7493 | 1642.0832 | 1891.9596 | 1710.1467 | 1996.9494 | 1836.4114 | 2091.0157 | 2332.4446
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 629.8168 | 612.833 | 556.7552 | 570.8259 | 488.6012 | 438.5513 | 433.8267 | 485.0101 | 432.1967 | 396.7003 | 404.3948 | 425.9744 | 387.0716 | 395.0553 | 383.7391 | 381.1546
| Feb | 632.6148 | 618.0988 | 559.1268 | 552.5027 | 486.8169 | 486.9656 | 437.7043 | 435.8438 | 432.9252 | 442.7436 | 401.0728 | 425.9757 | 394.9423 | 421.2039 | 402.5641 | 382.8915
| Mar | 638.6441 | 611.3742 | 572.2468 | 587.4108 | 486.9552 | 489.7227 | 437.6897 | 594.0613 | 434.292 | 446.2392 | 548.3611 | 431.9056 | 466.615 | 423.4563 | 413.2254 | 405.2399
| Apr | 644.2826 | 620.1771 | 572.6198 | 587.1042 | 491.1385 | 496.5511 | 436.8295 | 590.6829 | 434.2784 | 446.1424 | 534.4977 | 432.9984 | 560.7413 | 424.1977 | 465.9686 | 396.9298
| May | 646.3389 | 624.2053 | 577.1864 | 590.4605 | 486.7536 | 497.6449 | 437.5747 | 594.1452 | 432.9063 | 446.9511 | 593.9607 | 433.0368 | 575.8101 | 423.6094 | 514.8917 | 393.4339
| Jun | 640.2379 | 613.7647 | 581.4705 | 594.0712 | 487.6928 | 500.1701 | 437.1849 | 593.2967 | 432.7216 | 446.4078 | 599.2377 | 433.1035 | 574.2631 | 406.992 | 517.2153 | 392.5875
| Jul | 626.5618 | 622.3393 | 580.9349 | 587.9404 | 485.506 | 500.4242 | 436.9083 | 591.6189 | 433.7415 | 446.2849 | 590.8282 | 432.088 | 571.7111 | 419.456 | 515.1119 | 391.7646
| Aug | 629.2002 | 617.0342 | 581.8364 | 584.1342 | 484.7037 | 500.113 | 438.4751 | 603.6024 | 433.3151 | 446.4261 | 586.6008 | 432.3562 | 570.6942 | 423.1538 | 518.3865 | 393.088
| Sep | 628.7878 | 628.6542 | 579.1133 | 580.1201 | 487.0047 | 497.5958 | 436.5079 | 593.6291 | 432.7388 | 447.1141 | 593.006 | 433.0234 | 568.8663 | 424.6575 | 515.1524 | 409.3343
| Oct | 637.1936 | 609.4171 | 572.1209 | 583.2502 | 488.0144 | 494.0548 | 436.7217 | 586.1591 | 434.7496 | 447.0768 | 587.9329 | 432.8263 | 558.0396 | 425.6208 | 499.6727 | 409.2547
| Nov | 638.0162 | 612.0028 | 559.6415 | 566.6074 | 487.6302 | 488.0574 | 438.5263 | 579.3866 | 433.4547 | 434.488 | 589.6725 | 432.3572 | 439.7493 | 417.3593 | 421.1187 | 383.9101
| Dec | 636.2717 | 613.545 | 556.7659 | 558.6334 | 490.1439 | 487.0945 | 428.634 | 440.1678 | 423.2566 | 395.9596 | 405.1495 | 412.4612 | 388.9802 | 396.1052 | 384.5798 | 378.3607
Time of Peak Electrical Demand
| Jan | 04-JAN-20:00 | 18-JAN-20:10 | 27-JAN-20:10 | 24-JAN-20:10 | 26-JAN-20:10 | 29-JAN-08:00 | 27-JAN-20:19 | 09-JAN-06:10 | 26-JAN-20:19 | 27-JAN-20:00 | 17-JAN-20:00 | 24-JAN-20:19 | 30-JAN-20:00 | 30-JAN-20:00 | 20-JAN-20:49 | 21-JAN-08:00
| Feb | 17-FEB-20:10 | 22-FEB-20:00 | 27-FEB-20:10 | 22-FEB-07:10 | 23-FEB-20:10 | 08-FEB-20:10 | 13-FEB-20:00 | 13-FEB-06:30 | 13-FEB-20:10 | 21-FEB-20:10 | 17-FEB-20:00 | 10-FEB-20:00 | 19-FEB-20:00 | 03-FEB-20:30 | 22-FEB-20:00 | 28-FEB-20:19
| Mar | 14-MAR-19:10 | 31-MAR-19:10 | 17-MAR-19:10 | 28-MAR-19:10 | 29-MAR-19:10 | 22-MAR-19:10 | 29-MAR-19:00 | 09-MAR-20:10 | 16-MAR-19:10 | 28-MAR-19:10 | 31-MAR-18:10 | 27-MAR-19:30 | 19-MAR-19:00 | 29-MAR-19:19 | 22-MAR-19:10 | 29-MAR-19:00
| Apr | 19-APR-19:10 | 04-APR-19:10 | 26-APR-19:10 | 13-APR-19:10 | 11-APR-19:10 | 28-APR-19:10 | 27-APR-19:40 | 05-APR-19:10 | 28-APR-19:10 | 14-APR-19:30 | 28-APR-17:19 | 28-APR-19:19 | 16-APR-19:10 | 19-APR-19:19 | 04-APR-17:30 | 28-APR-19:00
| May | 05-MAY-19:10 | 11-MAY-19:10 | 19-MAY-19:19 | 26-MAY-19:40 | 08-MAY-19:10 | 31-MAY-19:10 | 03-MAY-19:19 | 05-MAY-19:10 | 08-MAY-19:00 | 01-MAY-19:19 | 04-MAY-19:10 | 12-MAY-19:49 | 15-MAY-19:30 | 10-MAY-19:49 | 31-MAY-19:49 | 12-MAY-19:00
| Jun | 02-JUN-19:10 | 14-JUN-19:19 | 26-JUN-19:40 | 12-JUN-19:49 | 29-JUN-19:00 | 21-JUN-19:10 | 08-JUN-19:00 | 05-JUN-19:30 | 12-JUN-19:00 | 08-JUN-19:00 | 15-JUN-19:30 | 01-JUN-19:00 | 22-JUN-19:00 | 15-JUN-19:00 | 15-JUN-19:00 | 07-JUN-19:10
| Jul | 24-JUL-19:00 | 28-JUL-19:19 | 10-JUL-19:49 | 11-JUL-19:49 | 10-JUL-19:10 | 06-JUL-19:10 | 06-JUL-19:00 | 19-JUL-19:30 | 12-JUL-19:19 | 12-JUL-19:00 | 17-JUL-19:19 | 10-JUL-19:30 | 03-JUL-19:00 | 31-JUL-19:00 | 28-JUL-19:49 | 05-JUL-19:10
| Aug | 04-AUG-19:10 | 11-AUG-19:10 | 23-AUG-19:10 | 29-AUG-19:10 | 23-AUG-19:10 | 01-AUG-19:49 | 02-AUG-19:30 | 18-AUG-19:10 | 24-AUG-19:19 | 16-AUG-19:19 | 01-AUG-19:10 | 23-AUG-19:10 | 15-AUG-19:19 | 23-AUG-19:00 | 23-AUG-19:10 | 31-AUG-19:10
| Sep | 08-SEP-19:00 | 26-SEP-19:10 | 11-SEP-19:10 | 12-SEP-19:10 | 20-SEP-19:10 | 11-SEP-19:10 | 18-SEP-19:00 | 08-SEP-19:10 | 08-SEP-19:10 | 19-SEP-19:10 | 26-SEP-19:10 | 15-SEP-19:40 | 13-SEP-19:10 | 21-SEP-19:10 | 06-SEP-19:10 | 20-SEP-19:10
| Oct | 24-OCT-19:10 | 26-OCT-19:10 | 02-OCT-19:10 | 12-OCT-19:10 | 20-OCT-19:00 | 06-OCT-19:10 | 25-OCT-19:00 | 20-OCT-19:10 | 04-OCT-19:10 | 05-OCT-19:10 | 11-OCT-19:10 | 02-OCT-19:10 | 08-OCT-19:10 | 23-OCT-19:10 | 07-OCT-19:10 | 03-OCT-19:00
| Nov | 16-NOV-20:10 | 24-NOV-20:10 | 06-NOV-20:10 | 22-NOV-20:00 | 20-NOV-20:10 | 21-NOV-20:10 | 16-NOV-20:10 | 03-NOV-19:10 | 10-NOV-20:10 | 03-NOV-19:00 | 02-NOV-19:10 | 03-NOV-19:10 | 02-NOV-17:19 | 20-NOV-20:00 | 02-NOV-19:00 | 14-NOV-07:00
| Dec | 28-DEC-20:10 | 20-DEC-20:40 | 13-DEC-20:00 | 04-DEC-20:00 | 29-DEC-20:10 | 05-DEC-20:10 | 17-DEC-20:10 | 05-DEC-06:19 | 05-DEC-20:19 | 31-DEC-20:00 | 11-DEC-20:00 | 22-DEC-20:00 | 01-DEC-20:00 | 01-DEC-20:00 | 01-DEC-20:00 | 18-DEC-07:00
Source Energy
| Total Source Energy (GJ) | 54797.58 | 53957.92 | 44496.03 | 47490.89 | 39800.36 | 44961.07 | 36744.07 | 48900.03 | 39782.65 | 25908.62 | 47819.36 | 40478.67 | 47252.08 | 42440.74 | 46305.32 | 47624.16
| Total Source Energy (MJ/m2) | 4829.99 | 4755.98 | 3921.98 | 4185.96 | 3508.1 | 3962.97 | 3238.71 | 4310.16 | 3506.54 | 2283.65 | 4214.91 | 3567.88 | 4164.91 | 3740.83 | 4081.46 | 4197.7
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9
| Total Building | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9
Emissions
| Carbon Equivalent (kg) | 1221980 | 1309840 | 1114830 | 1127150 | 464798.684 | 1104560 | 441122.5811 | 976691.4578 | 1183200 | 354773.7539 | 1679220 | 1176990 | 1148210 | 1065140 | 1098050 | 931252.8437
| CO2 (kg) | 2883200 | 3333260 | 2679280 | 2650860 | 1269400 | 2681060 | 1211230 | 2306320 | 2849550 | 936031.416 | 3995410 | 2850740 | 2784520 | 2605130 | 2689610 | 2463810
| NOX (kg) | 4853.6503 | 4237.5164 | 4286.4851 | 4676.6815 | 1105.8505 | 4133.1559 | 1059.5255 | 4045.2729 | 4594.6385 | 1137.3449 | 6726.7476 | 4528.1721 | 4457.5117 | 4056.1552 | 4190.3114 | 2746.8341
| SO2 (kg) | 17614.3262 | 16982.7807 | 13426.0968 | 11141.5727 | 8344.102 | 15984.1617 | 7182.9655 | 10786.8198 | 10880.9145 | 1840.7801 | 18600.8549 | 10515.3079 | 6297.1926 | 6129.0334 | 5707.2163 | 10682.6913
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0808 | 0.0485 | 0.0371 | 0.0415 | 0.0045 | 0.0307 | 0.0041 | 0.0445 | 0.0434 | 0.0083 | 0.0573 | 0.0421 | 0.0473 | 0.0438 | 0.0432 | 0.0382
| Water for Electricity (m3) | 2179.84 | 5792.46 | 99166.1 | 19814.7 | 50335.4 | 79708.2 | 43327.2 | 670.7232 | 11311.9 | 24296.6 | 4281.42 | 10931.3 | 4137.13 | 145321 | 3748.97 | 2143.08

## Picture
DOE Commercial Building Benchmark - Large Hotel

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
BLDG_ELEVATORS | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | 5.9 | 41.3 | 2153.5
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4 | 10.9 | 75.25 | 3923.75
|  |  | Sat | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4 | 10.25
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4 | 10.5
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | 8.55 | 58.7 | 3060.79
|  |  | Sat | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | 7.85
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3 | 8.1
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9 | 13.9 | 96.4 | 5026.57
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 13.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 13
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
GuestRoom_Eqp_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | 8.82 | 53.11 | 2769.31
|  |  | Sat, Sun, Hol | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | 9.01
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
GuestRoom_Ltg_Sch_Base | Fraction | Through 12/31 | WD | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33 | 9.51 | 58.28 | 3038.89
|  |  | Sat, Sun, Hol | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41 | 10.73
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
GuestRoom_Occ_Sch | Fraction | Through 12/31 | WD | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.28 | 0.28 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.2 | 0.35 | 0.35 | 0.35 | 0.5 | 0.5 | 0.58 | 0.65 | 0.65 | 9.87 | 59.52 | 3103.54
|  |  | Sat, Sun, Hol | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.34 | 0.34 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.34 | 0.35 | 0.65 | 0.65 | 0.5 | 0.5 | 0.5 | 10.17
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
INFIL_QUARTER_ON_SCH | Fraction | Through 12/31 | All | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6 | 42 | 2190
Kitchen_Elec_Equip_SCH | Fraction | Through 12/31 | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9 | 23.6 | 1230.57
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9
|  |  | SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9
Kitchen_Gas_Equip_SCH | Fraction | Through 12/31 | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65 | 21.9 | 1141.93
|  |  | SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65
LaundryRoom_Eqp_Elec_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 2085.71
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
LaundryRoom_Eqp_Gas_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 2085.71
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Lobby_Occ_Sch | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 6.6 | 38.6 | 2012.71
|  |  | Sat, Sun, Hol | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen_Exhaust_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 17 | 119 | 6205
CLGSETP_SCH | Temperature | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 618 | 4326 | 225570
HTGSETP_SCH | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 469 | 3283 | 171185
Corr_CLGSETP_SCH | Temperature | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
Corr_HTGSETP_SCH | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
Guest_CLGSETP_SCH | Temperature | Through 12/31 | All | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 4032 | 210240
Guest_HTGSETP_SCH | Temperature | Through 12/31 | All | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 3528 | 183960
Kitchen_CLGSETP_SCH | Temperature | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 652 | 4564 | 237980
Kitchen_HTGSETP_SCH | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 435 | 3045 | 158775
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
HVACOperationSchd | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 17 | 119 | 6205
MinOA_Sched | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 17 | 119 | 6205
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Kitchen_Flr_6_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Kitchen_Flr_6_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Kitchen_Flr_6_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Kitchen_Flr_6_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Kitchen_Flr_6_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
Kitchen_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.5 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | 9 | 63.3 | 3300.64
|  |  | Sat, WinterDesign | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.4 | 0.5 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3 | 9.3
|  |  | Sun, Hol, Other | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.55 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2 | 9
GuestRoom_SWH_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25 | 8 | 40 | 2085.71
|  |  | Other | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35 | 7.8
LaundryRoom_SWH_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 56 | 2920
Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Guest Room Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Guest Room Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Kitchen Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Kitchen Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Laundry Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Laundry Water Equipment Temp Sched | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600