## BuildingSummary
Building Summary Outpatient Health Care new construction
|  | Value | Data Source
Program
| Building Name | Outpatient Health Care Reference Building new construction 90.1-2004
| Available Fuel Types | gas, electricity
| Principal Building Activity | Health care, outpatient
Form
| Total Floor Area (m2) | 3804.01 | Doebber, I.; Bonnema, E.; Pless, S.; Torcellini, P. (2009). Technical Support Document: Development of the Advanced Energy Design Guide for Small Hospitals and Health Care Facilities – 30% Energy Savings. Golden, CO: National Renewable Energy Laboratory, NREL/TP-550-46314. Available at www.nrel.gov/docs/fy10osti/46314.pdf
| Building Shape | Irregular
| Aspect Ratio | 1.43
| Number of Floors | 3
Window Fraction (Window to Wall Ratio)
| South | 0.2408
| East | 0.1914
| North | 0.2052
| West | 0.1288
| Total | 0.1985
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | Zoned By Use
| Floor to Ceiling Height (m) | 3.05
| Floor to Floor Height (m) | 3.05
| Roof type | Built-up flat roof, insulation entirely above deck | Doebber, et al. 2009
Fabric
Exterior walls
| Construction Type | Steel frame | Doebber, et al. 2009
| Gross Dimensions - Total Area (m2) | 1553.34
| Net Dimensions - Total Area (m2) | 1245.05
| Wall to Skin Ratio | 0.53076
Roof
| Construction Type | IEAD | Doebber, et al. 2009
| Gross Dimensions - Total Area (m2) | 1373.29
| Net Dimensions - Total Area (m2) | 1373.29
| Roof to Skin Ratio | 0.46924
Window Dimensions (m2)
| South | 114.08
| East | 57.97
| North | 97.22
| West | 39.02
| Total Area (m2) | 308.29
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor | Doebber, et al. 2009
| Construction | 8in slab w/carpet | Doebber, et al. 2009
| Dimensions - Total Area (m2) | 1373.29
Interior Partitions
| Construction | Gypsum Board
Dimensions - Total Area (m2)
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 2746.58
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ft3/min per ft2 of exterior wall) | 0.27988
HVAC
| System Type | Packaged VAV With Reheat | Doebber, et al. 2009
| Heating Type | Hot Water Boiler, Furnace | Doebber, et al. 2009
| Cooling Type | DX Cooling Coil | Doebber, et al. 2009
| Fan Control | VAV | Doebber, et al. 2009
Service Water Heating
| SWH Type | Gas Water Heater
| Fuel | Gas
| Thermal Efficiency (%) | 80 | Standard 90.1-2004
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 240.48

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Floor 1 Anesthesia | Yes | 1 | 10.0335 | 30.5822 | 3.048 | 8.36 | 2.23 |  | 0 | 32.29 | 21.53 |  | 3.7854 |  | 6 | 60.2012 | 67.9604 | 0.29752
Floor 1 Bio Haz | Yes | 1 | 5.2026 | 15.8574 | 3.048 | 0 | 0 |  | 0 | 9.69 | 1.08 |  |  |  | 0.75 | 3.9019 |  | 0
Floor 1 Café | Yes | 1 | 39.0193 | 118.9309 | 3.048 | 18.58 | 8.92 | 1 | 39.0193 | 9.69 | 10.76 |  |  | 10 |  | 390.1928 |  | 0.17003
Floor 1 Clean | Yes | 1 | 11.7058 | 35.6793 | 3.048 | 0 | 0 | 5 | 2.3412 | 12.92 | 21.53 |  |  |  | 1.5 | 17.5587 |  | 0
Floor 1 Clean Work | Yes | 1 | 15.329 | 46.7228 | 3.048 | 0 | 0 | 5 | 3.0658 | 12.92 | 21.53 |  |  |  | 1.5 | 22.9935 |  | 0
Floor 1 Dictation | Yes | 1 | 11.7058 | 35.6793 | 3.048 | 0 | 0 | 20 | 0.58529 | 11.84 | 11.84 |  |  | 10 |  | 5.8529 |  | 0
Floor 1 Dressing Room | Yes | 1 | 4.1806 | 12.7426 | 3.048 | 8.36 | 2.32 | 20 | 0.20903 | 11.84 | 11.84 |  |  | 10 |  | 2.0903 |  | 0.71404
Floor 1 Electrical Room | No | 1 | 9.1045 | 27.7505 | 3.048 | 6.5 | 0 |  | 0 | 16.15 | 53.82 | [6 empty] | 0.25493
Floor 1 Elevator Pump Room | No | 1 | 8.4542 | 25.7684 | 3.048 | 18.58 | 0 |  | 0 | 16.15 | 529.29 | [6 empty] | 0.78476
Floor 1 Humid | Yes | 1 | 5.0168 | 15.2911 | 3.048 | 0 | 0 | 20 | 0.25084 | 11.84 | 11.84 |  |  | 10 |  | 2.5084 |  | 0
Floor 1 IT Hall | Yes | 1 | 13.0064 | 39.6436 | 3.048 | 0 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 3.2516 |  | 0
Floor 1 IT Room | Yes | 1 | 10.4051 | 31.7149 | 3.048 | 0 | 0 | 20 | 0.52026 | 11.84 | 11.84 |  |  | 10 |  | 5.2026 |  | 0
Floor 1 Lobby | Yes | 1 | 57.7857 | 176.1309 | 3.048 | 20.44 | 8.92 | 3.3333 | 17.3357 | 13.99 | 11.84 |  |  | 8 |  | 138.6857 |  | 0.12631
Floor 1 Lobby Hall | Yes | 1 | 22.2967 | 67.9605 | 3.048 | 0 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 5.5742 |  | 0
Floor 1 Lobby Toilet | No | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 |  | 0 | 9.69 | 4.31 | [5 empty] | 42.4752 | 0.39645
Floor 1 Locker Room | Yes | 1 | 61.316 | 186.8913 | 3.048 | 20.44 | 5.57 | 6.6667 | 9.1974 | 8.61 | 32.29 |  |  | 8 |  | 73.5792 |  | 0.11903
Floor 1 Locker Room Hall | Yes | 1 | 46.0799 | 140.4517 | 3.048 | 0 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 11.52 |  | 0
Floor 1 Lounge | Yes | 1 | 33.4451 | 101.9407 | 3.048 | 0 | 0 | 6.6667 | 5.0168 | 8.61 | 32.29 |  |  | 8 | 0 | 40.1341 |  | 0
Floor 1 Med Gas | Yes | 1 | 5.2026 | 15.8574 | 3.048 | 13.94 | 0 |  | 0 | 9.69 | 1.08 |  |  |  | 0.75 | 3.9019 |  | 1.3138
Floor 1 MRI Control Room | Yes | 1 | 15.6077 | 47.5723 | 3.048 | 4.65 | 0 | 5 | 3.1215 | 4.31 | 11.84 |  | 3.7854 |  | 1.5 | 23.4116 | 79.2871 | 0.10638
Floor 1 MRI Hall | Yes | 1 | 13.6567 | 41.6258 | 3.048 | 0 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 3.4142 |  | 0
Floor 1 MRI Room | Yes | 1 | 40.8773 | 124.5942 | 3.048 | 0 | 0 | 5 | 8.1755 | 4.31 | 571.116 |  | 3.7854 |  | 1.5 | 61.316 | 207.6567 | 0
Floor 1 MRI Toilet | No | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 |  | 0 | 9.69 | 4.31 | [5 empty] | 42.4752 | 0.39645
Floor 1 Nourishment | Yes | 1 | 16.9084 | 51.5367 | 3.048 | 0 | 0 | 5 | 3.3817 | 10.76 | 21.53 |  |  | 10 |  | 33.8167 |  | 0
Floor 1 Nurse Hall | Yes | 1 | 46.0799 | 140.4517 | 3.048 | 0 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 11.52 |  | 0
Floor 1 Nurse Janitor | No | 1 | 5.0168 | 15.2911 | 3.048 | 0 | 0 |  | 0 | 9.69 | 0 | [6 empty] | 0
Floor 1 Nurse Station | Yes | 1 | 24.2477 | 73.907 | 3.048 | 0 | 0 | 5 | 4.8495 | 10.76 | 21.53 |  |  | 10 |  | 48.4954 |  | 0
Floor 1 Nurse Toilet | No | 1 | 5.0168 | 15.2911 | 3.048 | 0 | 0 |  | 0 | 9.69 | 4.31 | [5 empty] | 42.4752 | 0
Floor 1 Office | Yes | 1 | 44.8722 | 136.7705 | 3.048 | 0 | 0 | 20 | 2.2436 | 11.84 | 11.84 |  |  | 10 |  | 22.4361 |  | 0
Floor 1 Operating Room 1 | Yes | 1 | 42.7354 | 130.2576 | 3.048 | 39.95 | 8.92 | 5 | 8.5471 | 23.68 | 43.07 | 75.29 | 22.7124 |  |  | 108.5479 |  | 0.3338
Floor 1 Operating Room 2 | Yes | 1 | 44.5935 | 135.921 | 3.048 | 22.3 | 6.69 | 5 | 8.9187 | 23.68 | 43.07 | 75.29 | 22.7124 |  |  | 113.2674 |  | 0.17856
Floor 1 Operating Room 3 | Yes | 1 | 44.2218 | 134.7883 | 3.048 | 0 | 0 | 5 | 8.8444 | 23.68 | 43.07 | 75.29 | 22.7124 |  |  | 112.3235 |  | 0
Floor 1 PACU | Yes | 1 | 10.0335 | 30.5822 | 3.048 | 0 | 0 | 5 | 2.0067 | 8.61 | 32.29 |  | 3.7854 |  |  | 16.9901 |  | 0
Floor 1 Pre-Op Hall | Yes | 1 | 49.0528 | 149.5131 | 3.048 | 0 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 12.2632 |  | 0
Floor 1 Pre-Op Room 1 | Yes | 1 | 17.5587 | 53.5189 | 3.048 | 3.72 | 0 | 10 | 1.7559 | 7.53 | 21.53 |  | 3.7854 |  |  | 29.7327 |  | 0.07565
Floor 1 Pre-Op Room 2 | Yes | 1 | 31.4012 | 95.711 | 3.048 | 0 | 0 | 10 | 3.1401 | 7.53 | 21.53 |  | 3.7854 |  |  | 53.1727 |  | 0
Floor 1 Pre-Op Toilet | No | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 |  | 0 | 9.69 | 4.31 | [5 empty] | 42.4752 | 0.39645
Floor 1 Procedure Room | Yes | 1 | 26.4774 | 80.7031 | 3.048 | 17.65 | 5.57 | 5 | 5.2955 | 29.06 | 32.29 |  | 3.7854 |  |  | 67.2525 |  | 0.23803
Floor 1 Reception | Yes | 1 | 47.2876 | 144.1329 | 3.048 | 12.08 | 3.34 | 3.3333 | 14.1863 | 13.99 | 11.84 |  |  | 8 |  | 113.4904 |  | 0.091218
Floor 1 Reception Hall | Yes | 1 | 11.8916 | 36.2456 | 3.048 | 0 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 2.9729 |  | 0
Floor 1 Recovery Room | Yes | 1 | 50.1676 | 152.9111 | 3.048 | 41.81 | 8.92 | 5 | 10.0335 | 8.61 | 32.29 |  | 3.7854 |  |  | 84.9505 |  | 0.29759
Floor 1 Scheduling | Yes | 1 | 11.0555 | 33.6971 | 3.048 | 6.5 | 0.74 | 20 | 0.55277 | 11.84 | 11.84 |  |  | 10 |  | 5.5277 |  | 0.20994
Floor 1 Scrub | Yes | 1 | 7.8039 | 23.7862 | 3.048 | 0 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 1.951 |  | 0
Floor 1 Soil | Yes | 1 | 11.7058 | 35.6793 | 3.048 | 0 | 0 | 5 | 2.3412 | 12.92 | 21.53 |  |  |  | 7.5 | 87.7934 | 99.1089 | 0
Floor 1 Soil Hold | Yes | 1 | 5.2026 | 15.8574 | 3.048 | 0 | 0 | 5 | 1.0405 | 12.92 | 21.53 |  |  |  | 7.5 | 39.0193 | 44.0468 | 0
Floor 1 Soil Work | Yes | 1 | 16.7225 | 50.9704 | 3.048 | 0 | 0 | 5 | 3.3445 | 12.92 | 21.53 |  |  |  | 7.5 | 125.4191 | 141.5841 | 0
Floor 1 Step Down | Yes | 1 | 27.8709 | 84.9506 | 3.048 | 34.37 | 6.69 | 5 | 5.5742 | 8.61 | 32.29 |  | 3.7854 |  |  | 47.1947 |  | 0.44034
Floor 1 Sterile Hall | Yes | 1 | 57.2283 | 174.4319 | 3.048 | 7.43 | 2.23 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 14.3071 |  | 0.046359
Floor 1 Sterile Storage | Yes | 1 | 36.7896 | 112.1348 | 3.048 | 0 | 0 |  | 0 | 9.69 | 1.08 |  |  |  | 0.75 | 27.5922 |  | 0
Floor 1 Storage | No | 1 | 85.4708 | 260.5152 | 3.048 | 58.5301 | 8.36 |  | 0 | 9.69 | 0 | [6 empty] | 0.6016
Floor 1 Sub-Sterile | Yes | 1 | 18.209 | 55.5011 | 3.048 | 13.01 | 2.97 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 4.5522 |  | 0.25512
Floor 1 Utility Hall | Yes | 1 | 23.7832 | 72.4912 | 3.048 | 14.86 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 5.9458 |  | 0.2231
Floor 1 Utility Janitor | No | 1 | 3.9019 | 11.8931 | 3.048 | 0 | 0 |  | 0 | 9.69 | 0 | [6 empty] | 0
Floor 1 Utility Room | No | 1 | 33.4451 | 101.9407 | 3.048 | 16.72 | 2.23 |  | 0 | 9.69 | 1.08 | [6 empty] | 0.53559
Floor 1 Vestibule | Yes | 1 | 6.689 | 20.3881 | 3.048 | 7.43 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 1.6723 |  | 0.39663
Floor 2 Conference | Yes | 1 | 31.2154 | 95.1447 | 3.048 | 37.16 | 8.92 | 2 | 15.6077 | 13.99 | 10.76 |  |  | 10 |  | 156.0771 |  | 0.42508
Floor 2 Conference Toilet | No | 1 | 5.9458 | 18.1228 | 3.048 | 0 | 0 |  | 0 | 9.69 | 4.31 | [5 empty] | 50.3426 | 0
Floor 2 Dictation | Yes | 1 | 6.5032 | 19.8218 | 3.048 | 0 | 0 | 20 | 0.32516 | 11.84 | 11.84 |  |  | 10 |  | 3.2516 |  | 0
Floor 2 Exam 1 | Yes | 1 | 33.4451 | 101.9407 | 3.048 | 39.02 | 8.92 | 5 | 6.689 | 16.15 | 11.84 |  |  |  | 1.5 | 50.1676 |  | 0.4166
Floor 2 Exam 2 | Yes | 1 | 50.1676 | 152.9111 | 3.048 | 16.72 | 3.72 | 5 | 10.0335 | 16.15 | 11.84 |  |  |  | 1.5 | 75.2515 |  | 0.11901
Floor 2 Exam 3 | Yes | 1 | 66.8902 | 203.8815 | 3.048 | 22.3 | 5.95 | 5 | 13.378 | 16.15 | 11.84 |  |  |  | 1.5 | 100.3353 |  | 0.11904
Floor 2 Exam 4 | Yes | 1 | 7.8039 | 23.7862 | 3.048 | 6.5 | 2.23 | 5 | 1.5608 | 16.15 | 11.84 |  |  |  | 1.5 | 11.7058 |  | 0.29742
Floor 2 Exam 5 | Yes | 1 | 32.5161 | 99.109 | 3.048 | 23.23 | 5.95 | 5 | 6.5032 | 16.15 | 11.84 |  |  |  | 1.5 | 48.7741 |  | 0.2551
Floor 2 Exam 6 | Yes | 1 | 20.9032 | 63.713 | 3.048 | 13.94 | 4.18 | 5 | 4.1806 | 16.15 | 11.84 |  |  |  | 1.5 | 31.3548 |  | 0.23813
Floor 2 Exam 7 | Yes | 1 | 73.5792 | 224.2696 | 3.048 | 22.3 | 5.57 | 5 | 14.7158 | 16.15 | 11.84 |  |  |  | 1.5 | 110.3688 |  | 0.10822
Floor 2 Exam 8 | Yes | 1 | 25.0838 | 76.4556 | 3.048 | 16.72 | 5.57 | 5 | 5.0168 | 16.15 | 11.84 |  |  |  | 1.5 | 37.6257 |  | 0.23801
Floor 2 Exam 9 | Yes | 1 | 36.7896 | 112.1348 | 3.048 | 11.15 | 2.79 | 5 | 7.3579 | 16.15 | 11.84 |  |  |  | 1.5 | 55.1844 |  | 0.10822
Floor 2 Exam Hall 1 | Yes | 1 | 16.7225 | 50.9704 | 3.048 | 5.57 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 4.1806 |  | 0.11894
Floor 2 Exam Hall 2 | Yes | 1 | 16.7225 | 50.9704 | 3.048 | 5.57 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 4.1806 |  | 0.11894
Floor 2 Exam Hall 3 | Yes | 1 | 16.7225 | 50.9704 | 3.048 | 5.57 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 4.1806 |  | 0.11894
Floor 2 Exam Hall 4 | Yes | 1 | 18.3948 | 56.0674 | 3.048 | 5.57 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 4.5987 |  | 0.10812
Floor 2 Exam Hall 5 | Yes | 1 | 18.3948 | 56.0674 | 3.048 | 5.57 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 4.5987 |  | 0.10812
Floor 2 Exam Hall 6 | Yes | 1 | 18.3948 | 56.0674 | 3.048 | 5.57 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 4.5987 |  | 0.10812
Floor 2 Janitor | No | 1 | 5.8529 | 17.8396 | 3.048 | 14.86 | 0 |  | 0 | 9.69 | 0 | [6 empty] | 0.90658
Floor 2 Lounge | Yes | 1 | 7.4322 | 22.6535 | 3.048 | 0 | 0 | 6.6667 | 1.1148 | 8.61 | 32.29 |  |  | 8 |  | 8.9187 |  | 0
Floor 2 Nurse Station 1 | Yes | 1 | 13.9355 | 42.4753 | 3.048 | 0 | 0 | 5 | 2.7871 | 10.76 | 21.53 |  |  | 10 |  | 27.8709 |  | 0
Floor 2 Nurse Station 2 | Yes | 1 | 16.7225 | 50.9704 | 3.048 | 0 | 0 | 5 | 3.3445 | 10.76 | 21.53 |  |  | 10 |  | 33.4451 |  | 0
Floor 2 Office | Yes | 1 | 52.0257 | 158.5745 | 3.048 | 37.16 | 8.92 | 20 | 2.6013 | 11.84 | 11.84 |  |  | 10 |  | 26.0129 |  | 0.25505
Floor 2 Office Hall | Yes | 1 | 41.2489 | 125.7269 | 3.048 | 0 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 10.3122 |  | 0
Floor 2 Reception | Yes | 1 | 91.4166 | 278.638 | 3.048 | 45.52 | 16.72 | 3.3333 | 27.425 | 13.99 | 11.84 |  |  | 8 |  | 219.3998 |  | 0.1778
Floor 2 Reception Hall | Yes | 1 | 52.3973 | 159.7072 | 3.048 | 87.3301 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 13.0993 |  | 0.59513
Floor 2 Reception Toilet | No | 1 | 11.7058 | 35.6793 | 3.048 | 0 | 0 |  | 0 | 9.69 | 4.31 | [5 empty] | 99.1089 | 0
Floor 2 Scheduling 1 | Yes | 1 | 30.1006 | 91.7467 | 3.048 | 0 | 0 | 20 | 1.505 | 11.84 | 11.84 |  |  | 10 |  | 15.0503 |  | 0
Floor 2 Scheduling 2 | Yes | 1 | 31.7728 | 96.8437 | 3.048 | 0 | 0 | 20 | 1.5886 | 11.84 | 11.84 |  |  | 10 |  | 15.8864 |  | 0
Floor 2 Storage 1 | No | 1 | 5.2026 | 15.8574 | 3.048 | 0 | 0 |  | 0 | 9.69 | 0 | [6 empty] | 0
Floor 2 Storage 2 | No | 1 | 11.1484 | 33.9802 | 3.048 | 0 | 0 |  | 0 | 9.69 | 0 | [6 empty] | 0
Floor 2 Storage 3 | No | 1 | 13.378 | 40.7763 | 3.048 | 0 | 0 |  | 0 | 9.69 | 0 | [6 empty] | 0
Floor 2 Utility | No | 1 | 11.7058 | 35.6793 | 3.048 | 8.36 | 2.23 |  | 0 | 9.69 | 1.08 | [6 empty] | 0.25502
Floor 2 Work | Yes | 1 | 157.0061 | 478.5551 | 3.048 | 24.15 | 5.57 | 20 | 7.8503 | 11.84 | 11.84 |  |  | 10 |  | 78.5031 |  | 0.054924
Floor 2 Work Hall | Yes | 1 | 77.4811 | 236.1627 | 3.048 | 5.57 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 19.3703 |  | 0.02567
Floor 2 Work Toilet | No | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 |  | 0 | 9.69 | 4.31 |  |  |  | 10 | 50.1676 | 42.4752 | 0.39645
Floor 2 X-Ray | Yes | 1 | 83.6127 | 254.8518 | 3.048 | 0 | 0 | 5 | 16.7225 | 4.31 | 14.0206 |  | 3.7854 |  | 1.5 | 125.4191 |  | 0
Floor 3 Dressing Room | Yes | 1 | 3.9019 | 11.8931 | 3.048 | 0 | 0 | 20 | 0.1951 | 11.84 | 11.84 |  |  | 10 |  | 1.951 |  | 0.35708
Floor 3 Elevator Hall | Yes | 1 | 34.3741 | 104.7724 | 3.048 | 3.72 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 8.5935 |  | 0.39572
Floor 3 Humid | Yes | 1 | 10.0335 | 30.5822 | 3.048 | 0 | 0 | 20 | 0.50168 | 11.84 | 11.84 |  |  | 10 | 0 | 5.0168 |  | 0.35708
Floor 3 Janitor | No | 1 | 5.8529 | 17.8396 | 3.048 | 14.86 | 0 |  | 0 | 9.69 | 0 | [6 empty] | 1.2637
Floor 3 Locker | Yes | 1 | 11.1484 | 33.9802 | 3.048 | 0 | 0 | 6.6667 | 1.6723 | 8.61 | 32.29 |  |  | 8 |  | 13.378 |  | 0.35708
Floor 3 Lounge | Yes | 1 | 70.5134 | 214.925 | 3.048 | 21.37 | 5.57 | 6.6667 | 10.577 | 8.61 | 32.29 |  |  | 8 |  | 84.6161 |  | 0.46529
Floor 3 Lounge Toilet | No | 1 | 17.8374 | 54.3684 | 3.048 | 11.15 | 4.18 |  | 0 | 9.69 | 4.31 | [5 empty] | 151.023 | 0.58028
Floor 3 Mechanical | No | 1 | 32.5161 | 99.109 | 3.048 | 23.23 | 5.95 |  | 0 | 16.15 | 53.82 | [6 empty] | 0.61218
Floor 3 Mechanical Hall | Yes | 1 | 27.8709 | 84.9506 | 3.048 | 0 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 6.9677 |  | 0.35708
Floor 3 Office | Yes | 1 | 282.0536 | 859.7002 | 3.048 | 68.7501 | 19.51 | 20 | 14.1027 | 11.84 | 11.84 |  |  | 10 |  | 141.0268 |  | 0.44411
Floor 3 Office Hall | Yes | 1 | 77.4811 | 236.1627 | 3.048 | 5.57 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 19.3703 |  | 0.38274
Floor 3 Office Toilet | No | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 |  | 0 | 9.69 | 4.31 | [5 empty] | 42.4752 | 0.75353
Floor 3 Physical Therapy 1 | Yes | 1 | 120.774 | 368.1193 | 3.048 | 78.9701 | 28.99 | 5 | 24.1548 | 9.69 | 16.15 |  | 3.7854 | 8 |  | 193.2383 |  | 0.59055
Floor 3 Physical Therapy 2 | Yes | 1 | 54.9986 | 167.6359 | 3.048 | 0 | 0 | 5 | 10.9997 | 9.69 | 16.15 |  | 3.7854 | 8 |  | 87.9978 |  | 0.35708
Floor 3 Physical Therapy Toilet | No | 1 | 7.8039 | 23.7862 | 3.048 | 0 | 0 |  | 0 | 9.69 | 4.31 | [5 empty] | 66.0726 | 0.35708
Floor 3 Storage 1 | No | 1 | 10.0335 | 30.5822 | 3.048 | 0 | 0 |  | 0 | 9.69 | 0 | [6 empty] | 0.35708
Floor 3 Storage 2 | No | 1 | 7.8039 | 23.7862 | 3.048 | 0 | 0 |  | 0 | 9.69 | 0 | [6 empty] | 0.35708
Floor 3 Treatment | Yes | 1 | 44.2218 | 134.7883 | 3.048 | 0 | 0 | 5 | 8.8444 | 16.15 | 11.84 |  |  |  | 1.5 | 66.3328 |  | 0.35708
Floor 3 Undeveloped 1 | No | 1 | 210.7041 | 642.2266 | 3.048 | 66.8901 | 25.64 |  | 0 | 0 | 0 | [6 empty] | 0.47043
Floor 3 Undeveloped 2 | No | 1 | 107.0243 | 326.2103 | 3.048 | 52.03 | 13.38 |  | 0 | 0 | 0 | [6 empty] | 0.53067
Floor 3 Utility | No | 1 | 20.0671 | 61.1644 | 3.048 | 0 | 0 |  | 0 | 9.69 | 1.08 | [6 empty] | 0.35708
Floor 3 Work | Yes | 1 | 53.3263 | 162.5388 | 3.048 | 38.09 | 8.92 | 20 | 2.6663 | 11.84 | 11.84 |  |  | 10 |  | 26.6632 |  | 0.61213
NE Stair | No | 1 | 15.6077 | 142.717 | 9.144 | 97.5501 | 12.02 |  | 0 | 10.76 | 0 | [6 empty] | 1
NW Elevator | No | 1 | 13.0064 | 118.9309 | 9.144 | 75.2501 | 0 |  | 0 | 10.76 | 0 | [6 empty] | 1
NW Stair | No | 1 | 17.8374 | 163.1052 | 9.144 | 111.4801 | 11.15 |  | 0 | 10.76 | 0 | [6 empty] | 1
SW Stair | No | 1 | 8.9187 | 81.5526 | 9.144 | 55.7401 | 1.11 |  | 0 | 10.76 | 0 | [6 empty] | 1
Total Conditioned Zones |  |  | 3088.5616 | 11932.163 |  | 1634.1215 | 308.28 |  | 398.9164
Data Source | [7 empty] | 1 |  | 2 | 5 | 5 | 5 | 3, 4 | 3, 4 | 3, 4 | 5 | 6
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] AIA Guidelines for Design and Construction of Hospital and Health Care Facilities: 2001 Edition. Washington, D.C.: American Institute of Architects.
[4] Green Guide for Health Care: Best Practices for Creating High Performance Healing Environments, Version 2.2. www.gghc.org.
[5] Doebber, I.; Bonnema, E.; Pless, S.; Torcellini, P. (2009). Technical Support Document: Development of the Advanced Energy Design Guide for Small Hospitals and Health
[6] DOE Commercial Reference Buildings Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 12.0363 | 183.3674 | 43.3615 | 187.8142 |  | 88.8067 | 19.7797 | 264.2744 | 7.5099 | 58.4502 | 342.01 | 70.3698 | 110.6579 | 10.7551 | 12.5902 | 0.66527
Fabric | [6 empty] | weighting factor is for all of 3B
Exterior walls
| Construction Type | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame
| R-value (m2·K / W) | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 2.0964 | 2.0964 | 2.0964 | 2.0964 | 2.7548 | 2.7548
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.849 | 2.849 | 2.849 | 2.849 | 2.7933 | 3.7175
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
| SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.296
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.162 | 0.162 | 0.162 | 0.223 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.212
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet
| R-value (m2·K / W) | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463
HVAC
HVAC Sizing
Air Conditioning (kW)
| AHU-1_COOLC DXCOIL | 239.0574 | 237.8764 | 229.0538 | 225.7241 | 185.7094 | 201.2808 | 171.2715 | 225.3641 | 196.7908 | 175.2028 | 222.4906 | 192.5701 | 218.001 | 184.9672 | 192.6326 | 156.1667
| AHU-2_COOLC DXCOIL | 259.5151 | 266.679 | 273.4642 | 251.0924 | 196.3489 | 242.4959 | 191.7279 | 255.1759 | 211.8523 | 199.2625 | 250.4079 | 203.8138 | 243.1055 | 197.8202 | 219.0875 | 163.5167
Heating (kW)
| HEATSYS1 BOILER | 124.739 | 125.1364 | 115.3736 | 124.9673 | 115.0652 | 113.5958 | 117.9526 | 130.357 | 114.6396 | 122.5312 | 139.2338 | 122.7386 | 143.0675 | 133.9838 | 143.2942 | 159.0514
HVAC Efficiency
Air Conditioning (COP)
| AHU-1_COOLC DXCOIL | 3.13 | 3.13 | 3.13 | 3.13 | 3.23 | 3.23 | 3.23 | 3.13 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
| AHU-2_COOLC DXCOIL | 3.13 | 3.13 | 3.13 | 3.13 | 3.23 | 3.13 | 3.23 | 3.13 | 3.23 | 3.23 | 3.13 | 3.23 | 3.13 | 3.23 | 3.23 | 3.23
Heating Efficiency (%)
| HEATSYS1 BOILER | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
HVAC Control - Economizer
| AHU-1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| AHU-2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| AHU-1_FAN | 10.67 | 10.73 | 10.83 | 10.74 | 10.24 | 10.67 | 10.35 | 10.57 | 11.89 | 10.37 | 10.47 | 11.63 | 10.54 | 11.17 | 10.42 | 9.43
| AHU-2_FAN | 11.23 | 11.52 | 12.65 | 11.51 | 10.38 | 12.31 | 11.26 | 11.48 | 12.8 | 11.25 | 11.3 | 12.31 | 11.29 | 11.95 | 11.25 | 9.88
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.080422 | 0.10724 | 0.080411 | 0.099098 | 0.12353 | 0.095539 | 0.14454 | 0.069274 | 0.03706 | 0.071891 | 0.096404 | 0.037065 | 0.054617 | 0.071735 | 0.054479 | 0.091464
| Total Cost ($/m2) | 32.82 | 42.03 | 32.37 | 36.88 | 41.72 | 37.65 | 46.42 | 25.67 | 14.16 | 23.46 | 34.35 | 13.69 | 19.71 | 25.78 | 19.21 | 32.33
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011419 | 0.0081636 | 0.0085953 | 0.010826 | 0.0083853 | 0.0081505 | 0.0083855 | 0.010109 | 0.0072254 | 0.0082707 | 0.0089806 | 0.0072323 | 0.0079817 | 0.008852 | 0.0079898 | 0.0041911
| Total Cost ($/m2) | 7.03 | 5.78 | 6.24 | 8.46 | 6.51 | 5.68 | 7.13 | 8.4 | 5.42 | 7.11 | 7.73 | 5.59 | 7.3 | 7.49 | 7.51 | 4.56
Total Utility Costs
| Cost Intensity ($/m2) | 39.85 | 47.81 | 38.61 | 45.34 | 48.23 | 43.33 | 53.55 | 34.07 | 19.59 | 30.57 | 42.09 | 19.28 | 27.01 | 33.28 | 26.71 | 36.89
Energy - End Uses
Electricity (kWh)
| Heating | 2750 | 20816.6667 | 17477.7778 | 29069.4444 | 8694.4444 | 18180.5556 | 30847.2222 | 51352.7778 | 32391.6667 | 53158.3333 | 58491.6667 | 39622.2222 | 74955.5556 | 62761.1111 | 84986.1111 | 114708.3333
| Cooling | 591175 | 497258.3333 | 487636.1111 | 383083.3333 | 317280.5556 | 385605.5556 | 237102.7778 | 328241.6667 | 284688.8889 | 211827.7778 | 255002.7778 | 231925 | 228186.1111 | 187141.6667 | 158988.8889 | 105688.8889
| Interior Lighting | 156236.1111 | 156236.1111 | 156236.1111 | 156236.1111 | 156236.1111 | 156236.1111 | 156236.1111 | 156236.1111 | 156236.1111 | 156236.1111 | 156236.1111 | 156236.1111 | 156236.1111 | 156236.1111 | 156236.1111 | 156236.1111
| Exterior Lighting | 61608.3333 | 61586.1111 | 61575 | 61563.8889 | 61516.6667 | 61502.7778 | 61536.1111 | 61500 | 61522.2222 | 61400 | 61508.3333 | 61472.2222 | 61469.4444 | 61455.5556 | 61419.4444 | 61044.4444
| Interior Equipment | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 234483.3333 | 233108.3333 | 239219.4444 | 231930.5556 | 219658.3333 | 234708.3333 | 221594.4444 | 227780.5556 | 259883.3333 | 222430.5556 | 225180.5556 | 251833.3333 | 227100 | 240466.6667 | 224694.4444 | 212491.6667
| Pumps | 5430.5556 | 5436.1111 | 5013.8889 | 5430.5556 | 4977.7778 | 4922.2222 | 5113.8889 | 5644.4444 | 4997.2222 | 5319.4444 | 6027.7778 | 5333.3333 | 6200 | 5805.5556 | 6213.8889 | 6822.2222
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 997.2222 | 16533.3333 | 64552.7778 | 48738.8889 | 16658.3333 | 138005.5556 | 9636.1111 | 79036.1111 | 154227.7778 | 31144.4444 | 93377.7778 | 159169.4444 | 119044.4444 | 153633.3333 | 148680.5556 | 187783.3333
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1552455.5556 | 1490752.7778 | 1531488.8889 | 1415827.7778 | 1284802.7778 | 1498941.6667 | 1221841.6667 | 1409569.4444 | 1453725 | 1241294.4444 | 1355600 | 1405369.4444 | 1372966.6667 | 1367275 | 1340997.2222 | 1344547.2222
Gas (MJ)
| Heating | 2125390 | 2470790 | 2541070 | 2745050 | 2724900 | 2428430 | 3003760 | 2928530 | 2624750 | 3037450 | 3040290 | 2703810 | 3240530 | 2981850 | 3331820 | 3892890
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 28110 | 33520 | 30380 | 38750 | 37740 | 34120 | 42220 | 42850 | 42060 | 44990 | 46480 | 46290 | 49570 | 50170 | 54750 | 60970
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 2341870 | 2692690 | 2759820 | 2972180 | 2951020 | 2650930 | 3234350 | 3159760 | 2855180 | 3270820 | 3275140 | 2938470 | 3478480 | 3220390 | 3574940 | 4142240
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 7930720 | 8059400 | 8273180 | 8069160 | 7576310 | 8047120 | 7632980 | 8234210 | 8088590 | 7739470 | 8155300 | 7997800 | 8421160 | 8142590 | 8402530 | 8982610
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 2.6025 | 19.7003 | 16.5404 | 27.5104 | 8.2282 | 17.2055 | 29.1929 | 48.5987 | 30.6545 | 50.3074 | 55.3547 | 37.4973 | 70.9357 | 59.3952 | 80.4283 | 108.5565
| Cooling (elec) | 559.4701 | 470.5902 | 461.4841 | 362.5385 | 300.2647 | 364.9254 | 224.3869 | 310.638 | 269.421 | 200.4674 | 241.3269 | 219.4868 | 215.9484 | 177.1052 | 150.4623 | 100.0208
| Interior Lighting (elec) | 147.8571 | 147.8571 | 147.8571 | 147.8571 | 147.8571 | 147.8571 | 147.8571 | 147.8571 | 147.8571 | 147.8571 | 147.8571 | 147.8571 | 147.8571 | 147.8571 | 147.8571 | 147.8571
| Exterior Lighting (elec) | 58.3043 | 58.2832 | 58.2727 | 58.2622 | 58.2175 | 58.2044 | 58.2359 | 58.2017 | 58.2228 | 58.1071 | 58.2096 | 58.1755 | 58.1728 | 58.1597 | 58.1255 | 57.7706
| Interior Equipment (elec) | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 221.9079 | 220.6067 | 226.39 | 219.4921 | 207.878 | 222.1209 | 209.7103 | 215.5646 | 245.9457 | 210.5015 | 213.1041 | 238.3274 | 214.9206 | 227.5704 | 212.644 | 201.0957
| Pumps (elec) | 5.1393 | 5.1446 | 4.745 | 5.1393 | 4.7108 | 4.6582 | 4.8396 | 5.3417 | 4.7292 | 5.0342 | 5.7045 | 5.0473 | 5.8675 | 5.4942 | 5.8806 | 6.4563
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0.94374 | 15.6466 | 61.0908 | 46.125 | 15.7649 | 130.6043 | 9.1193 | 74.7974 | 145.9565 | 29.4742 | 88.3699 | 150.6331 | 112.6601 | 145.3939 | 140.7068 | 177.7125
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1469.197 | 1410.8033 | 1449.3548 | 1339.8966 | 1215.8985 | 1418.5531 | 1156.314 | 1333.9739 | 1375.7614 | 1174.7235 | 1282.8988 | 1329.9991 | 1299.3341 | 1293.9477 | 1269.0792 | 1272.4388
Gas (MJ/m2)
| Heating (gas) | 558.7236 | 649.5225 | 667.9977 | 721.6201 | 716.323 | 638.3869 | 789.6299 | 769.8534 | 689.9956 | 798.4863 | 799.2329 | 710.7789 | 851.8721 | 783.8702 | 875.8705 | 1023.3648
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 7.3896 | 8.8118 | 7.9863 | 10.1866 | 9.9211 | 8.9695 | 11.0988 | 11.2644 | 11.0568 | 11.827 | 12.2187 | 12.1687 | 13.031 | 13.1887 | 14.3927 | 16.0278
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 615.6319 | 707.8557 | 725.5028 | 781.3281 | 775.7656 | 696.8778 | 850.2475 | 830.6392 | 750.5711 | 859.8348 | 860.9704 | 772.4664 | 914.4245 | 846.5777 | 939.782 | 1088.9141
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 2084.8315 | 2118.659 | 2174.8576 | 2121.2247 | 1991.6641 | 2115.4308 | 2006.5615 | 2164.6131 | 2126.3325 | 2034.5556 | 2143.8692 | 2102.4656 | 2213.7586 | 2140.528 | 2208.8612 | 2361.3529
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 294.8016 | 288.0118 | 288.056 | 259.886 | 281.4216 | 275.5915 | 243.9994 | 285.2281 | 274.8997 | 262.4887 | 301.3492 | 300.1374 | 314.1468 | 315.3248 | 316.3809 | 327.9224
| Feb | 290.7202 | 283.9051 | 304.5992 | 263.0122 | 261.6335 | 278.3968 | 252.9937 | 271.4311 | 290.4364 | 245.5415 | 255.2869 | 269.4811 | 279.7085 | 297.0573 | 285.9622 | 296.3518
| Mar | 293.4515 | 279.9775 | 332.2087 | 286.4516 | 276.9686 | 282.5753 | 236.4988 | 267.7569 | 300.2128 | 243.5012 | 250.9568 | 304.8547 | 271.333 | 272.0402 | 263.1316 | 280.8168
| Apr | 296.5601 | 291.8536 | 326.9202 | 281.96 | 303.9742 | 294.8418 | 254.6125 | 266.4255 | 328.2974 | 240.904 | 251.143 | 286.0058 | 247.6293 | 272.6199 | 254.8951 | 263.5116
| May | 314.5112 | 316.5285 | 348.7084 | 293.3193 | 254.2648 | 345.4813 | 253.1791 | 283.6139 | 323.0693 | 253.0169 | 281.3501 | 305.4193 | 278.327 | 281.5462 | 262.8526 | 261.8923
| Jun | 320.8099 | 319.3198 | 407.2703 | 303.7386 | 257.8802 | 380.4211 | 255.1489 | 317.6667 | 351.332 | 259.4225 | 306.5147 | 321.4585 | 302.1084 | 303.0565 | 274.39 | 265.9312
| Jul | 313.1878 | 321.3973 | 367.9783 | 320.5334 | 260.5833 | 361.9185 | 264.2958 | 321.3891 | 350.2005 | 269.3337 | 309.6912 | 317.786 | 298.5684 | 305.72 | 285.6337 | 258.3671
| Aug | 317.1632 | 326.1526 | 366.2862 | 308.6044 | 268.6801 | 335.6285 | 260.9262 | 321.413 | 305.0935 | 263.4466 | 303.1005 | 316.8882 | 299.7768 | 292.2502 | 280.348 | 251.5745
| Sep | 312.3842 | 317.288 | 338.0401 | 293.8026 | 269.803 | 337.1521 | 285.5128 | 300.8343 | 314.4393 | 267.4552 | 287.1345 | 323.787 | 282.81 | 279.7194 | 266.4356 | 233.2577
| Oct | 307.699 | 303.422 | 321.363 | 291.7689 | 284.6167 | 309.6748 | 258.7236 | 282.5487 | 305.8471 | 243.6981 | 272.4515 | 310.7467 | 250.5599 | 271.0477 | 252.1889 | 273.9821
| Nov | 298.9814 | 292.6658 | 306.2614 | 261.5966 | 262.7198 | 275.8777 | 246.627 | 270.0528 | 279.9011 | 258.5396 | 272.21 | 289.1677 | 271.8293 | 260.9622 | 275.3091 | 283.548
| Dec | 294.4665 | 284.382 | 297.8748 | 273.5122 | 278.3042 | 281.7916 | 250.5587 | 267.1821 | 272.0852 | 261.7326 | 272.1729 | 286.9749 | 277.6402 | 306.2698 | 278.9566 | 293.8406
Time of Peak Electrical Demand
| Jan | 06-JAN-17:49 | 03-JAN-13:00 | 26-JAN-15:00 | 30-JAN-07:10 | 26-JAN-13:09 | 30-JAN-16:00 | 17-JAN-07:10 | 17-JAN-07:10 | 23-JAN-07:10 | 03-JAN-17:00 | 09-JAN-07:10 | 09-JAN-07:10 | 09-JAN-07:10 | 09-JAN-08:09 | 09-JAN-07:10 | 17-JAN-09:09
| Feb | 23-FEB-11:00 | 23-FEB-14:39 | 28-FEB-17:19 | 14-FEB-07:10 | 10-FEB-10:00 | 08-FEB-17:19 | 15-FEB-17:49 | 06-FEB-07:10 | 14-FEB-14:00 | 21-FEB-17:40 | 06-FEB-09:09 | 08-FEB-17:30 | 06-FEB-07:10 | 27-FEB-07:10 | 02-FEB-07:10 | 03-FEB-09:09
| Mar | 13-MAR-15:50 | 24-MAR-13:00 | 30-MAR-15:00 | 22-MAR-16:00 | 30-MAR-12:09 | 21-MAR-15:00 | 13-MAR-12:00 | 09-MAR-15:00 | 02-MAR-14:00 | 20-MAR-06:10 | 20-MAR-08:09 | 30-MAR-13:00 | 13-MAR-06:10 | 30-MAR-16:19 | 27-MAR-08:09 | 13-MAR-07:10
| Apr | 03-APR-14:09 | 21-APR-14:00 | 26-APR-16:19 | 14-APR-16:10 | 11-APR-16:00 | 21-APR-16:19 | 13-APR-15:20 | 04-APR-15:00 | 21-APR-16:00 | 14-APR-16:00 | 28-APR-16:00 | 26-APR-16:19 | 14-APR-15:00 | 06-APR-16:19 | 03-APR-08:09 | 03-APR-06:10
| May | 24-MAY-14:00 | 26-MAY-14:00 | 19-MAY-16:19 | 31-MAY-16:00 | 30-MAY-08:00 | 11-MAY-15:00 | 17-MAY-13:00 | 31-MAY-15:00 | 12-MAY-16:19 | 05-MAY-15:00 | 04-MAY-16:00 | 18-MAY-12:00 | 31-MAY-12:09 | 04-MAY-16:00 | 31-MAY-16:00 | 24-MAY-14:00
| Jun | 28-JUN-14:00 | 13-JUN-14:00 | 08-JUN-15:00 | 19-JUN-14:00 | 28-JUN-12:00 | 27-JUN-15:00 | 15-JUN-12:00 | 30-JUN-16:00 | 26-JUN-16:00 | 27-JUN-16:00 | 08-JUN-12:00 | 28-JUN-12:09 | 29-JUN-14:00 | 30-JUN-15:00 | 14-JUN-15:09 | 15-JUN-16:19
| Jul | 13-JUL-14:00 | 05-JUL-15:00 | 19-JUL-16:00 | 03-JUL-15:00 | 10-JUL-15:00 | 24-JUL-16:19 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-16:19 | 24-JUL-14:00 | 13-JUL-14:00 | 17-JUL-15:00 | 13-JUL-16:40 | 21-JUL-16:00 | 06-JUL-16:00 | 21-JUL-16:00
| Aug | 21-AUG-14:00 | 31-AUG-13:00 | 01-AUG-16:00 | 17-AUG-14:00 | 08-AUG-12:00 | 18-AUG-14:00 | 15-AUG-12:09 | 17-AUG-15:09 | 01-AUG-15:09 | 18-AUG-16:49 | 04-AUG-15:00 | 29-AUG-15:00 | 25-AUG-16:00 | 18-AUG-16:00 | 11-AUG-14:00 | 15-AUG-16:00
| Sep | 07-SEP-13:00 | 15-SEP-14:00 | 08-SEP-15:00 | 11-SEP-13:00 | 25-SEP-12:00 | 20-SEP-14:00 | 28-SEP-14:00 | 08-SEP-14:00 | 20-SEP-16:00 | 01-SEP-15:00 | 27-SEP-15:00 | 06-SEP-13:09 | 14-SEP-14:00 | 01-SEP-16:00 | 07-SEP-14:00 | 25-SEP-06:10
| Oct | 06-OCT-14:30 | 06-OCT-15:00 | 02-OCT-16:00 | 12-OCT-15:00 | 30-OCT-12:00 | 03-OCT-15:00 | 30-OCT-13:30 | 20-OCT-15:09 | 13-OCT-14:00 | 17-OCT-12:00 | 31-OCT-16:49 | 05-OCT-15:20 | 06-OCT-14:00 | 19-OCT-16:00 | 30-OCT-06:10 | 30-OCT-08:09
| Nov | 07-NOV-17:40 | 27-NOV-17:19 | 13-NOV-13:00 | 16-NOV-17:40 | 08-NOV-11:00 | 10-NOV-16:00 | 16-NOV-16:00 | 03-NOV-13:00 | 08-NOV-17:19 | 20-NOV-07:10 | 02-NOV-16:49 | 10-NOV-13:00 | 27-NOV-07:10 | 27-NOV-07:10 | 24-NOV-07:10 | 06-NOV-08:09
| Dec | 15-DEC-17:30 | 19-DEC-17:30 | 06-DEC-17:19 | 18-DEC-07:10 | 18-DEC-10:00 | 05-DEC-16:30 | 29-DEC-16:00 | 26-DEC-07:10 | 18-DEC-07:10 | 11-DEC-07:10 | 26-DEC-07:10 | 11-DEC-07:10 | 11-DEC-07:10 | 11-DEC-07:10 | 21-DEC-07:10 | 29-DEC-09:09
Source Energy
| Total Source Energy (GJ) | 21095.52 | 22432.3 | 20452.48 | 20391.87 | 17537.77 | 22196.98 | 17145.66 | 21596.69 | 20482.3 | 11356.13 | 20881.5 | 19995.66 | 20786.48 | 20626.22 | 20496.26 | 21813.14
| Total Source Energy (MJ/m2) | 5545.6 | 5897.02 | 5376.56 | 5360.63 | 4610.34 | 5835.15 | 4507.26 | 5677.35 | 5384.4 | 2985.31 | 5489.34 | 5256.47 | 5464.36 | 5422.23 | 5388.07 | 5734.25
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 1.33 | 22.14 | 86.45 | 65.27 | 22.31 | 184.82 | 12.91 | 105.85 | 206.54 | 41.71 | 125.05 | 213.16 | 159.43 | 205.75 | 199.11 | 251.48
| Water Systems | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48
| Total Building | 241.81 | 262.62 | 326.93 | 305.75 | 262.79 | 425.3 | 253.38 | 346.33 | 447.02 | 282.19 | 365.53 | 453.64 | 399.9 | 446.23 | 439.59 | 491.96
Emissions
| Carbon Equivalent (kg) | 467991.173 | 545813.231 | 512085.8148 | 489723.5028 | 203364.2802 | 553358.7084 | 201115.5855 | 437359.0577 | 645329.9334 | 149390.2295 | 781796.8792 | 627078.7363 | 532682.9101 | 557726.3962 | 523479.7563 | 453034.5754
| CO2 (kg) | 1107880 | 1388050 | 1231020 | 1144680 | 554621.6581 | 1335530 | 549738.8098 | 1017640 | 1532470 | 385173.2744 | 1838190 | 1490780 | 1264660 | 1329910 | 1244460 | 1163560
| NOX (kg) | 1849.4601 | 1767.4302 | 1968.1418 | 2051.9524 | 482.6407 | 2089.0612 | 479.2311 | 1854.9794 | 2562.8269 | 499.7793 | 3191.3499 | 2486.0108 | 2141.6025 | 2215.2164 | 2100.1305 | 1383.2714
| SO2 (kg) | 6645.7637 | 7111.6096 | 6159.1607 | 4970.354 | 3739.4097 | 8246.0825 | 3556.2763 | 5146.3396 | 6348.8858 | 960.297 | 9136.5376 | 6137.749 | 3241.3506 | 3651.655 | 3165.9256 | 6845.3972
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0305 | 0.0203 | 0.017 | 0.0185 | 0.002 | 0.0157 | 0.0019 | 0.0211 | 0.025 | 0.0041 | 0.0279 | 0.0242 | 0.024 | 0.0257 | 0.0235 | 0.0236
| Water for Electricity (m3) | 822.4264 | 2425.63 | 45491.9 | 8839.86 | 22558.2 | 41121.9 | 21452.8 | 320.0253 | 6601.07 | 12682 | 2103.13 | 6381.49 | 2130.07 | 86609 | 2080.48 | 1373.7

## Picture
DOE Commercial Building Benchmark - Outpatient Health Care

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.05 | 0.05 | 12.29 | 71.86 | 3666.11
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 6.41
|  |  | Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 4
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 16.4 | 102.6 | 5349.86
|  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 11.6
|  |  | Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 9
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | 13.5 | 74.75 | 3897.68
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 5.6
|  |  | Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.65
BLDG_OCC_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05 | 12.5 | 66.7 | 3477.93
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 3.75
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
INFIL_SCH | Fraction | Through 12/31 | SummerDesign, WinterDesign | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
|  |  | Other | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84 | 4380
RADIOLOGY_EQUIP_SCH | Fraction | Through 12/31 | WD, Sat, SummerDesign | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 11.64 | 70.08 | 3654.17
|  |  | Other | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.24
OR_CLGSETP_SCH | Temperature | Through 12/31 | All | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 489.9 | 3429.3 | 178813.5
OR_HTGSETP_SCH | Temperature | Through 12/31 | All | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 439.2 | 3074.4 | 160308
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 563.6 | 3995.6 | 208342
|  |  | Sat, WinterDesign | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 577.6
|  |  | Other | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600
HTGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 475.6 | 3278.8 | 170966
|  |  | Sat, WinterDesign | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 461.6
|  |  | Other | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 439.2
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinRelHumSetSch | Humidity | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
AHU-1_MinOAFracSchedule | Fraction | Through 12/31 | All | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 7.92 | 55.44 | 2890.8
AHU-1_Fan_Sch | Fraction | Through 12/31 | WD, Sat | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 17 | 102 | 5151
|  |  | SummerDesign, WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AHU-2_Fan_Sch | Fraction | Through 12/31 | WD, Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 72 | 3754.29
|  |  | SummerDesign, WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VAV_SAT_SCH | Temperature | Through 12/31 | All | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 307.2 | 2150.4 | 112128
CAV_SAT_SCH | Temperature | Through 12/31 | All | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 266.4 | 1864.8 | 97236
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HeatSys1 Loop Setpoint Sched | Temperature | Through 12/31 | All | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 1972.8 | 13809.6 | 720072
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0.01 | 0.01 | 7.83 | 41.88 | 2183.74
|  |  | Sat | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 2.49
|  |  | Other | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.24
Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600