## BuildingSummary
Building Summary Small Office new construction
|  | Value | Data Source
Program
| Building Name | Small Office Reference Building new construction 90.1-2004
| Available Fuel Types | gas, electricity
| Principal Building Activity | Office
Form
| Total Floor Area (m2) | 511 | 2003 CBECS, ASHRAE Small Office 30% Advanced Energy Design Guide
| Building Shape | Rectangle
| Aspect Ratio | 1.5
| Number of Floors | 1
Window Fraction (Window to Wall Ratio)
| South | 0.244
| East | 0.198
| North | 0.198
| West | 0.198
| Total | 0.212
Skylight/TDD Percentage
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | core zone with four perimeter zones
| Floor to Ceiling Height (m) | 3.05
| Roof type | Attic | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Mass wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 281.5
| Net Dimensions - Total Area (m2) | 222
| Wall to Skin Ratio | 0.32
Roof
| Construction Type | Attic | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 598.76
| Net Dimensions - Total Area (m2) | 598.76
| Roof to Skin Ratio | 0.68
Window Dimensions (m2)
| South | 16.73
| East | 11.16
| North | 16.73
| West | 11.16
| Total Area (m2) | 55.78
| Operable area (m2) | 0
Skylights/TDD
Dimensions - Total Area (m2)
Operable area (m2)
Foundation
| Foundation Type | Mass Floor
| Construction | 4in slab w/carpet
| Dimensions - Total Area (m2) | 511
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 0
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 1022.46
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.45 | See Reference Building Technical Report
HVAC
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | Unitary DX | 2003 CBECS
| Fan Control | Constant volume | 2003 CBECS
Service Water Heating
| SWH Type | gas water heater
| Fuel | gas
| Thermal Efficiency (%) | 80 | Standard 90.1-2004
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 17.63

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Core_ZN | Yes | 1 | 149.66 | 456.46 | 3.05 | 0 | 0 | 18.5806 | 8.0546 | 10.7639 | 10.7639 |  | 11.3562 | 10 |  | 80.5463 |  | 0
Perimeter_ZN_1 | Yes | 1 | 113.45 | 346.02 | 3.05 | 84.4501 | 20.64 | 18.5806 | 6.1058 | 10.7639 | 10.7639 |  |  | 10 |  | 61.0582 |  | 0.62247
Perimeter_ZN_2 | Yes | 1 | 67.3 | 205.26 | 3.0499 | 56.3001 | 11.16 | 18.5806 | 3.6221 | 10.7639 | 10.7639 |  |  | 10 |  | 36.2205 |  | 0.65537
Perimeter_ZN_3 | Yes | 1 | 113.45 | 346.02 | 3.05 | 84.4501 | 16.73 | 18.5806 | 6.1058 | 10.7639 | 10.7639 |  |  | 10 |  | 61.0582 |  | 0.62247
Perimeter_ZN_4 | Yes | 1 | 67.3 | 205.26 | 3.0499 | 56.3001 | 11.16 | 18.5806 | 3.6221 | 10.7639 | 10.7639 |  |  | 10 |  | 36.2205 |  | 0.65537
Attic | No | 1 | 567.98 | 720.19 | 1.268 | 0 | 0 | [8 empty] | 0 |  | 1
Total Conditioned Zones |  |  | 511.16 | 1559.02 |  | 281.5003 | 59.6901 |  | 27.5104
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Commercial Reference Buildings Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 201.9091 | 2559.5418 | 695.7164 | 2316.0945 |  | 1142.2145 | 186.9745 | 2251.0327 | 113.8618 | 294.7673 | 2213.0109 | 774.1455 | 580.2291 | 72.6764 | 77.7964 | 11.2727
Fabric | [6 empty] | weighting factor is for all of 3B
Exterior walls
| Construction Type | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall
| R-value (m2·K / W) | 0.4207 | 0.4207 | 0.4207 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.4327 | 1.4327 | 1.692 | 1.692 | 1.9569 | 2.2026
Roof
| Construction Type | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic
| R-value attic floor (m2·K / W) | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 6.5229 | 6.5229 | 6.5229 | 6.5229
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
| SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.296
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.162 | 0.162 | 0.162 | 0.223 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.212
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC:1_COOLC DXCOIL | 9.6595 | 8.7615 | 8.0624 | 8.8038 | 7.2501 | 6.8721 | 5.2359 | 8.311 | 7.5531 | 6.1595 | 8.0913 | 7.2523 | 7.9314 | 6.7071 | 6.2086 | 5.8184
| PSZ-AC:2_COOLC DXCOIL | 7.4175 | 6.5834 | 7.7527 | 6.7311 | 5.4317 | 5.639 | 8.0721 | 6.5094 | 5.2103 | 6.7194 | 6.3738 | 5.394 | 6.2216 | 5.899 | 6.3897 | 6.5265
| PSZ-AC:3_COOLC DXCOIL | 6.3974 | 6.2333 | 6.1228 | 5.3234 | 4.3144 | 4.7869 | 4.3764 | 5.7847 | 5.4489 | 4.5952 | 5.6451 | 5.2726 | 5.5406 | 5.0791 | 5.4412 | 4.093
| PSZ-AC:4_COOLC DXCOIL | 7.767 | 6.955 | 7.7585 | 6.9131 | 5.3116 | 5.79 | 3.3136 | 6.5833 | 5.4518 | 4.5292 | 6.3898 | 5.1686 | 6.2192 | 5.5841 | 5.2619 | 6.2268
| PSZ-AC:5_COOLC DXCOIL | 7.4152 | 7.4992 | 7.5134 | 5.8286 | 4.6665 | 5.2609 | 5.552 | 6.5666 | 6.3331 | 5.2694 | 6.4564 | 6.1137 | 6.166 | 5.7844 | 6.0431 | 4.093
Heating (kW)
| PSZ-AC:1_HEATC | 12.2619 | 13.044 | 11.3748 | 13.0981 | 11.2862 | 10.8629 | 9.0032 | 13.4036 | 11.0348 | 10.8842 | 13.9832 | 11.4401 | 14.1931 | 12.1611 | 12.8233 | 14.0426
| PSZ-AC:2_HEATC | 9.5949 | 9.9054 | 10.0731 | 10.153 | 8.5336 | 8.7858 | 12.5212 | 10.6372 | 7.7758 | 11.0579 | 11.1249 | 8.5536 | 11.2326 | 10.1995 | 11.2118 | 13.5366
| PSZ-AC:3_HEATC | 8.5187 | 8.8429 | 8.7328 | 7.7694 | 6.5993 | 7.0621 | 6.8557 | 8.9174 | 7.3071 | 7.3939 | 9.1634 | 7.4382 | 9.2493 | 7.9535 | 9.2626 | 8.3328
| PSZ-AC:4_HEATC | 10.1849 | 10.5472 | 10.5497 | 10.4639 | 8.3191 | 8.9795 | 5.8282 | 10.7644 | 8.0517 | 8.0587 | 11.1522 | 8.2964 | 11.2251 | 9.8202 | 10.4533 | 13.1269
| PSZ-AC:5_HEATC | 9.9364 | 10.5529 | 10.6253 | 8.3416 | 7.0864 | 7.6705 | 8.4878 | 9.7342 | 8.3173 | 8.3172 | 9.8854 | 8.3975 | 9.8513 | 8.8031 | 10.057 | 8.3328
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC:1_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
| PSZ-AC:2_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
| PSZ-AC:3_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
| PSZ-AC:4_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
| PSZ-AC:5_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
Heating Efficiency (%)
| PSZ-AC:1_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC:2_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC:3_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC:4_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC:5_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
HVAC Control - Economizer
| PSZ-AC:1_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC:2_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC:3_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC:4_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC:5_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
Fan Max Flow Rate (m3/s )
| PSZ-AC:1_FAN | 0.48 | 0.47 | 0.44 | 0.47 | 0.43 | 0.42 | 0.32 | 0.45 | 0.46 | 0.37 | 0.45 | 0.44 | 0.44 | 0.41 | 0.38 | 0.35
| PSZ-AC:2_FAN | 0.38 | 0.36 | 0.4 | 0.37 | 0.33 | 0.34 | 0.49 | 0.36 | 0.31 | 0.41 | 0.36 | 0.33 | 0.35 | 0.36 | 0.35 | 0.39
| PSZ-AC:3_FAN | 0.35 | 0.34 | 0.36 | 0.3 | 0.26 | 0.29 | 0.26 | 0.33 | 0.33 | 0.28 | 0.33 | 0.32 | 0.32 | 0.31 | 0.33 | 0.25
| PSZ-AC:4_FAN | 0.4 | 0.39 | 0.42 | 0.38 | 0.32 | 0.35 | 0.2 | 0.37 | 0.33 | 0.27 | 0.36 | 0.31 | 0.35 | 0.34 | 0.32 | 0.38
| PSZ-AC:5_FAN | 0.41 | 0.42 | 0.45 | 0.32 | 0.28 | 0.32 | 0.34 | 0.36 | 0.38 | 0.32 | 0.36 | 0.37 | 0.35 | 0.35 | 0.37 | 0.25
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.10232 | 0.119 | 0.12121 | 0.11748 | 0.12765 | 0.10058 | 0.15966 | 0.074943 | 0.075236 | 0.073211 | 0.064125 | 0.075276 | 0.074878 | 0.075544 | 0.074722 | 0.10025
| Total Cost ($/m2) | 16.32 | 17.44 | 18.93 | 15.41 | 15.7 | 13.52 | 18.88 | 9.68 | 9.6 | 8.65 | 8.13 | 9.29 | 9.42 | 9.19 | 9.09 | 12.02
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011467 | 0.0081068 | 0.0084069 | 0.0099266 | 0.0084397 | 0.0078851 | 0.0086046 | 0.0097332 | 0.0069517 | 0.008434 | 0.0083434 | 0.0069201 | 0.0079145 | 0.008049 | 0.0078859 | 0.004113
| Total Cost ($/m2) | 0.23 | 0.43 | 0.32 | 0.61 | 0.2 | 0.33 | 0.39 | 1.06 | 0.5 | 0.87 | 1.34 | 0.78 | 1.69 | 1.4 | 2.02 | 2.08
Total Utility Costs
| Cost Intensity ($/m2) | 16.55 | 17.87 | 19.25 | 16.02 | 15.9 | 13.84 | 19.27 | 10.74 | 10.09 | 9.52 | 9.46 | 10.07 | 11.1 | 10.59 | 11.11 | 14.1
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 19244.4444 | 13258.3333 | 16669.4444 | 6852.7778 | 3986.1111 | 8980.5556 | 1663.8889 | 5491.6667 | 5152.7778 | 1388.8889 | 4158.3333 | 3138.8889 | 3577.7778 | 2080.5556 | 1575 | 547.2222
| Interior Lighting | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222
| Exterior Lighting | 10066.6667 | 10063.8889 | 10061.1111 | 10058.3333 | 10052.7778 | 10050 | 10055.5556 | 10047.2222 | 10052.7778 | 10033.3333 | 10050 | 10044.4444 | 10044.4444 | 10041.6667 | 10036.1111 | 9975
| Interior Equipment | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 12083.3333 | 11472.2222 | 12997.2222 | 10011.1111 | 8716.6667 | 9547.2222 | 8622.2222 | 10358.3333 | 9894.4444 | 8888.8889 | 10463.8889 | 9761.1111 | 10541.6667 | 9963.8889 | 10438.8889 | 10661.1111
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 81508.3333 | 74908.3333 | 79841.6667 | 67036.1111 | 62869.4444 | 68691.6667 | 60455.5556 | 66013.8889 | 65213.8889 | 60425 | 64786.1111 | 63061.1111 | 64280.5556 | 62202.7778 | 62166.6667 | 61297.2222
Gas (MJ)
| Heating | 150 | 16750 | 8940 | 20650 | 1210 | 10620 | 11670 | 44500 | 25220 | 41040 | 70300 | 46040 | 97070 | 76960 | 118920 | 245480
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 10180 | 10580 | 10350 | 10970 | 10890 | 10630 | 11220 | 11270 | 11210 | 11420 | 11530 | 11520 | 11760 | 11800 | 12140 | 12590
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 10340 | 27330 | 19290 | 31610 | 12100 | 21240 | 22890 | 55770 | 36430 | 52470 | 81830 | 57560 | 108830 | 88760 | 131060 | 258070
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 303770 | 297000 | 306720 | 272940 | 238430 | 268530 | 240530 | 293420 | 271210 | 270000 | 315070 | 284570 | 340240 | 312690 | 354860 | 478750
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 135.5349 | 93.3759 | 117.3996 | 48.2628 | 28.0734 | 63.2483 | 11.7184 | 38.6767 | 36.29 | 9.7817 | 29.2863 | 22.1066 | 25.1976 | 14.6529 | 11.0924 | 3.854
| Interior Lighting (elec) | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046
| Exterior Lighting (elec) | 70.8976 | 70.878 | 70.8584 | 70.8389 | 70.7997 | 70.7802 | 70.8193 | 70.7606 | 70.7997 | 70.6628 | 70.7802 | 70.7411 | 70.7411 | 70.7215 | 70.6824 | 70.252
| Interior Equipment (elec) | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 85.1006 | 80.7966 | 91.5369 | 70.5063 | 61.3898 | 67.2392 | 60.7246 | 72.9517 | 69.6846 | 62.6027 | 73.6951 | 68.7456 | 74.2429 | 70.1737 | 73.5191 | 75.0841
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 574.0473 | 527.5648 | 562.3093 | 472.1222 | 442.7772 | 483.782 | 425.7767 | 464.9229 | 459.2887 | 425.5615 | 456.2759 | 444.1271 | 452.7154 | 438.082 | 437.8277 | 431.7044
Gas (MJ/m2)
| Heating (gas) | 0.29345 | 32.7686 | 17.4896 | 40.3983 | 2.3672 | 20.7763 | 22.8304 | 87.0569 | 49.3388 | 80.288 | 137.5303 | 90.0696 | 189.9014 | 150.5595 | 232.6473 | 480.241
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 19.9155 | 20.698 | 20.2481 | 21.461 | 21.3045 | 20.7958 | 21.9501 | 22.0479 | 21.9305 | 22.3413 | 22.5565 | 22.537 | 23.0065 | 23.0847 | 23.7499 | 24.6303
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 20.2285 | 53.4666 | 37.7377 | 61.8397 | 23.6716 | 41.5525 | 44.7805 | 109.1048 | 71.2693 | 102.6489 | 160.0869 | 112.6066 | 212.9079 | 173.6443 | 256.3972 | 504.8713
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 594.2758 | 581.0314 | 600.047 | 533.962 | 466.4489 | 525.3345 | 470.5572 | 574.0277 | 530.5775 | 528.2103 | 616.3823 | 556.7141 | 665.6233 | 611.7263 | 694.2249 | 936.5952
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 17.4675 | 15.6119 | 14.4383 | 12.9281 | 14.4721 | 14.4485 | 14.0591 | 14.3769 | 12.5973 | 14.1141 | 14.3576 | 14.2492 | 14.3121 | 14.2389 | 14.2205 | 14.078
| Feb | 17.9631 | 15.9495 | 15.2949 | 12.8853 | 13.8892 | 13.0099 | 13.7082 | 12.2218 | 13.283 | 12.0857 | 14.3576 | 12.3216 | 12.0167 | 12.2933 | 11.9634 | 14.078
| Mar | 18.3376 | 15.8942 | 17.6902 | 13.9691 | 13.7565 | 13.9086 | 12.7809 | 13.8427 | 13.4206 | 13.0001 | 13.0806 | 13.4128 | 12.4088 | 13.1829 | 12.0293 | 14.078
| Apr | 18.8747 | 17.305 | 17.9055 | 15.5994 | 14.5698 | 16.2301 | 13.8064 | 14.3945 | 14.8646 | 12.6295 | 13.3987 | 14.1643 | 13.2652 | 12.7746 | 12.4436 | 11.8457
| May | 19.7251 | 20.0651 | 20.8081 | 17.2441 | 14.6337 | 17.8225 | 13.9985 | 16.0811 | 16.3283 | 14.0774 | 15.8276 | 15.2713 | 15.8928 | 13.9668 | 14.1033 | 13.0005
| Jun | 20.9769 | 20.294 | 24.3027 | 18.4107 | 14.5615 | 20.6495 | 14.4378 | 19.2562 | 17.776 | 14.7443 | 18.2704 | 16.5176 | 18.0921 | 16.6642 | 15.9384 | 14.3041
| Jul | 20.4669 | 20.8989 | 23.9188 | 19.9352 | 15.3704 | 20.3336 | 15.5513 | 19.9544 | 18.4247 | 15.8437 | 18.9933 | 17.5718 | 18.2264 | 17.0713 | 17.1777 | 14.4725
| Aug | 20.7191 | 20.7884 | 23.9145 | 18.3682 | 16.0878 | 19.7378 | 14.7663 | 19.7093 | 18.2124 | 15.5498 | 18.7259 | 17.6932 | 18.0008 | 16.5206 | 16.4536 | 14.1958
| Sep | 20.0729 | 19.7515 | 21.876 | 17.682 | 16.176 | 19.2346 | 16.9611 | 17.4155 | 16.2796 | 15.2957 | 16.6874 | 15.7968 | 16.2798 | 15.1404 | 15.1449 | 11.9952
| Oct | 19.5894 | 18.6125 | 18.5749 | 16.2083 | 15.3307 | 16.5363 | 14.466 | 15.7302 | 14.9555 | 13.1977 | 14.7439 | 14.9807 | 13.6542 | 14.2389 | 12.8986 | 14.078
| Nov | 18.4045 | 16.5974 | 16.7981 | 13.9185 | 15.6108 | 15.4931 | 14.5547 | 15.0477 | 14.4752 | 14.1141 | 14.3576 | 14.3862 | 14.3121 | 14.2389 | 14.2205 | 14.078
| Dec | 17.39 | 15.6049 | 14.1604 | 12.6153 | 15.2141 | 14.812 | 14.1401 | 14.3769 | 14.4109 | 14.1141 | 14.3576 | 14.2853 | 14.3121 | 14.2389 | 14.2205 | 14.078
Time of Peak Electrical Demand
| Jan | 23-JAN-15:00 | 03-JAN-13:00 | 27-JAN-14:00 | 23-JAN-16:30 | 12-JAN-16:00 | 18-JAN-16:49 | 02-JAN-16:00 | 02-JAN-16:49 | 27-JAN-15:09 | 02-JAN-16:30 | 02-JAN-16:30 | 02-JAN-16:49 | 02-JAN-16:40 | 04-JAN-16:49 | 02-JAN-16:30 | 02-JAN-08:09
| Feb | 22-FEB-15:00 | 23-FEB-15:09 | 28-FEB-16:30 | 22-FEB-15:00 | 13-FEB-11:00 | 27-FEB-15:00 | 15-FEB-15:00 | 16-FEB-13:20 | 14-FEB-15:50 | 21-FEB-13:20 | 01-FEB-16:00 | 07-FEB-13:20 | 22-FEB-13:20 | 03-FEB-14:30 | 22-FEB-14:20 | 01-FEB-08:09
| Mar | 13-MAR-15:50 | 28-MAR-14:00 | 17-MAR-15:00 | 28-MAR-15:00 | 31-MAR-14:00 | 31-MAR-15:00 | 01-MAR-13:00 | 10-MAR-10:00 | 02-MAR-15:30 | 29-MAR-15:50 | 31-MAR-14:00 | 30-MAR-15:00 | 23-MAR-15:50 | 30-MAR-15:00 | 22-MAR-13:00 | 01-MAR-08:09
| Apr | 03-APR-14:39 | 21-APR-15:30 | 26-APR-15:00 | 14-APR-15:00 | 11-APR-15:00 | 21-APR-15:39 | 13-APR-14:00 | 04-APR-15:00 | 21-APR-15:00 | 19-APR-15:00 | 28-APR-15:00 | 26-APR-15:00 | 14-APR-15:00 | 06-APR-15:00 | 04-APR-15:30 | 25-APR-13:30
| May | 24-MAY-14:00 | 18-MAY-15:30 | 30-MAY-15:00 | 15-MAY-14:00 | 30-MAY-08:00 | 31-MAY-15:00 | 17-MAY-13:00 | 31-MAY-15:00 | 31-MAY-15:00 | 05-MAY-15:00 | 30-MAY-15:00 | 23-MAY-15:00 | 31-MAY-12:09 | 16-MAY-15:00 | 31-MAY-15:00 | 24-MAY-14:00
| Jun | 28-JUN-14:00 | 13-JUN-15:39 | 28-JUN-15:00 | 19-JUN-14:00 | 30-JUN-15:30 | 27-JUN-15:00 | 16-JUN-15:00 | 30-JUN-15:00 | 29-JUN-15:30 | 28-JUN-14:00 | 08-JUN-12:00 | 27-JUN-15:00 | 29-JUN-15:00 | 30-JUN-14:00 | 14-JUN-15:00 | 21-JUN-15:00
| Jul | 13-JUL-15:20 | 05-JUL-15:00 | 11-JUL-15:00 | 03-JUL-15:00 | 10-JUL-15:00 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-15:00 | 24-JUL-14:00 | 03-JUL-14:00 | 17-JUL-15:30 | 13-JUL-15:00 | 21-JUL-15:00 | 06-JUL-15:00 | 21-JUL-15:00
| Aug | 21-AUG-15:09 | 31-AUG-15:00 | 01-AUG-15:00 | 17-AUG-15:30 | 08-AUG-09:00 | 04-AUG-15:00 | 15-AUG-12:09 | 09-AUG-14:00 | 01-AUG-14:00 | 07-AUG-15:20 | 04-AUG-15:00 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-15:30 | 15-AUG-13:00
| Sep | 11-SEP-14:00 | 15-SEP-14:00 | 11-SEP-15:00 | 11-SEP-13:00 | 25-SEP-12:09 | 01-SEP-14:00 | 28-SEP-14:00 | 08-SEP-15:20 | 29-SEP-14:39 | 01-SEP-15:00 | 27-SEP-14:00 | 06-SEP-14:00 | 14-SEP-14:00 | 01-SEP-15:00 | 07-SEP-14:00 | 07-SEP-15:00
| Oct | 06-OCT-15:00 | 06-OCT-15:00 | 02-OCT-14:00 | 12-OCT-15:00 | 19-OCT-10:00 | 03-OCT-14:00 | 31-OCT-12:00 | 12-OCT-14:00 | 13-OCT-14:39 | 17-OCT-14:00 | 31-OCT-13:30 | 05-OCT-14:00 | 06-OCT-14:00 | 30-OCT-07:10 | 06-OCT-14:00 | 03-OCT-07:10
| Nov | 07-NOV-14:00 | 03-NOV-14:30 | 13-NOV-15:30 | 22-NOV-14:00 | 09-NOV-16:00 | 10-NOV-16:40 | 14-NOV-16:00 | 06-NOV-16:00 | 13-NOV-16:00 | 06-NOV-16:49 | 06-NOV-16:40 | 10-NOV-16:49 | 06-NOV-16:00 | 08-NOV-16:00 | 06-NOV-16:49 | 01-NOV-07:10
| Dec | 15-DEC-15:30 | 19-DEC-15:20 | 11-DEC-15:00 | 05-DEC-14:39 | 18-DEC-16:49 | 05-DEC-16:30 | 07-DEC-16:49 | 01-DEC-16:40 | 05-DEC-16:49 | 01-DEC-16:19 | 01-DEC-16:19 | 21-DEC-16:40 | 01-DEC-16:30 | 11-DEC-16:40 | 01-DEC-16:19 | 01-DEC-08:09
Source Energy
| Total Source Energy (GJ) | 984.6 | 1009.3 | 930.21 | 846.36 | 713.71 | 907.75 | 698.59 | 910.74 | 818.77 | 436.24 | 916.41 | 816.09 | 914.2 | 875.3 | 912.31 | 1070.06
| Total Source Energy (MJ/m2) | 1926.23 | 1974.53 | 1819.81 | 1655.78 | 1396.27 | 1775.87 | 1366.69 | 1781.72 | 1601.79 | 853.43 | 1792.82 | 1596.56 | 1788.5 | 1712.39 | 1784.79 | 2093.41
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63
| Total Building | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63
Emissions
| Carbon Equivalent (kg) | 22540.2466 | 25479.6312 | 24450.2121 | 21219.8225 | 7565.5739 | 23550.8827 | 7477.9383 | 18819.901 | 27297.2424 | 5347.2084 | 36016.9536 | 26797.7287 | 23965.3687 | 24331.565 | 23642.2135 | 21902.3134
| CO2 (kg) | 52300.1081 | 64122.9355 | 57686.5232 | 48513.7168 | 20246.6813 | 55980.0262 | 20055.3672 | 42854.6113 | 63972.5557 | 13188.2282 | 83959.6279 | 63021.6271 | 56395.3534 | 57493.7242 | 55884.3769 | 56653.5438
| NOX (kg) | 91.7758 | 83.7048 | 96.7132 | 91.9948 | 17.3594 | 90.9929 | 17.225 | 82.5121 | 110.6352 | 19.2797 | 148.9889 | 108.0348 | 97.7119 | 98.0463 | 95.7175 | 66.3381
| SO2 (kg) | 348.8935 | 357.3241 | 321.0653 | 235.3073 | 182.9468 | 377.8615 | 175.9256 | 240.992 | 284.791 | 46.7186 | 436.6359 | 275.3847 | 151.7417 | 166.1106 | 146.7554 | 312.1014
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0016 | 0.001 | 0.0009 | 0.0009 | 0.0001 | 0.0007 | 0.0001 | 0.001 | 0.0011 | 0.0002 | 0.0013 | 0.0011 | 0.0011 | 0.0012 | 0.0011 | 0.0011
| Water for Electricity (m3) | 43.18 | 121.886 | 2371.65 | 418.5502 | 1103.85 | 1884.47 | 1061.47 | 14.9876 | 296.1286 | 617.3613 | 100.5135 | 286.3415 | 99.7275 | 3940.13 | 96.4459 | 62.6271

## Picture
DOE Commercial Building Benchmark - Small Office

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
INFIL_QUARTER_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 12 | 99 | 5162.14
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 15
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
BLDG_OCC_SCH | Fraction | Through 12/31 | SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 16.1 | 47.4 | 2471.57
|  |  | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 9.1
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05 | 10.5 | 55.3 | 2883.5
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 2.8
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 14.1 | 78.95 | 4116.68
|  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 8.45
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 7.2
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 597.6 | 3596.4 | 187526.57
|  |  | Sat | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 608.4
|  |  | Other | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 640.8
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8 | 2743.2 | 143038.29
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 439.2
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
MinOA_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 15 | 86 | 4484.29
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 11
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 92 | 4797.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05 | 5.37 | 29.42 | 1534.04
|  |  | Sat, WinterDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05 | 2.57
|  |  | Other | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 1.13
Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600