## BuildingSummary
Building Summary Supermarket new construction
|  | Value | Data Source
Program
| Building Name | Super Market Reference Building new construction 90.1-2004
| Available Fuel Types | gas, electricity
| Principal Building Activity | Food Sales
Form
| Total Floor Area (m2) | 4181 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 1.5
| Number of Floors | 1
| Window Fraction (Window to Wall Ratio) | South: 0.362 East: 0.00 North: 0.00 West: 0.00 Total: 0.109
Skylight/TDD Percentage
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | Office, DryStorage, Deli, Sales, Produce, Bakery
| Floor to Ceiling Height (m) | 6.1
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Mass wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1609.58
| Net Dimensions - Total Area (m2) | 1434.88
| Wall to Skin Ratio | 0.28
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 4181
| Net Dimensions - Total Area (m2) | 4181
| Roof to Skin Ratio | 0.72
Window
| Dimensions - Total Area (m2) | South: 174.7 East: 0.00 North: 0.00 West: 0.00 Total: 174.7
| Operable area (m2) | 0
Skylights/TDD
Dimensions - Total Area (m2)
Operable area (m2)
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab-on-grade
| Dimensions - Total Area (m2) | 4181
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 46.47
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.25 | See Reference Building Technical Report
HVAC
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | Unitary DX | 2003 CBECS
| Fan Control | Constant volume | 2003 CBECS
Service Water Heating
| SWH Type | N/A
| Fuel | N/A
| Thermal Efficiency (%) | N/A
| Temperature Setpoint (ºC ) | N/A
| Water Consumption (m3 ) | N/A

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Office | Yes | 1 | 88.84 | 541.72 | 6.0977 | 115.0801 | 0 | 18.5806 | 4.7813 | 11.8403 | 8.0729 |  |  | 10 |  | 47.8132 |  | 0.40969
DryStorage | Yes | 1 | 621.89 | 3792.03 | 6.0976 | 477.2404 | 0 | 27.8709 | 22.3132 | 8.6111 | 8.0729 |  |  |  | 0.75 | 466.4175 |  | 0.31547
Deli | Yes | 1 | 224.72 | 1370.24 | 6.0975 | 138.4301 | 0 | 11.6129 | 19.3509 | 18.2986 | 53.8195 | 26.9097 | 18.927 |  | 1.5 | 337.08 | 1415.841 | 0.28845
Sales | Yes | 1 | 2324.94 | 14176.6 | 6.0976 | 323.5203 | 174.7002 | 11.6129 | 200.2034 | 18.2986 | 5.3819 |  |  |  | 1.5 | 3487.41 |  | 0.20333
Produce | Yes | 1 | 711.36 | 4337.61 | 6.0976 | 366.1803 | 0 | 11.6129 | 61.2561 | 18.2986 | 5.3819 |  |  |  | 1.5 | 1067.04 |  | 0.27037
Bakery | Yes | 1 | 209.04 | 1274.65 | 6.0976 | 189.1302 | 0 | 11.6129 | 18.0007 | 18.2986 | 53.8195 | 26.9097 | 18.927 |  | 1.5 | 313.56 | 353.9603 | 0.33998
Total Conditioned Zones |  |  | 4180.79 | 25492.85 |  | 1609.5815 | 174.7002 |  | 325.9056 | [6 empty] | 5719.3207 | 1769.8013
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Commercial Reference Buildings Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 3.2427 | 48.5293 | 13.8511 | 58.2142 |  | 36.0031 | 4.9396 | 93.7809 | 1.6382 | 10.8413 | 113.3876 | 15.6058 | 24.6924 | 2.8076 | 2.9867 | 0.54444
Fabric | [6 empty] | weighting factor is for all of 3B
Exterior walls
| Construction Type | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall
| R-value (m2·K / W) | 0.4207 | 0.4207 | 0.4207 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.4327 | 1.4327 | 1.692 | 1.692 | 1.9569 | 2.2026
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.849 | 2.849 | 2.849 | 2.849 | 2.7933 | 3.7175
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
| SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.296
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.162 | 0.162 | 0.162 | 0.223 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.212
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade
| R-value (m2·K / W) | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC:1_COOLC DXCOIL | 9.4188 | 10.1661 | 9.0212 | 9.9073 | 5.904 | 7.8239 | 5.7616 | 10.8719 | 9.0455 | 7.0491 | 12.8846 | 10.5165 | 13.8909 | 11.4451 | 13.6368 | 12.4037
| PSZ-AC:2_COOLC DXCOIL | 46.2229 | 59.4624 | 49.1553 | 60.1288 | 31.3453 | 51.7902 | 33.5101 | 65.0262 | 50.16 | 42.6913 | 76.0248 | 60.4541 | 82.8354 | 61.3035 | 86.8618 | 66.9876
| PSZ-AC:3_COOLC DXCOIL | 56.4759 | 55.4381 | 55.2275 | 56.6479 | 46.9854 | 42.4422 | 27.2528 | 53.9303 | 35.7606 | 30.4314 | 53.849 | 34.7572 | 53.8502 | 32.7017 | 32.0076 | 26.6125
| PSZ-AC:4_COOLC DXCOIL | 114.6373 | 187.2928 | 183.9187 | 202.078 | 137.2072 | 201.6655 | 132.6487 | 210.714 | 227.7159 | 172.7709 | 240.672 | 256.8657 | 258.3261 | 237.6864 | 274.0209 | 202.9031
| PSZ-AC:5_COOLC DXCOIL | 54.5528 | 65.0467 | 58.5394 | 64.9221 | 38.5895 | 59.5616 | 33.7974 | 69.0495 | 51.288 | 40.8584 | 79.4702 | 57.8963 | 85.5442 | 63.6627 | 87.3825 | 69.1593
| PSZ-AC:6_COOLC DXCOIL | 41.1882 | 37.6013 | 44.0536 | 38.7297 | 34.1553 | 34.8905 | 29.62 | 36.5946 | 36.4415 | 31.5104 | 35.9428 | 35.9644 | 35.7392 | 34.308 | 31.9965 | 30.1277
Heating (kW)
| PSZ-AC:1_HEATC | 11.4942 | 13.042 | 12.0433 | 11.662 | 7.4177 | 10.3255 | 8.9141 | 13.2389 | 11.8725 | 11.0255 | 15.5809 | 14.0051 | 16.7279 | 16.3604 | 17.0815 | 20.757
| PSZ-AC:2_HEATC | 50.3627 | 71.7059 | 61.9834 | 70.1146 | 42.7236 | 62.135 | 52.8358 | 78.4217 | 69.1778 | 66.7072 | 92.4758 | 82.205 | 100.9119 | 98.2297 | 103.9927 | 127.7689
| PSZ-AC:3_HEATC | 88.051 | 114.1035 | 95.9029 | 125.7743 | 84.6602 | 96.2122 | 73.2744 | 133.2925 | 105.3486 | 97.5759 | 155.4785 | 122.2274 | 168.0302 | 139.4864 | 148.4686 | 157.8973
| PSZ-AC:4_HEATC | 161.1949 | 272.2155 | 237.9483 | 296.4955 | 201.893 | 262.1494 | 231.1317 | 329.6852 | 289.8858 | 282.6402 | 391.1872 | 344.6745 | 426.3284 | 410.7784 | 443.4022 | 543.2742
| PSZ-AC:5_HEATC | 67.2919 | 90.5133 | 77.563 | 93.5097 | 58.3 | 81.6486 | 70.1522 | 105.1393 | 90.9016 | 88.7688 | 125.0352 | 108.5373 | 136.3579 | 131.3995 | 141.3731 | 176.0159
| PSZ-AC:6_HEATC | 55.4888 | 58.6626 | 58.6034 | 60.2988 | 53.0994 | 53.1718 | 48.2638 | 61.3908 | 51.4117 | 53.102 | 63.9354 | 53.7604 | 65.5061 | 57.6239 | 60.6598 | 65.2832
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC:1_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
| PSZ-AC:2_COOLC DXCOIL | 3.3 | 3.3 | 3.3 | 3.3 | 3.5 | 3.3 | 3.5 | 3.3 | 3.3 | 3.3 | 3.23 | 3.3 | 3.23 | 3.3 | 3.23 | 3.3
| PSZ-AC:3_COOLC DXCOIL | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.5 | 3.3 | 3.5 | 3.5 | 3.3 | 3.5 | 3.3 | 3.5 | 3.5 | 3.5
| PSZ-AC:4_COOLC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.13 | 3.23 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.23
| PSZ-AC:5_COOLC DXCOIL | 3.3 | 3.3 | 3.3 | 3.3 | 3.5 | 3.3 | 3.5 | 3.3 | 3.3 | 3.3 | 3.23 | 3.3 | 3.23 | 3.3 | 3.23 | 3.3
| PSZ-AC:6_COOLC DXCOIL | 3.3 | 3.5 | 3.3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Heating Efficiency (%)
| PSZ-AC:1_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC:2_HEATC | 0.8 | 0.78 | 0.8 | 0.78 | 0.8 | 0.8 | 0.8 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:3_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:4_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:5_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.8 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:6_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
HVAC Control - Economizer
| PSZ-AC:1_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC:2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC:3_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ-AC:4_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC:5_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC:6_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
Fan Max Flow Rate (m3/s )
| BAKERY EXHAUST FAN | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
| DELI EXHAUST FAN | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34
| SALES EXHAUST FAN | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08
| PSZ-AC:1_FAN | 0.46 | 0.51 | 0.49 | 0.45 | 0.29 | 0.42 | 0.34 | 0.49 | 0.55 | 0.42 | 0.58 | 0.64 | 0.62 | 0.69 | 0.65 | 0.75
| PSZ-AC:2_FAN | 1.86 | 2.53 | 2.34 | 2.45 | 1.5 | 2.35 | 1.85 | 2.62 | 2.89 | 2.3 | 3.06 | 3.35 | 3.34 | 3.7 | 3.5 | 4.05
| PSZ-AC:3_FAN | 2.27 | 2.23 | 2.22 | 2.28 | 2.1 | 2.06 | 1.65 | 2.17 | 2.16 | 1.84 | 2.17 | 2.1 | 2.17 | 1.98 | 1.87 | 1.61
| PSZ-AC:4_FAN | 4.62 | 7.54 | 7.41 | 8.14 | 6.14 | 8.12 | 6.75 | 8.49 | 9.75 | 7.74 | 9.69 | 10.9 | 10.4 | 11.64 | 11.03 | 12.26
| PSZ-AC:5_FAN | 2.2 | 2.62 | 2.48 | 2.61 | 1.73 | 2.55 | 2.04 | 2.78 | 3.1 | 2.47 | 3.2 | 3.5 | 3.44 | 3.85 | 3.63 | 4.18
| PSZ-AC:6_FAN | 2.18 | 2.15 | 2.33 | 2.23 | 2.06 | 2.11 | 1.79 | 2.14 | 2.2 | 1.9 | 2.14 | 2.17 | 2.14 | 2.07 | 1.93 | 1.82
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.079833 | 0.10697 | 0.078077 | 0.099017 | 0.12218 | 0.094848 | 0.14403 | 0.069184 | 0.037048 | 0.070791 | 0.096932 | 0.037049 | 0.055153 | 0.069884 | 0.05504 | 0.088521
| Total Cost ($/m2) | 38.11 | 48.87 | 33.61 | 41.55 | 49.38 | 37.78 | 55.02 | 27.9 | 14.24 | 26.64 | 38.19 | 14.04 | 21.64 | 26.8 | 20.98 | 33.78
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011442 | 0.0080767 | 0.0082764 | 0.0098027 | 0.0085191 | 0.0077768 | 0.0084739 | 0.0097389 | 0.0069619 | 0.0083606 | 0.0084422 | 0.0069947 | 0.0078567 | 0.0083107 | 0.0078775 | 0.0041507
| Total Cost ($/m2) | 0.87 | 2.18 | 2.28 | 4.4 | 2.68 | 3.12 | 4.65 | 6.44 | 3.92 | 6.1 | 6.94 | 4.96 | 7.69 | 7.44 | 9.35 | 7.09
Total Utility Costs
| Cost Intensity ($/m2) | 38.98 | 51.04 | 35.89 | 45.96 | 52.06 | 40.9 | 59.66 | 34.34 | 18.16 | 32.73 | 45.12 | 18.99 | 29.33 | 34.24 | 30.34 | 40.87
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 103819.4444 | 82238.8889 | 108275 | 39788.8889 | 8469.4444 | 62633.3333 | 2175 | 31097.2222 | 24027.7778 | 3352.7778 | 20238.8889 | 14627.7778 | 17516.6667 | 9525 | 7508.3333 | 3736.1111
| Interior Lighting | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778
| Exterior Lighting | 59366.6667 | 59261.1111 | 59244.4444 | 59341.6667 | 59330.5556 | 59275 | 59208.3333 | 59269.4444 | 59261.1111 | 59172.2222 | 59188.8889 | 59200 | 59236.1111 | 59163.8889 | 59147.2222 | 58794.4444
| Interior Equipment | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 108875 | 148108.3333 | 145416.6667 | 153761.1111 | 117208.3333 | 150561.1111 | 123841.6667 | 161219.4444 | 170986.1111 | 143333.3333 | 175077.7778 | 191388.8889 | 190263.8889 | 242880.5556 | 218427.7778 | 270913.8889
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 1246013.8889 | 1142794.4444 | 1009013.8889 | 1024025 | 1027019.4444 | 915047.2222 | 934111.1111 | 956980.5556 | 875488.8889 | 889663.8889 | 914869.4444 | 841063.8889 | 896055.5556 | 814258.3333 | 831116.6667 | 784505.5556
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1995700 | 1910025 | 1799572.2222 | 1754544.4444 | 1689650 | 1665138.8889 | 1596961.1111 | 1686191.6667 | 1607388.8889 | 1573147.2222 | 1646997.2222 | 1583902.7778 | 1640697.2222 | 1603452.7778 | 1593822.2222 | 1595575
Gas (MJ)
| Heating | 99670 | 906910 | 933250 | 1656720 | 1092660 | 1459050 | 2069910 | 2540180 | 2132070 | 2824690 | 3211490 | 2737570 | 3865780 | 3516400 | 4737400 | 6911110
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 18460 | 20420 | 19290 | 22320 | 21950 | 20660 | 23570 | 23810 | 23530 | 24580 | 25110 | 25050 | 26250 | 26450 | 28110 | 30360
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 317260 | 1126460 | 1151670 | 1878160 | 1313740 | 1678830 | 2292610 | 2763120 | 2354730 | 3048390 | 3435730 | 2961740 | 4091150 | 3741970 | 4964630 | 7140600
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 7501780 | 8002550 | 7630130 | 8194520 | 7396490 | 7673330 | 8041670 | 8833400 | 8141330 | 8711720 | 9364920 | 8663800 | 9997660 | 9514400 | 10702400 | 12884670
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 89.397 | 70.8144 | 93.2336 | 34.2615 | 7.2929 | 53.9324 | 1.8729 | 26.7772 | 20.6899 | 2.887 | 17.4273 | 12.5957 | 15.0833 | 8.2018 | 6.4653 | 3.2171
| Interior Lighting (elec) | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453
| Exterior Lighting (elec) | 51.1195 | 51.0286 | 51.0143 | 51.098 | 51.0884 | 51.0406 | 50.9832 | 51.0358 | 51.0286 | 50.9521 | 50.9664 | 50.976 | 51.0071 | 50.9449 | 50.9306 | 50.6268
| Interior Equipment (elec) | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 93.7502 | 127.5333 | 125.2156 | 132.4008 | 100.9259 | 129.6454 | 106.6377 | 138.823 | 147.2329 | 123.4216 | 150.7562 | 164.8014 | 163.8327 | 209.1399 | 188.0841 | 233.2789
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 1072.9192 | 984.0389 | 868.843 | 881.7688 | 884.3472 | 787.93 | 804.3456 | 824.038 | 753.8671 | 766.0729 | 787.777 | 724.2244 | 771.5767 | 701.1426 | 715.659 | 675.523
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1718.4599 | 1644.6868 | 1549.578 | 1510.8054 | 1454.926 | 1433.8199 | 1375.1133 | 1451.9481 | 1384.0925 | 1354.6076 | 1418.1985 | 1363.869 | 1412.7737 | 1380.7032 | 1372.4105 | 1373.9198
Gas (MJ/m2)
| Heating (gas) | 23.84 | 216.9231 | 223.2234 | 396.2696 | 261.3525 | 348.9891 | 495.1002 | 607.5837 | 509.9682 | 675.6355 | 768.1539 | 654.7973 | 924.653 | 841.0851 | 1133.1351 | 1653.0632
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 4.4154 | 4.8842 | 4.614 | 5.3387 | 5.2502 | 4.9416 | 5.6377 | 5.6951 | 5.6281 | 5.8793 | 6.006 | 5.9917 | 6.2787 | 6.3266 | 6.7236 | 7.2618
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 75.8852 | 269.4371 | 275.4671 | 449.2357 | 314.2325 | 401.5581 | 548.3677 | 660.9086 | 563.2261 | 729.1421 | 821.7897 | 708.4164 | 978.5591 | 895.039 | 1187.4861 | 1707.9547
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 1794.3451 | 1914.1239 | 1825.045 | 1960.041 | 1769.1609 | 1835.378 | 1923.481 | 2112.8543 | 1947.3186 | 2083.7497 | 2239.9881 | 2072.2878 | 2391.3327 | 2275.7421 | 2559.899 | 3081.8745
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 360.4727 | 357.8689 | 313.6288 | 339.8971 | 317.3563 | 306.9148 | 318.9003 | 310.2289 | 299.835 | 304.0091 | 305.0063 | 305.3251 | 301.3075 | 311.5744 | 302.3663 | 308.4167
| Feb | 364.9106 | 348.2719 | 320.5684 | 317.9152 | 317.1582 | 319.0713 | 324.3508 | 307.9435 | 304.3837 | 304.2596 | 304.1612 | 302.6516 | 300.8312 | 319.8785 | 305.085 | 307.512
| Mar | 362.7757 | 347.1386 | 339.5126 | 330.3696 | 322.1272 | 304.1124 | 307.3332 | 345.9412 | 309.108 | 305.7246 | 320.9797 | 307.0346 | 305.1012 | 310.7841 | 301.2702 | 307.5488
| Apr | 372.555 | 365.6017 | 345.5532 | 347.1042 | 315.2915 | 342.3349 | 312.0653 | 333.6566 | 317.4392 | 309.5854 | 323.0833 | 316.6076 | 325.7869 | 310.7655 | 307.5067 | 302.9315
| May | 383.0492 | 402.3899 | 385.5569 | 374.319 | 332.5993 | 357.8716 | 320.3007 | 357.346 | 336.2605 | 329.3624 | 358.0677 | 334.2809 | 368.3121 | 330.065 | 320.0649 | 322.6294
| Jun | 404.7535 | 406.1376 | 444.4933 | 388.6512 | 330.7647 | 400.6798 | 327.1405 | 405.8595 | 356.5273 | 329.3884 | 379.412 | 350.064 | 393.1845 | 361.7006 | 363.9236 | 345.9353
| Jul | 394.5089 | 416.1971 | 441.8643 | 408.2736 | 341.3787 | 399.5872 | 340.0158 | 411.9615 | 367.3504 | 345.0511 | 402.6983 | 362.4994 | 393.8981 | 372.061 | 384.2806 | 346.1522
| Aug | 396.2853 | 414.2159 | 441.7539 | 389.8402 | 348.0809 | 399.9498 | 335.9035 | 408.4042 | 374.5861 | 342.1477 | 398.0654 | 364.5192 | 393.3042 | 363.5773 | 368.0937 | 344.6866
| Sep | 383.519 | 400.2437 | 412.1701 | 370.2189 | 344.8762 | 378.7834 | 342.4032 | 364.3456 | 339.9232 | 345.2695 | 360.1223 | 342.0393 | 353.0258 | 349.0654 | 345.9043 | 317.4394
| Oct | 383.031 | 370.706 | 362.2551 | 346.8364 | 333.7377 | 347.7632 | 325.1509 | 346.8698 | 327.6686 | 324.7558 | 352.0559 | 317.6417 | 322.858 | 323.1378 | 323.6758 | 309.6392
| Nov | 368.8671 | 369.4641 | 334.7331 | 337.666 | 328.9547 | 315.3789 | 326.6372 | 347.6824 | 308.9423 | 327.2482 | 352.616 | 306.5842 | 318.6961 | 313.2145 | 321.6967 | 309.7935
| Dec | 363.4951 | 354.7079 | 329.59 | 336.785 | 324.4194 | 305.2231 | 318.608 | 310.8615 | 300.5106 | 306.8942 | 312.4621 | 300.9959 | 302.0787 | 310.1927 | 303.979 | 314.1535
Time of Peak Electrical Demand
| Jan | 06-JAN-18:15 | 20-JAN-18:15 | 05-JAN-18:15 | 24-JAN-18:15 | 10-JAN-18:15 | 23-JAN-18:15 | 05-JAN-18:15 | 09-JAN-11:15 | 05-JAN-18:15 | 14-JAN-11:15 | 17-JAN-18:15 | 27-JAN-18:15 | 30-JAN-18:15 | 23-JAN-18:15 | 13-JAN-18:15 | 20-JAN-18:15
| Feb | 23-FEB-18:15 | 15-FEB-18:15 | 14-FEB-18:15 | 21-FEB-18:15 | 13-FEB-18:15 | 10-FEB-18:15 | 15-FEB-18:15 | 03-FEB-18:15 | 14-FEB-18:15 | 24-FEB-18:15 | 21-FEB-18:15 | 24-FEB-18:15 | 27-FEB-18:15 | 02-FEB-18:15 | 21-FEB-18:15 | 27-FEB-18:15
| Mar | 13-MAR-17:15 | 28-MAR-17:15 | 17-MAR-17:15 | 29-MAR-17:15 | 06-MAR-18:15 | 31-MAR-17:15 | 09-MAR-18:15 | 09-MAR-18:15 | 08-MAR-18:15 | 08-MAR-18:15 | 14-MAR-17:15 | 30-MAR-17:15 | 23-MAR-17:15 | 30-MAR-17:15 | 10-MAR-18:15 | 06-MAR-18:15
| Apr | 03-APR-17:15 | 29-APR-10:00 | 26-APR-17:15 | 14-APR-17:15 | 10-APR-10:45 | 21-APR-17:15 | 29-APR-10:45 | 04-APR-17:15 | 21-APR-17:15 | 29-APR-10:15 | 10-APR-10:15 | 26-APR-10:45 | 01-APR-17:15 | 24-APR-10:15 | 14-APR-10:15 | 14-APR-10:15
| May | 15-MAY-17:15 | 26-MAY-17:15 | 30-MAY-17:15 | 31-MAY-17:15 | 30-MAY-10:45 | 31-MAY-17:15 | 24-MAY-17:15 | 15-MAY-17:15 | 31-MAY-17:15 | 05-MAY-17:15 | 30-MAY-17:15 | 24-MAY-10:45 | 27-MAY-17:15 | 25-MAY-17:15 | 27-MAY-10:45 | 31-MAY-10:15
| Jun | 27-JUN-17:15 | 13-JUN-17:15 | 28-JUN-17:15 | 19-JUN-17:15 | 28-JUN-17:15 | 27-JUN-17:15 | 16-JUN-10:45 | 30-JUN-17:15 | 29-JUN-17:15 | 28-JUN-10:45 | 08-JUN-10:00 | 28-JUN-10:45 | 29-JUN-17:15 | 30-JUN-17:15 | 14-JUN-17:15 | 21-JUN-17:15
| Jul | 13-JUL-17:15 | 05-JUL-17:15 | 19-JUL-17:15 | 03-JUL-17:15 | 29-JUL-10:45 | 25-JUL-17:15 | 03-JUL-10:45 | 25-JUL-10:00 | 18-JUL-17:15 | 31-JUL-17:15 | 14-JUL-10:00 | 19-JUL-10:45 | 13-JUL-17:15 | 21-JUL-17:15 | 06-JUL-17:15 | 11-JUL-17:15
| Aug | 21-AUG-17:15 | 31-AUG-17:15 | 01-AUG-17:15 | 14-AUG-17:15 | 08-AUG-17:15 | 02-AUG-17:15 | 15-AUG-10:45 | 17-AUG-17:15 | 01-AUG-17:15 | 18-AUG-17:15 | 04-AUG-17:15 | 30-AUG-10:45 | 25-AUG-17:15 | 11-AUG-17:15 | 11-AUG-17:15 | 15-AUG-17:15
| Sep | 13-SEP-17:15 | 16-SEP-10:00 | 08-SEP-17:15 | 06-SEP-17:15 | 09-SEP-10:45 | 01-SEP-17:15 | 29-SEP-10:45 | 08-SEP-17:15 | 01-SEP-17:15 | 02-SEP-10:45 | 06-SEP-10:45 | 09-SEP-10:45 | 14-SEP-17:15 | 01-SEP-17:15 | 08-SEP-17:15 | 01-SEP-17:15
| Oct | 06-OCT-17:15 | 06-OCT-17:15 | 13-OCT-17:15 | 20-OCT-17:15 | 19-OCT-17:15 | 06-OCT-17:15 | 27-OCT-17:15 | 20-OCT-17:15 | 11-OCT-17:15 | 18-OCT-17:15 | 31-OCT-17:15 | 05-OCT-10:45 | 27-OCT-17:15 | 06-OCT-17:15 | 27-OCT-17:15 | 02-OCT-10:15
| Nov | 07-NOV-18:15 | 27-NOV-18:15 | 13-NOV-18:15 | 28-NOV-18:15 | 03-NOV-17:15 | 21-NOV-18:15 | 16-NOV-18:15 | 03-NOV-17:15 | 09-NOV-18:15 | 03-NOV-17:15 | 02-NOV-17:15 | 16-NOV-18:15 | 02-NOV-17:15 | 07-NOV-18:15 | 08-NOV-18:15 | 14-NOV-18:15
| Dec | 15-DEC-18:15 | 19-DEC-18:15 | 13-DEC-18:15 | 04-DEC-18:15 | 04-DEC-18:15 | 05-DEC-18:15 | 14-DEC-18:15 | 23-DEC-11:15 | 21-DEC-18:15 | 28-DEC-18:15 | 12-DEC-18:15 | 21-DEC-18:15 | 08-DEC-18:15 | 29-DEC-18:15 | 26-DEC-18:15 | 18-DEC-11:15
Source Energy
| Total Source Energy (GJ) | 24177.49 | 26204.05 | 21748.98 | 23299.18 | 20260.7 | 23275.62 | 20296.88 | 24724.67 | 21771.29 | 13194.37 | 24776.72 | 22153.64 | 24768.21 | 24151.2 | 25142.08 | 28315.35
| Total Source Energy (MJ/m2) | 5782.99 | 6267.72 | 5202.12 | 5572.91 | 4846.14 | 5567.27 | 4854.79 | 5913.87 | 5207.45 | 3155.95 | 5926.32 | 5298.91 | 5924.28 | 5776.7 | 6013.71 | 6772.72
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12
| Total Building | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12
Emissions
| Carbon Equivalent (kg) | 553041.023 | 657422.7308 | 564014.1361 | 574332.1133 | 221152.7799 | 591883.8788 | 227972.2041 | 504854.1821 | 699076.9497 | 169549.5688 | 940050.6348 | 700429.8701 | 635373.6965 | 653439.7556 | 635080.4163 | 577738.9396
| CO2 (kg) | 1283880 | 1657380 | 1337550 | 1324490 | 595637.3887 | 1417650 | 617716.2028 | 1164370 | 1652660 | 431000.9307 | 2205010 | 1661930 | 1507860 | 1557830 | 1516380 | 1496710
| NOX (kg) | 2250.1097 | 2154.6142 | 2213.7435 | 2457.471 | 513.2971 | 2260.8083 | 534.8484 | 2170.9184 | 2795.781 | 581.5113 | 3851.651 | 2785.2734 | 2556.1156 | 2596.2211 | 2529.9331 | 1746.7707
| SO2 (kg) | 8542.4765 | 9111.1184 | 7236.7443 | 6158.9519 | 4917.0346 | 9160.0506 | 4647.5815 | 6156.0099 | 7019.7733 | 1216.7338 | 11100.361 | 6917.3855 | 3873.405 | 4282.4149 | 3763.0092 | 8124.0285
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.039 | 0.0257 | 0.0197 | 0.0227 | 0.0023 | 0.0173 | 0.0023 | 0.0251 | 0.0276 | 0.0051 | 0.0338 | 0.0273 | 0.0287 | 0.0301 | 0.028 | 0.0282
| Water for Electricity (m3) | 1057.24 | 3107.83 | 53455.2 | 10954.7 | 29666.5 | 45681.4 | 28039.1 | 382.8286 | 7298.83 | 16072.5 | 2555.22 | 7192.19 | 2545.44 | 101569 | 2472.72 | 1630.17

## Picture
DOE Commercial Building Benchmark - Super Market
Sales
Bakery
Deli
Produce
Office
DryStorage

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Deli_Exhaust_SCH | On/Off | Through 12/31 | WinterDesign, SummerDesign | [24 empty] | 24 | 0 | 0 | bar: 1 to 24
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | 13.9 | 91.6 | 4776.29
|  |  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15 | 12.3
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.15 | 0.15 | 9.8
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | 11.3 | 72.2 | 3764.71
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | 9.9
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 5.8
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0 | 0 | 7.6 | 49 | 2555
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | 7.6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 3.4
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16 | 115.5 | 6022.5
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19.5
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLGSETP_SCH | Temperature | Through 12/31 | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 0 | 0
|  |  | Other | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624
HTGSETP_SCH | Temperature | Through 12/31 | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4 | 0 | 0
|  |  | Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8
HVACOperationSchd | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 112 | 5840
MinOA_Sched | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 112 | 5840
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Bakery_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Bakery_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Bakery_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Bakery_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Deli_Case:1_ MULTIDECKDIARYANDDELICASE_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2 | 10.4 | 72.8 | 3796
Deli_Case:1_ MULTIDECKDIARYANDDELICASE_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Deli_Case:1_ MULTIDECKDIARYANDDELICASE_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Deli_Case:1_ MULTIDECKDIARYANDDELICASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 595 | 31025
Deli_Case:2_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Deli_Case:2_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Deli_Case:2_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Deli_Case:2_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Produce_Case:1_ MULTIDECKDIARYANDDELICASE_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2 | 10.4 | 72.8 | 3796
Produce_Case:1_ MULTIDECKDIARYANDDELICASE_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Produce_Case:1_ MULTIDECKDIARYANDDELICASE_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Produce_Case:1_ MULTIDECKDIARYANDDELICASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 595 | 31025
Sales_Case:1_MEATDISPLAYCASE_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Sales_Case:1_MEATDISPLAYCASE_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Sales_Case:1_MEATDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 595 | 31025
Sales_Case:2_ MULTIDECKDIARYANDDELICASE_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2 | 10.4 | 72.8 | 3796
Sales_Case:2_ MULTIDECKDIARYANDDELICASE_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Sales_Case:2_ MULTIDECKDIARYANDDELICASE_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Sales_Case:2_ MULTIDECKDIARYANDDELICASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 595 | 31025
Sales_Case:3_GLASSDOORFROZENFOOD_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2 | 10.4 | 72.8 | 3796
Sales_Case:3_GLASSDOORFROZENFOOD_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57 | 3.97 | 206.83
Sales_Case:3_GLASSDOORFROZENFOOD_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73 | 5.13 | 267.67
Sales_Case:3_GLASSDOORFROZENFOOD_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 595 | 31025
Sales_Case:4_OPENWELLICECREAMDISPLAYCASE_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2 | 10.4 | 72.8 | 3796
Sales_Case:4_OPENWELLICECREAMDISPLAYCASE_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Sales_Case:4_OPENWELLICECREAMDISPLAYCASE_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Sales_Case:4_OPENWELLICECREAMDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 595 | 31025
Sales_Case:5_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Sales_Case:5_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Sales_Case:5_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Sales_Case:5_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Sales_Case:6_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Sales_Case:6_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Sales_Case:6_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Sales_Case:6_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Sales_Case:7_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Sales_Case:7_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Sales_Case:7_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Sales_Case:7_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0.23 | 0.13 | 0.08 | 6.62 | 44.59 | 2325.05
|  |  | Sat, WinterDesign | 0.11 | 0.1 | 0.08 | 0.06 | 0.06 | 0.06 | 0.07 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0.16 | 0.13 | 6.9
|  |  | Sun, Hol, Other | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07 | 0.1 | 0.12 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.1 | 0.06 | 4.59
Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600