## BuildingSummary
Building Summary Large Hotel new construction
|  | Value | Data Source
Program
| Building Name | Large Hotel
| Available Fuel Types | gas, electricity
| Principal Building Activity | Lodging
Form
| Total Floor Area (m2) | 11344.93 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 3.8 1st floor, 5.1 other floors
| Number of Floors | 6 plus basement
Window Fraction (Window to Wall Ratio)
| South | 0.3254
| East | 0.2112
| North | 0.2311
| West | 0.2112
| Total | 0.2663
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | See pictures
| Floor to Ceiling Height (m) | 3.96 1st floor, 3.05 other floors
| Floor to Floor Height (m) | 3.96 1st floor, 3.05 other floors
| Roof type | Insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Mass Wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 4462.84
| Net Dimensions - Total Area (m2) | 3248.53
| Wall to Skin Ratio | 0.75127
Roof
| Construction Type | Insulation entirely above deck | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1477.55
| Net Dimensions - Total Area (m2) | 1477.55
| Roof to Skin Ratio | 0.24873
Window Dimensions (m2)
| South | 609.46
| East | 85.84
| North | 432.93
| West | 85.84
| Total Area (m2) | 1214.07
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Basement
| Construction | 4 in slab w/carpet
| Dimensions - Total Area (m2) | 1978.83
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 15687.82
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 22690.58
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.31 | See Benchmark Technical Report
HVAC
| System Type | FCU in rooms, CV ventilation, MZVAV in common areas | 2003 CBECS
| Heating Type | Gas boiler | 2003 CBECS
| Cooling Type | Air cooled chiller | 2003 CBECS
| Fan Control | Variable | 2003 CBECS
Service Water Heating
| SWH Type | gas boiler
| Fuel | gas
| Thermal Efficiency (%) | 80
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 7180

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Basement | Yes | 1 | 1978.83 | 4826.41 | 2.439 | 0 | 0 | 37.1613 | 53.2498 | 10.76 | 5.38 | 0 | 0 | 0 | 0.25398 | 502.5718 | 0 | 0
Retail_1_Flr_1 | Yes | 1 | 67.07 | 265.76 | 3.9624 | 68.84 | 23.3 | 6.1939 | 10.8285 | 16.14 | 10.76 | 0 | 0 | 0 | 1.5239 | 102.2043 | 0 | 0.55659
Retail_2_Flr_1 | Yes | 1 | 77.67 | 307.76 | 3.9624 | 26.57 | 0 | 6.1939 | 12.5399 | 16.14 | 10.76 | 0 | 0 | 0 | 1.5239 | 118.3571 | 0 | 0.093963
Mech_Flr_1 | Yes | 1 | 164.24 | 650.8 | 3.9625 | 62.8 | 0 | 0 | 0 | 16.14 | 5.38 | 0 | 0 | 0 | 0.25398 | 41.7127 | 0 | 0.10502
Storage_Flr_1 | Yes | 1 | 94.76 | 375.47 | 3.9623 | 36.23 | 0 | 46.4516 | 2.04 | 9.684 | 2.69 | 0 | 0 | 0 | 0.76195 | 72.1998 | 0 | 0.10502
Laundry_Flr_1 | Yes | 1 | 78.04 | 309.22 | 3.9623 | 85.75 | 0 | 23.2258 | 3.3601 | 6.456 | 61.6768 | 535.8521 | 592.7936 | 7.0785 | 0 | 23.7842 | 235.9735 | 0.30182
Cafe_Flr_1 | Yes | 1 | 188.86 | 748.35 | 3.9625 | 152.17 | 65.62 | 1.3935 | 135.5247 | 13.988 | 5.38 | 0 | 0 | 9.438 | 0 | 1279.0819 | 0 | 0.49598
Lobby_Flr_1 | Yes | 1 | 1308.19 | 5183.56 | 3.9624 | 434.79 | 85.24 | 3.0965 | 422.479 | 11.836 | 8.07 | 0 | 0 | 9.438 | 0 | 3987.3572 | 0 | 0.096077
Room_1_Flr_3 | Yes | 4 | 39.02 | 118.94 | 3.0482 | 39.95 | 13.18 | 26.0133 | 1.5 | 11.836 | 14.3 | 0 | 4.7317 | 0 | 0 | 14.157 | 0 | 0.36556
Room_2_Flr_3 | Yes | 4 | 39.02 | 118.93 | 3.0479 | 39.95 | 13.18 | 26.0133 | 1.5 | 11.836 | 14.3 | 0 | 4.7317 | 0 | 0 | 14.157 | 0 | 0.3656
Room_3_Mult19_Flr_3 | Yes | 76 | 24.52 | 74.75 | 3.0485 | 11.15 | 3.68 | 16.3467 | 1.5 | 11.836 | 14.3 | 0 | 89.9032 | 0 | 0 | 14.157 | 0 | 0.16235
Room_4_Mult19_Flr_3 | Yes | 76 | 24.53 | 74.77 | 3.0481 | 11.15 | 3.68 | 16.3533 | 1.5 | 11.836 | 14.3 | 0 | 89.9032 | 0 | 0 | 14.157 | 0 | 0.1623
Room_5_Flr_3 | Yes | 4 | 39.02 | 118.94 | 3.0482 | 39.95 | 13.18 | 26.0133 | 1.5 | 11.836 | 14.3 | 0 | 4.7317 | 0 | 0 | 14.157 | 0 | 0.36556
Room_6_Flr_3 | Yes | 4 | 39.02 | 118.93 | 3.0479 | 39.95 | 13.18 | 26.0133 | 1.5 | 11.836 | 14.3 | 0 | 4.7317 | 0 | 0 | 14.157 | 0 | 0.3656
Corridor_Flr_3 | Yes | 4 | 389.4 | 1186.91 | 3.048 | 48.31 | 15.94 | 92.9031 | 4.1915 | 5.38 | 0 | 0 | 0 | 0 | 0.25398 | 98.8976 | 0 | 0.044299
Room_1_Flr_6 | Yes | 1 | 39.02 | 118.94 | 3.0482 | 39.95 | 13.19 | 26.0133 | 1.5 | 11.836 | 14.3 | 0 | 4.7317 | 0 | 0 | 14.157 | 0 | 0.72262
Room_2_Flr_6 | Yes | 1 | 39.02 | 118.93 | 3.0479 | 39.95 | 13.19 | 26.0133 | 1.5 | 11.836 | 14.3 | 0 | 4.7317 | 0 | 0 | 14.157 | 0 | 0.72268
Room_3_Mult9_Flr_6 | Yes | 9 | 24.53 | 74.77 | 3.0481 | 63.18 | 6.75 | 16.3533 | 1.5 | 11.836 | 14.3 | 0 | 42.5858 | 0 | 0 | 14.157 | 0 | 1.2767
Banquet_Flr_6 | Yes | 1 | 331.66 | 1010.89 | 3.048 | 97.55 | 32.21 | 1.3935 | 237.997 | 13.988 | 67.816 | 0 | 0 | 10 | 0 | 2246.2157 | 0 | 0.46211
Dining_Flr_6 | Yes | 1 | 331.66 | 1010.89 | 3.048 | 97.55 | 32.21 | 1.3935 | 237.997 | 13.988 | 67.816 | 0 | 0 | 10 | 0 | 2246.2157 | 0 | 0.46211
Kitchen_Flr_6 | Yes | 1 | 103.3 | 314.87 | 3.0481 | 87.33 | 26.38 | 18.5806 | 5.5596 | 12.912 | 508.0443 | 1612.8391 | 503.4582 | 8 | 0 | 39.3533 | 1887.788 | 0.65892
Corridor_Flr_6 | Yes | 1 | 412.12 | 1256.16 | 3.048 | 137.5 | 28.22 | 92.9031 | 4.436 | 5.38 | 0 | 0 | 0 | 0 | 0.25398 | 104.6679 | 0 | 0.4762
Building Total Conditioned Zones |  |  | 11344.93 | 35185.06 |  | 4462.84 | 1214.31 |  | 1411.2773 |  |  |  | 15229.9891
Data Source | [7 empty] | 1 |  | 2 | 4, 5 | 4, 5 | 4, 5 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report
[5] Smith, V. A. and D.R. Fisher. (2001). Estimating Food Service Loads and Profiles. ASHRAE Transactions 2001. V. 107. Pt 2. Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 11.7809 | 67.2676 | 13.5344 | 68.8195 |  | 85.905 | 11.4406 | 103.8454 | 4.0102 | 13.276 | 99.5961 | 21.6382 | 24.5558 | 6.2509 | 4.15 | 0.38782
Fabric | [6 empty] | weighting factor is for all of 3B
Exterior walls
| Construction Type | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall
| R-value (m2·K / W) | 1.1669 | 1.1669 | 1.1669 | 1.4327 | 1.4327 | 1.4327 | 1.4327 | 1.692 | 1.692 | 1.692 | 1.9569 | 1.9569 | 1.9569 | 1.9569 | 2.2026 | 2.4814
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.849 | 2.849 | 2.849 | 2.849 | 2.7933 | 3.7175
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
| SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.702
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.162 | 0.162 | 0.162 | 0.223 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.633
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement
| Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
| R-value (m2·K / W) | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366
HVAC
HVAC Sizing
Air Conditioning (kW)
| COOLSYS1 CHILLER | 3646.0214 | 3476.2505 | 2830.165 | 3112.8895 | 2133.6393 | 2123.5384 | 1555.6826 | 3166.9676 | 1510.574 | 1678.9859 | 3136.138 | 1499.3268 | 3103.4119 | 1407.2227 | 2427.234 | 1321.877
Heating (kW)
| HEATSYS1 BOILER | 2126.0786 | 2837.7778 | 2392.0257 | 3077.3534 | 2196.3643 | 2591.3273 | 2428.9352 | 3412.5042 | 2776.6811 | 2925.3227 | 4011.374 | 3324.5001 | 4344.7147 | 4007.2531 | 4447.748 | 5546.105
HVAC Efficiency
| Air Conditioning (COP) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
| Heating Efficiency (%) | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
HVAC Control - Economizer
| KITCHEN_FLR_6 EXHAUST FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| LAUNDRY_FLR_1 EXHAUST FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| ROOM_1_FLR_3 FAN COILFAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| ROOM_1_FLR_6 FAN COILFAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| ROOM_2_FLR_3 FAN COILFAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| ROOM_2_FLR_6 FAN COILFAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| ROOM_3_MULT19_FLR_3 FAN COILFAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| ROOM_5_FLR_3 FAN COILFAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| ROOM_6_FLR_3 FAN COILFAN | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA
| FLR_3_DOAS_FAN | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA
Fan Max Flow Rate (m3/s )
| CORRIDOR_FLR_6 UNIT HEATERFAN | 0.1 | 0.25 | 0.18 | 0.27 | 0.1 | 0.21 | 0.17 | 0.3 | 0.33 | 0.23 | 0.4 | 0.45 | 0.47 | 0.54 | 0.51 | 0.5
| DINING_FLR_6 EXHAUST FAN | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84
| KITCHEN_FLR_6 EXHAUST FAN | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
| LAUNDRY_FLR_1 EXHAUST FAN | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
| ROOM_1_FLR_3 FAN COILFAN | 1.13 | 1.16 | 1.31 | 1.29 | 1.17 | 1.39 | 1.72 | 1.25 | 1.38 | 1.23 | 1.27 | 1.36 | 1.27 | 1.33 | 1.41 | 1.76
| ROOM_1_FLR_6 FAN COILFAN | 0.31 | 0.32 | 0.36 | 0.37 | 0.33 | 0.39 | 0.47 | 0.35 | 0.39 | 0.34 | 0.35 | 0.38 | 0.35 | 0.37 | 0.39 | 0.48
| ROOM_2_FLR_3 FAN COILFAN | 1.15 | 1.17 | 1.31 | 1.29 | 1.13 | 1.39 | 1.47 | 1.24 | 1.38 | 1.16 | 1.25 | 1.34 | 1.24 | 1.29 | 1.37 | 1.61
| ROOM_2_FLR_6 FAN COILFAN | 0.32 | 0.33 | 0.36 | 0.37 | 0.32 | 0.39 | 0.41 | 0.35 | 0.39 | 0.32 | 0.35 | 0.38 | 0.34 | 0.36 | 0.38 | 0.45
| ROOM_3_MULT19_FLR_3 FAN COILFAN | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45
| ROOM_3_MULT9_FLR_6 FAN COILFAN | 1.15 | 1.15 | 1.32 | 1.15 | 1.15 | 1.26 | 2.41 | 1.15 | 1.19 | 1.62 | 1.21 | 1.2 | 1.3 | 1.4 | 1.53 | 2.69
| ROOM_4_MULT19_FLR_3 FAN COILFAN | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45
| ROOM_5_FLR_3 FAN COILFAN | 0.93 | 0.94 | 1.06 | 1.06 | 0.94 | 1.1 | 1.37 | 1.02 | 1.08 | 1 | 1.03 | 1.05 | 1.04 | 1.05 | 1.14 | 1.57
| ROOM_6_FLR_3 FAN COILFAN | 0.95 | 0.95 | 1.07 | 1.06 | 0.92 | 1.1 | 1.14 | 1.02 | 1.07 | 0.94 | 1.02 | 1.04 | 1.03 | 1.03 | 1.12 | 1.41
| FLR_3_DOAS_FAN | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38
| FLR_6_DOAS_FAN | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.079771 | 0.10772 | 0.075855 | 0.098926 | 0.12217 | 0.089833 | 0.14356 | 0.068926 | 0.037038 | 0.071132 | 0.09687 | 0.03704 | 0.054344 | 0.070517 | 0.05402 | 0.090012
| Total Cost ($/m2) | 14.83 | 18.82 | 13.04 | 16.06 | 18.86 | 14.76 | 21.48 | 10.86 | 5.71 | 10.42 | 14.81 | 5.58 | 8.25 | 10.42 | 7.95 | 13.33
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011451 | 0.0081749 | 0.0085448 | 0.010664 | 0.0084023 | 0.0080812 | 0.0084141 | 0.010025 | 0.0071673 | 0.0083008 | 0.008831 | 0.0071662 | 0.0079649 | 0.008668 | 0.0079623 | 0.0041847
| Total Cost ($/m2) | 5.18 | 4.86 | 4.42 | 7.78 | 5.31 | 4.88 | 6.22 | 8.8 | 5.75 | 7.35 | 9 | 6.74 | 9.2 | 9.56 | 10.5 | 7.07
Total Utility Costs
| Cost Intensity ($/m2) | 20.01 | 23.68 | 17.46 | 23.84 | 24.17 | 19.64 | 27.7 | 19.66 | 11.46 | 17.78 | 23.81 | 12.31 | 17.45 | 19.98 | 18.45 | 20.39
Energy - End Uses
Electricity (kWh)
| Heating | 2.7778 | 16.6667 | 197.2222 | 0 | 0 | 152.7778 | 0 | 33.3333 | 2.7778 | 0 | 186.1111 | 144.4444 | 902.7778 | 658.3333 | 1413.8889 | 3075
| Cooling | 518494.4444 | 397261.1111 | 362644.4444 | 261219.4444 | 180819.4444 | 280411.1111 | 116758.3333 | 212569.4444 | 167736.1111 | 94272.2222 | 161666.6667 | 131775 | 148638.8889 | 101858.3333 | 93669.4444 | 84919.4444
| Interior Lighting | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111
| Exterior Lighting | 15175 | 15169.4444 | 15166.6667 | 15163.8889 | 15152.7778 | 15150 | 15158.3333 | 15150 | 15155.5556 | 15125 | 15150 | 15141.6667 | 15141.6667 | 15138.8889 | 15130.5556 | 15036.1111
| Interior Equipment | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222
| Exterior Equipment | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556
| Fans | 310763.8889 | 309008.3333 | 315519.4444 | 312216.6667 | 307188.8889 | 316113.8889 | 320261.1111 | 308969.4444 | 317869.4444 | 308472.2222 | 309352.7778 | 315652.7778 | 309897.2222 | 313672.2222 | 313241.6667 | 329772.2222
| Pumps | 34330.5556 | 30266.6667 | 26022.2222 | 23741.6667 | 18994.4444 | 21980.5556 | 16150 | 21516.6667 | 18244.4444 | 15375 | 19672.2222 | 17025 | 19825 | 16580.5556 | 17269.4444 | 18863.8889
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 21797.2222 | 21100 | 21263.8889 | 20494.4444 | 20541.6667 | 20794.4444 | 20025 | 20036.1111 | 20063.8889 | 19666.6667 | 19713.8889 | 19702.7778 | 19558.3333 | 19375 | 19111.1111 | 18755.5556
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 2109752.7778 | 1982011.1111 | 1950002.7778 | 1842027.7778 | 1751883.3333 | 1863791.6667 | 1697541.6667 | 1787458.3333 | 1748261.1111 | 1662097.2222 | 1734930.5556 | 1708630.5556 | 1723150 | 1676475 | 1669019.4444 | 1679613.8889
Gas (MJ)
| Heating | 160140 | 772390 | 473610 | 1341910 | 418970 | 762890 | 814690 | 2263010 | 1550400 | 1965010 | 3203720 | 2341420 | 4169370 | 3482220 | 5083060 | 8136520
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 3733730 | 4733760 | 4159320 | 5696910 | 5509670 | 4851590 | 6333890 | 6453970 | 6310440 | 6847790 | 7118450 | 7083790 | 7692620 | 7796880 | 8639650 | 9786010
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 5132520 | 6744790 | 5871580 | 8277480 | 7167290 | 6853130 | 8387220 | 9955620 | 9099490 | 10051440 | 11560830 | 10663860 | 13100650 | 12517750 | 14961360 | 19161180
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 12727630 | 13880030 | 12891590 | 14908780 | 13474070 | 13562780 | 14498370 | 16390470 | 15393230 | 16035000 | 17806580 | 16814930 | 19303990 | 18553060 | 20969830 | 25207790
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0.00088142 | 0.0052885 | 0.062581 | 0 | 0 | 0.048478 | 0 | 0.010577 | 0.00088142 | 0 | 0.059055 | 0.045834 | 0.28646 | 0.2089 | 0.44864 | 0.97574
| Cooling (elec) | 164.5247 | 126.0558 | 115.0715 | 82.8881 | 57.3762 | 88.9779 | 37.0489 | 67.4509 | 53.2247 | 29.9137 | 51.2988 | 41.8138 | 47.1649 | 32.3209 | 29.7225 | 26.946
| Interior Lighting (elec) | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025
| Exterior Lighting (elec) | 4.8152 | 4.8135 | 4.8126 | 4.8117 | 4.8082 | 4.8073 | 4.8099 | 4.8073 | 4.809 | 4.7993 | 4.8073 | 4.8046 | 4.8046 | 4.8038 | 4.8011 | 4.7711
| Interior Equipment (elec) | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696
| Exterior Equipment (elec) | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184
| Fans (elec) | 98.6092 | 98.0521 | 100.1182 | 99.0702 | 97.4748 | 100.3068 | 101.6228 | 98.0398 | 100.8639 | 97.882 | 98.1614 | 100.1605 | 98.3342 | 99.5321 | 99.3954 | 104.6408
| Pumps (elec) | 10.8935 | 9.604 | 8.2572 | 7.5335 | 6.0272 | 6.9747 | 5.1246 | 6.8275 | 5.7892 | 4.8787 | 6.2422 | 5.4022 | 6.2907 | 5.2612 | 5.4798 | 5.9857
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 6.9165 | 6.6953 | 6.7473 | 6.5031 | 6.5181 | 6.5983 | 6.3542 | 6.3577 | 6.3665 | 6.2405 | 6.2555 | 6.2519 | 6.2061 | 6.1479 | 6.0642 | 5.9514
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 669.4505 | 628.9165 | 618.7599 | 584.4981 | 555.8941 | 591.404 | 538.6508 | 567.1825 | 554.7447 | 527.4039 | 550.5148 | 542.1695 | 546.7767 | 531.9661 | 529.6004 | 532.9621
Gas (MJ/m2)
| Heating (gas) | 14.1151 | 68.0802 | 41.7451 | 118.279 | 36.929 | 67.2429 | 71.8087 | 199.4669 | 136.6558 | 173.2005 | 282.3833 | 206.3782 | 367.4979 | 306.9309 | 448.0326 | 717.1716
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 329.0996 | 417.2445 | 366.612 | 502.1388 | 485.635 | 427.6303 | 558.2837 | 568.8678 | 556.2167 | 603.58 | 627.4366 | 624.3816 | 678.0453 | 687.235 | 761.5187 | 862.5615
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 452.3921 | 594.5013 | 517.5346 | 729.5962 | 631.7415 | 604.0507 | 739.2689 | 877.5113 | 802.05 | 885.9571 | 1018.9982 | 939.9372 | 1154.7215 | 1103.3433 | 1318.7287 | 1688.9106
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 1121.8426 | 1223.4178 | 1136.2944 | 1314.0942 | 1187.6356 | 1195.4547 | 1277.9197 | 1444.6938 | 1356.7948 | 1413.3618 | 1569.513 | 1482.1067 | 1701.4982 | 1635.3095 | 1848.3291 | 2221.8727
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 376.6357 | 362.2208 | 326.9893 | 329.2755 | 329.2308 | 312.1424 | 312.7448 | 308.4862 | 311.9229 | 308.1131 | 308.3857 | 310.8998 | 306.9607 | 308.1357 | 307.106 | 311.9265
| Feb | 375.5719 | 340.6627 | 331.7206 | 313.1747 | 322.2843 | 318.5122 | 323.9583 | 308.9577 | 313.2754 | 312.07 | 308.0479 | 310.7736 | 307.2025 | 310.2515 | 308.7903 | 311.194
| Mar | 386.38 | 362.3534 | 367.876 | 337.9507 | 322.457 | 329.1792 | 314.3134 | 333.9984 | 319.6577 | 322.6578 | 321.8763 | 322.7132 | 311.4706 | 319.3609 | 309.7518 | 315.8782
| Apr | 393.0419 | 386.8727 | 366.4093 | 353.4614 | 341.0742 | 360.7989 | 325.0196 | 334.3995 | 336.5263 | 319.2073 | 317.2333 | 332.8422 | 328.2956 | 322.034 | 313.5345 | 316.8015
| May | 406.5766 | 420.1389 | 395.573 | 384.2575 | 340.6526 | 374.4882 | 327.4518 | 368.1449 | 350.7624 | 334.5088 | 346.3754 | 345.4547 | 382.8936 | 331.4726 | 329.6484 | 333.1347
| Jun | 429.1125 | 412.1735 | 456.8674 | 403.5028 | 339.2091 | 423.7562 | 331.0335 | 406.8295 | 363.1566 | 340.3549 | 380.1214 | 350.4972 | 396.7848 | 361.257 | 367.1073 | 355.8808
| Jul | 415.6243 | 429.1541 | 443.6799 | 416.0736 | 342.4773 | 419.8821 | 352.4753 | 428.6623 | 372.4243 | 350.6779 | 399.9034 | 363.9306 | 411.5485 | 361.5633 | 384.0297 | 354.8876
| Aug | 420.2757 | 438.551 | 445.469 | 400.4025 | 352.8703 | 407.4437 | 328.7437 | 428.3239 | 369.4086 | 344.2608 | 418.8505 | 355.1936 | 407.4872 | 353.7585 | 374.5686 | 346.7792
| Sep | 410.2135 | 414.6797 | 409.9352 | 381.5697 | 345.237 | 381.6912 | 353.0754 | 357.3178 | 346.2694 | 359.259 | 366.8763 | 346.3475 | 352.512 | 346.4248 | 351.1241 | 318.3067
| Oct | 407.7201 | 391.4102 | 373.6755 | 356.8217 | 338.8899 | 353.1829 | 334.7441 | 361.8814 | 338.6732 | 323.1115 | 338.8798 | 325.804 | 326.8392 | 325.903 | 315.4925 | 315.0969
| Nov | 388.9296 | 381.749 | 334.8877 | 326.1603 | 329.8939 | 323.7416 | 319.2481 | 338.2797 | 319.7815 | 310.987 | 336.1076 | 312.345 | 312.1286 | 310.2319 | 310.8688 | 309.331
| Dec | 373.8636 | 363.585 | 325.8014 | 325.6694 | 330.403 | 317.1783 | 312.0586 | 307.7338 | 310.848 | 307.5114 | 308.5831 | 309.8327 | 306.744 | 307.8926 | 306.6879 | 310.4992
Time of Peak Electrical Demand
| Jan | 06-JAN-20:00 | 06-JAN-20:10 | 27-JAN-20:10 | 24-JAN-20:00 | 26-JAN-20:10 | 18-JAN-20:40 | 27-JAN-20:19 | 05-JAN-20:00 | 26-JAN-20:19 | 02-JAN-20:00 | 17-JAN-20:00 | 23-JAN-20:10 | 30-JAN-20:00 | 30-JAN-20:00 | 09-JAN-20:10 | 12-JAN-20:10
| Feb | 23-FEB-20:10 | 20-FEB-20:10 | 27-FEB-20:10 | 21-FEB-20:00 | 13-FEB-20:00 | 27-FEB-20:10 | 15-FEB-20:10 | 15-FEB-20:30 | 13-FEB-20:19 | 21-FEB-20:10 | 27-FEB-20:00 | 10-FEB-20:00 | 27-FEB-20:00 | 03-FEB-20:40 | 22-FEB-20:00 | 03-FEB-20:10
| Mar | 13-MAR-19:10 | 28-MAR-19:00 | 17-MAR-19:10 | 28-MAR-19:10 | 29-MAR-19:00 | 30-MAR-19:10 | 30-MAR-19:19 | 09-MAR-20:00 | 20-MAR-19:10 | 29-MAR-19:10 | 31-MAR-19:10 | 30-MAR-19:10 | 28-MAR-19:00 | 30-MAR-19:10 | 22-MAR-19:10 | 29-MAR-19:30
| Apr | 03-APR-19:10 | 30-APR-19:10 | 26-APR-19:10 | 14-APR-19:10 | 11-APR-19:10 | 21-APR-19:10 | 13-APR-19:10 | 05-APR-19:10 | 21-APR-19:10 | 14-APR-19:10 | 28-APR-19:00 | 26-APR-19:10 | 02-APR-19:49 | 06-APR-19:10 | 04-APR-19:10 | 25-APR-19:10
| May | 15-MAY-19:10 | 26-MAY-19:10 | 28-MAY-19:10 | 31-MAY-19:10 | 30-MAY-19:10 | 31-MAY-19:10 | 25-MAY-19:19 | 15-MAY-19:10 | 30-MAY-19:10 | 04-MAY-19:19 | 30-MAY-19:19 | 23-MAY-19:19 | 27-MAY-17:10 | 25-MAY-19:10 | 31-MAY-19:10 | 24-MAY-19:10
| Jun | 27-JUN-19:19 | 29-JUN-19:30 | 27-JUN-19:10 | 08-JUN-19:10 | 28-JUN-19:10 | 27-JUN-19:10 | 16-JUN-19:30 | 30-JUN-19:10 | 28-JUN-19:19 | 27-JUN-19:10 | 19-JUN-19:30 | 27-JUN-19:10 | 29-JUN-19:10 | 29-JUN-19:10 | 14-JUN-19:10 | 15-JUN-19:00
| Jul | 11-JUL-19:19 | 05-JUL-19:10 | 11-JUL-19:10 | 03-JUL-19:10 | 28-JUL-19:00 | 24-JUL-19:10 | 02-JUL-19:30 | 24-JUL-19:10 | 18-JUL-19:10 | 24-JUL-19:10 | 14-JUL-19:30 | 10-JUL-19:10 | 13-JUL-19:10 | 21-JUL-19:10 | 06-JUL-19:10 | 11-JUL-19:10
| Aug | 21-AUG-19:10 | 06-AUG-19:10 | 01-AUG-19:10 | 14-AUG-19:10 | 16-AUG-19:10 | 04-AUG-19:10 | 14-AUG-19:10 | 17-AUG-19:10 | 01-AUG-19:10 | 18-AUG-19:19 | 04-AUG-19:10 | 29-AUG-19:10 | 25-AUG-19:10 | 11-AUG-19:10 | 13-AUG-19:19 | 15-AUG-19:10
| Sep | 01-SEP-19:00 | 15-SEP-19:19 | 08-SEP-19:10 | 11-SEP-19:10 | 25-SEP-19:10 | 01-SEP-19:00 | 28-SEP-19:00 | 27-SEP-19:10 | 13-SEP-19:10 | 02-SEP-17:10 | 06-SEP-19:10 | 01-SEP-19:10 | 13-SEP-19:10 | 01-SEP-19:10 | 08-SEP-19:10 | 08-SEP-19:49
| Oct | 06-OCT-19:10 | 30-OCT-19:10 | 02-OCT-19:10 | 20-OCT-19:10 | 05-OCT-19:00 | 03-OCT-19:10 | 16-OCT-19:10 | 02-OCT-19:00 | 02-OCT-19:10 | 17-OCT-19:10 | 30-OCT-19:10 | 05-OCT-19:10 | 08-OCT-19:10 | 05-OCT-19:10 | 06-OCT-19:10 | 03-OCT-19:10
| Nov | 01-NOV-19:00 | 27-NOV-20:10 | 02-NOV-19:10 | 22-NOV-20:00 | 09-NOV-20:00 | 09-NOV-20:10 | 15-NOV-20:00 | 03-NOV-19:10 | 09-NOV-20:00 | 03-NOV-19:00 | 02-NOV-19:00 | 01-NOV-19:40 | 02-NOV-19:10 | 20-NOV-20:00 | 02-NOV-19:00 | 22-NOV-20:00
| Dec | 15-DEC-20:10 | 02-DEC-20:10 | 13-DEC-20:00 | 04-DEC-20:00 | 18-DEC-20:10 | 05-DEC-20:10 | 07-DEC-20:19 | 06-DEC-20:00 | 07-DEC-20:19 | 28-DEC-20:00 | 11-DEC-20:00 | 21-DEC-20:19 | 01-DEC-20:00 | 01-DEC-20:00 | 01-DEC-20:00 | 28-DEC-20:00
Source Energy
| Total Source Energy (GJ) | 30797.7 | 33280.49 | 28616.06 | 31346.7 | 27346.18 | 31484.03 | 28072.86 | 33882.56 | 30819.28 | 21399.52 | 34771.86 | 32054.19 | 35626.8 | 34648.11 | 36988.92 | 42522.49
| Total Source Energy (MJ/m2) | 2714.58 | 2933.42 | 2522.29 | 2762.97 | 2410.36 | 2775.08 | 2474.41 | 2986.49 | 2716.48 | 1886.2 | 3064.87 | 2825.33 | 3140.23 | 3053.96 | 3260.29 | 3748.03
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9
| Total Building | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9
Emissions
| Carbon Equivalent (kg) | 671152.6448 | 782748.07 | 694538.5348 | 716677.4511 | 333981.0958 | 752190.8442 | 349628.9707 | 661882.2772 | 878249.9572 | 302312.2268 | 1133450 | 890270.7137 | 826062.6302 | 838375.3816 | 841087.771 | 818149.8664
| CO2 (kg) | 1607180 | 2010350 | 1690260 | 1719050 | 920024.7916 | 1845920 | 966627.6559 | 1600390 | 2138150 | 811249.7515 | 2736490 | 2181930 | 2042320 | 2077110 | 2096540 | 2182220
| NOX (kg) | 2605.6079 | 2499.5569 | 2617.4952 | 2878.2621 | 806.787 | 2765.7944 | 849.9796 | 2633.6541 | 3350.0729 | 937.4832 | 4432.9335 | 3357.8828 | 3100.9977 | 3121.4863 | 3111.0612 | 2389.5564
| SO2 (kg) | 9031.9649 | 9455.9951 | 7842.9252 | 6467.7358 | 5099.6945 | 10254.1803 | 4941.8901 | 6527.6063 | 7636.7478 | 1287.3622 | 11695.1446 | 7464.1085 | 4070.4225 | 4479.7411 | 3943.1638 | 8555.0364
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0417 | 0.0273 | 0.0219 | 0.0245 | 0.0031 | 0.02 | 0.0031 | 0.0274 | 0.0307 | 0.0061 | 0.0365 | 0.0302 | 0.0311 | 0.0324 | 0.0304 | 0.031
| Water for Electricity (m3) | 1117.66 | 3224.96 | 57923.7 | 11500.9 | 30759.2 | 51131.2 | 29805 | 405.8203 | 7938.5 | 16981.3 | 2691.64 | 7758.55 | 2673.37 | 106195 | 2589.38 | 1716.03

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 12727.63 | 1121.84 | 1121.84
Net Site Energy | 12727.63 | 1121.84 | 1121.84
Total Source Energy | 30797.7 | 2714.58 | 2714.58
Net Source Energy | 30797.7 | 2714.58 | 2714.58
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0.01 | 160.14 | 0 | 0 | 0 | 0
Cooling | 1866.58 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 54.63 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1118.75 | 0 | 0 | 0 | 0 | 0
Pumps | 123.59 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 3733.73 | 0 | 0 | 0 | 44332.9
Refrigeration | 78.47 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7595.11 | 5132.52 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 10.76 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 13.99 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 5.38 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 5.38 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 12.91 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 6.46 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 11.84 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 16.14 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 16.14 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 16.14 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 11.84 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 9.68 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.251 | 0.11 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.62 | 65.62 | 5.835 | 0.251 | 0.11 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.15 | 8.58 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.15 | 8.59 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.83 | 5.83 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.21 | 5.21 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.251 | 0.11 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.251 | 0.11 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.251 | 0.11 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.251 | 0.11 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 85.24 | 85.24 | 5.835 | 0.251 | 0.11 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 23.3 | 23.3 | 5.835 | 0.251 | 0.11 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 5.838 | 0.251 | 0.11 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 5.838 | 0.251 | 0.11 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 4.6 | 5.838 | 0.251 | 0.11 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.59 | 8.59 | 5.838 | 0.251 | 0.11 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 5.838 | 0.251 | 0.11 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 5.838 | 0.251 | 0.11 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 4.6 | 5.838 | 0.251 | 0.11 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.59 | 8.59 | 5.838 | 0.251 | 0.11 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 3.68 | 279.51 | 5.838 | 0.251 | 0.11 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 6.75 | 60.74 | 5.838 | 0.251 | 0.11 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 3.68 | 279.6 | 5.838 | 0.251 | 0.11 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 5.838 | 0.251 | 0.11 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 5.838 | 0.251 | 0.11 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 5.838 | 0.251 | 0.11 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 5.838 | 0.251 | 0.11 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 5.84 | 0.251 | 0.11
North Total or Average |  |  | 432.93 | 5.84 | 0.251 | 0.11
Non-North Total or Average |  |  | 781.15 | 5.84 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3646021.41 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 2126078.56 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 29248.4 | 20268.5 | 8979.9 | 0.69 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 7943.58 | 5539.88 | 2403.7 | 0.7 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 29786.02 | 20650.75 | 9135.27 | 0.69 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 8106.32 | 5656.28 | 2450.04 | 0.7 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 706193.2 | 446107.78 | 260085.42 | 0.63 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 40022.58 | 25227.6 | 14794.98 | 0.63 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 706193.2 | 446107.78 | 260085.42 | 0.63 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 24318.09 | 16825.72 | 7492.37 | 0.69 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 24868.77 | 17143.73 | 7725.03 | 0.69 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 81928.73 | 51785.59 | 30143.14 | 0.63 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 5414.45 | 3415.61 | 1998.84 | 0.63 | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 1038935.62 | 681291.91 | 357643.71 | 0.66 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 36701.6 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 48059.53 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16475.74 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 3344.72 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 2234.46 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 4047.91 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 37706.83 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 15314.14 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 46068.52 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 84357.2 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 962.65 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4633.86 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5650.81 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 8191.96 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 2193.41 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 8199.36 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 2200.26 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 710011.01 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 39827.49 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 710011.01 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 7785.87 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 8091.84 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 618.58 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 25443.75 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 1665.96 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | 104652.73 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.1 | 9.61 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.13 | 716.63 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.31 | 197.53 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.15 | 730.63 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.32 | 201.82 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.15 | 730.08 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.93 | 593.83 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.95 | 602.25 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 35.17 | 58520.02 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 33410.74 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 11707.09 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 129350.6828 | 205.6562 | 695.0374 | 0 | 0.0032 | 86003.6665 | 53610.4346
February | 116611.8455 | 185.9881 | 631.1965 | 0 | 0.0029 | 78104.5662 | 48389.39
March | 129634.5951 | 207.6725 | 708.8798 | 0 | 0.0033 | 87717.9713 | 53884.907
April | 129026.656 | 208.6813 | 721.1605 | 0 | 0.0033 | 89239.4305 | 53830.8724
May | 139527.1866 | 227.821 | 796.825 | 0 | 0.0037 | 98604.4104 | 58427.871
June | 137878.0919 | 226.461 | 797.8961 | 0 | 0.0037 | 98738.1215 | 57870.8342
July | 145812.1119 | 240.3405 | 850.4851 | 0 | 0.0039 | 105246.6447 | 61285.9172
August | 145104.151 | 238.8027 | 843.4367 | 0 | 0.0039 | 104374.0961 | 60951.1944
September | 139382.9926 | 228.4078 | 802.4732 | 0 | 0.0037 | 99304.0792 | 58449.8787
October | 139289.7659 | 226.4454 | 787.6932 | 0 | 0.0036 | 97473.5102 | 58229.4557
November | 128364.7446 | 206.5326 | 708.9752 | 0 | 0.0033 | 87730.5984 | 53446.6875
December | 127199.4298 | 202.7985 | 687.9061 | 0 | 0.0032 | 85121.7659 | 52775.2021
Annual Sum or Average | 1607180 | 2605.6079 | 9031.9649 | 0 | 0.0417 | 1117660 | 671152.6448
Minimum of Months | 116611.8455 | 185.9881 | 631.1965 | 0 | 0.0029 | 78104.5662 | 48389.39
Maximum of Months | 145812.1119 | 240.3405 | 850.4851 | 0 | 0.0039 | 105246.6447 | 61285.9172
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 584443000000 | 376635.695 | 06-JAN-20:00 | 115409.094 | 92719.3 | 35980.725 | 0 | 72904.105 | 3472 | 4808.862 | 0 | 48888.791 | 0 | 0 | 0 | 2452.819 | 0 | 0
February | 530764000000 | 375571.916 | 23-FEB-20:10 | 115409.094 | 92719.3 | 36134.256 | 0 | 71191.292 | 3472 | 4766.587 | 0 | 48888.791 | 0 | 0 | 0 | 2990.596 | 0 | 0
March | 596092000000 | 386380.003 | 13-MAR-19:10 | 115409.094 | 92719.3 | 36198.547 | 0 | 81701.503 | 3472 | 4955.772 | 0 | 48888.791 | 0 | 0 | 0 | 3034.995 | 0 | 0
April | 606432000000 | 393041.925 | 03-APR-19:10 | 115409.094 | 92719.3 | 36421.466 | 0 | 87976.936 | 3472 | 5085.866 | 0 | 48888.791 | 0 | 0 | 0 | 3068.472 | 0 | 0
May | 670072000000 | 406576.575 | 15-MAY-19:10 | 115409.094 | 92719.3 | 36476.763 | 0 | 101096.087 | 3472 | 5443.506 | 0 | 48888.791 | 0 | 0 | 0 | 3071.034 | 0 | 0
June | 670980000000 | 429112.48 | 27-JUN-19:19 | 115409.094 | 92719.3 | 36624.082 | 0 | 123714.79 | 3472 | 5704.547 | 0 | 48888.791 | 0 | 0 | 0 | 2579.876 | 0 | 0
July | 715209000000 | 415624.255 | 11-JUL-19:19 | 115409.094 | 92719.3 | 36253.637 | 0 | 110860.106 | 3472 | 5473.941 | 0 | 48888.791 | 0 | 0 | 0 | 2547.386 | 0 | 0
August | 709280000000 | 420275.67 | 21-AUG-19:10 | 115409.094 | 92719.3 | 36526.11 | 0 | 114543.649 | 3472 | 5581.828 | 0 | 48888.791 | 0 | 0 | 0 | 3134.898 | 0 | 0
September | 674826000000 | 410213.502 | 01-SEP-19:00 | 115409.094 | 92719.3 | 36369.756 | 0 | 105372.185 | 3472 | 5449.377 | 0 | 48888.791 | 0 | 0 | 0 | 2532.999 | 0 | 0
October | 662387000000 | 407720.061 | 06-OCT-19:10 | 115409.094 | 92719.3 | 36457.833 | 0 | 102830.457 | 3472 | 5411.917 | 0 | 48888.791 | 0 | 0 | 0 | 2530.669 | 0 | 0
November | 596178000000 | 388929.552 | 01-NOV-19:00 | 115409.094 | 92719.3 | 36167.856 | 0 | 84262.248 | 3472 | 4957.27 | 0 | 48888.791 | 0 | 0 | 0 | 3052.993 | 0 | 0
December | 578450000000 | 373863.606 | 15-DEC-20:10 | 115409.094 | 92719.3 | 36020.689 | 0 | 70627.434 | 3472 | 4285.241 | 0 | 48888.791 | 0 | 0 | 0 | 2441.057 | 0 | 0
Annual Sum or Average | 7595110000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 530764000000 | 373863.606 |  | 115409.094 | 92719.3 | 35980.725 | 0 | 70627.434 | 3472 | 4285.241 | 0 | 48888.791 | 0 | 0 | 0 | 2441.057 | 0 | 0
Maximum of Months | 715209000000 | 429112.48 |  | 115409.094 | 92719.3 | 36624.082 | 0 | 123714.79 | 3472 | 5704.547 | 0 | 48888.791 | 0 | 0 | 0 | 3134.898 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 168296.93 | 58772.34 | 0 | 227069.27
Cost per Total Building Area ($/m2) | 14.83 | 5.18 | 0 | 20.01
Cost per Net Conditioned Building Area ($/m2) | 14.83 | 5.18 | 0 | 20.01

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 13880.03 | 1223.42 | 1223.42
Net Site Energy | 13880.03 | 1223.42 | 1223.42
Total Source Energy | 33280.49 | 2933.42 | 2933.42
Net Source Energy | 33280.49 | 2933.42 | 2933.42
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0.06 | 772.39 | 0 | 0 | 0 | 0
Cooling | 1430.14 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 54.61 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1112.43 | 0 | 0 | 0 | 0 | 0
Pumps | 108.96 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 4733.76 | 0 | 0 | 0 | 44332.9
Refrigeration | 75.96 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7135.24 | 6744.79 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 10.76 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 13.99 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 5.38 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 5.38 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 12.91 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 6.46 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 11.84 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 16.14 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 16.14 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 16.14 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 11.84 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 9.68 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.251 | 0.11 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.62 | 65.62 | 5.835 | 0.251 | 0.11 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.15 | 8.58 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.15 | 8.59 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.83 | 5.83 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.21 | 5.21 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.251 | 0.11 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.251 | 0.11 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.251 | 0.11 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.251 | 0.11 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 85.24 | 85.24 | 5.835 | 0.251 | 0.11 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 23.3 | 23.3 | 5.835 | 0.251 | 0.11 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 5.838 | 0.251 | 0.11 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 5.838 | 0.251 | 0.11 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 4.6 | 5.838 | 0.251 | 0.11 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.59 | 8.59 | 5.838 | 0.251 | 0.11 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 5.838 | 0.251 | 0.11 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 5.838 | 0.251 | 0.11 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 4.6 | 5.838 | 0.251 | 0.11 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.59 | 8.59 | 5.838 | 0.251 | 0.11 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 3.68 | 279.51 | 5.838 | 0.251 | 0.11 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 6.75 | 60.74 | 5.838 | 0.251 | 0.11 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 3.68 | 279.6 | 5.838 | 0.251 | 0.11 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 5.838 | 0.251 | 0.11 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 5.838 | 0.251 | 0.11 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 5.838 | 0.251 | 0.11 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 5.838 | 0.251 | 0.11 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 5.84 | 0.251 | 0.11
North Total or Average |  |  | 432.93 | 5.84 | 0.251 | 0.11
Non-North Total or Average |  |  | 781.15 | 5.84 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3476250.45 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 2837777.85 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 29756.55 | 20608.19 | 9148.36 | 0.69 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 8156.65 | 5684.58 | 2472.06 | 0.7 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 29998.04 | 20779.86 | 9218.18 | 0.69 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 8242.72 | 5746.3 | 2496.42 | 0.7 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 698246.72 | 440343.37 | 257903.35 | 0.63 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 39866.74 | 25047.25 | 14819.49 | 0.63 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 698246.72 | 440343.37 | 257903.35 | 0.63 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 24101.45 | 16662.03 | 7439.42 | 0.69 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 24488.71 | 16864.64 | 7624.07 | 0.69 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 81018.15 | 51122.3 | 29895.85 | 0.63 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 5388.7 | 3388.86 | 1999.84 | 0.63 | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 746676.53 | 498487.04 | 248189.49 | 0.67 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 36179.82 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 46859.67 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17765.89 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 3332.46 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 2401.86 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 9635.26 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 37193.27 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 15293.58 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 46081.33 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 83746.24 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 919.9 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4584.35 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5638.36 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 13285.15 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 3575.11 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 13269.29 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 3577.85 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 823599.64 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 46199.15 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 823599.64 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 12454.58 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 12942.62 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 616.31 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 45387.07 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 2971.77 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | 206449.99 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.25 | 23.25 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.16 | 740.6 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.32 | 205.97 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.17 | 747.03 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.33 | 208.3 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.15 | 730.08 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.94 | 597.73 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.95 | 602.09 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 35.13 | 58440.53 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 31855.02 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 15626.01 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 165177.8037 | 199.8988 | 700.2692 | 0 | 0.0021 | 238797.8425 | 63607.9614
February | 145781.1875 | 176.1652 | 614.3996 | 0 | 0.0018 | 209514.0519 | 56105.0793
March | 159702.9559 | 196.1644 | 717.5517 | 0 | 0.0021 | 244708.0807 | 61872.3382
April | 159856.9365 | 198.8363 | 753.0157 | 0 | 0.0022 | 256816.0536 | 62252.017
May | 173695.2345 | 217.9973 | 845.4899 | 0 | 0.0024 | 288364.5675 | 67892.1166
June | 177146.8388 | 223.8535 | 883.6398 | 0 | 0.0025 | 301383.7464 | 69437.7228
July | 188963.9337 | 239.6218 | 954.2868 | 0 | 0.0027 | 325483.485 | 74177.4591
August | 185757.0112 | 235.3086 | 934.6378 | 0 | 0.0027 | 318780.5044 | 72886.8014
September | 171423.6106 | 216.118 | 848.0425 | 0 | 0.0024 | 289240.0617 | 67129.4679
October | 166570.6556 | 208.2819 | 799.9752 | 0 | 0.0023 | 272837.3037 | 65007.6219
November | 155216.0806 | 191.9495 | 715.549 | 0 | 0.0021 | 244032.2203 | 60301.1341
December | 161053.8862 | 195.3616 | 689.1378 | 0 | 0.002 | 235004.5765 | 62078.3503
Annual Sum or Average | 2010350 | 2499.5569 | 9455.9951 | 0 | 0.0273 | 3224960 | 782748.07
Minimum of Months | 145781.1875 | 176.1652 | 614.3996 | 0 | 0.0018 | 209514.0519 | 56105.0793
Maximum of Months | 188963.9337 | 239.6218 | 954.2868 | 0 | 0.0027 | 325483.485 | 74177.4591
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 528341000000 | 362220.818 | 06-JAN-20:10 | 115409.094 | 92719.3 | 35851.847 | 0 | 59603.705 | 3472 | 3847.736 | 0 | 48888.791 | 0 | 0 | 0 | 2428.345 | 0 | 0
February | 463550000000 | 340662.707 | 20-FEB-20:10 | 108704.857 | 91473.541 | 35811.506 | 0 | 46159.921 | 3472 | 3296.421 | 0 | 48888.791 | 0 | 0 | 0 | 2855.671 | 0 | 0
March | 541417000000 | 362353.356 | 28-MAR-19:00 | 115409.094 | 92719.3 | 36010.51 | 0 | 59547.377 | 3472 | 3871.031 | 0 | 48888.791 | 0 | 0 | 0 | 2435.252 | 0 | 0
April | 568206000000 | 386872.679 | 30-APR-19:10 | 108704.857 | 91473.541 | 36236.22 | 0 | 89289.638 | 3472 | 5814.989 | 0 | 48888.791 | 0 | 0 | 0 | 2992.644 | 0 | 0
May | 638007000000 | 420138.925 | 26-MAY-19:10 | 115409.094 | 92719.3 | 36643.625 | 0 | 113924.856 | 3472 | 6511.739 | 0 | 48888.791 | 0 | 0 | 0 | 2569.519 | 0 | 0
June | 666812000000 | 412173.509 | 29-JUN-19:30 | 115409.094 | 92719.3 | 36534.378 | 0 | 105743.914 | 3472 | 6299.639 | 0 | 48888.791 | 0 | 0 | 0 | 3106.393 | 0 | 0
July | 720133000000 | 429154.103 | 05-JUL-19:10 | 115409.094 | 92719.3 | 36758.874 | 0 | 125245.177 | 0 | 6969.918 | 0 | 48888.791 | 0 | 0 | 0 | 3162.95 | 0 | 0
August | 705302000000 | 438550.962 | 06-AUG-19:10 | 108704.857 | 91473.541 | 36579.447 | 0 | 138819.268 | 3472 | 7475.122 | 0 | 48888.791 | 0 | 0 | 0 | 3137.935 | 0 | 0
September | 639944000000 | 414679.729 | 15-SEP-19:19 | 115409.094 | 92719.3 | 36405.354 | 0 | 108769.357 | 3472 | 6479.655 | 0 | 48888.791 | 0 | 0 | 0 | 2536.178 | 0 | 0
October | 603653000000 | 391410.219 | 30-OCT-19:10 | 115409.094 | 92719.3 | 36104.516 | 0 | 86169.953 | 3472 | 5625.627 | 0 | 48888.791 | 0 | 0 | 0 | 3020.938 | 0 | 0
November | 539922000000 | 381748.969 | 27-NOV-20:10 | 115409.094 | 92719.3 | 35951.184 | 0 | 77022.625 | 3472 | 5299.372 | 0 | 48888.791 | 0 | 0 | 0 | 2986.603 | 0 | 0
December | 519948000000 | 363584.977 | 02-DEC-20:10 | 102000.62 | 88982.023 | 35811.506 | 0 | 76328.326 | 3472 | 5176.807 | 0 | 48888.791 | 0 | 0 | 0 | 2924.904 | 0 | 0
Annual Sum or Average | 7135240000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 463550000000 | 340662.707 |  | 102000.62 | 88982.023 | 35811.506 | 0 | 46159.921 | 0 | 3296.421 | 0 | 48888.791 | 0 | 0 | 0 | 2428.345 | 0 | 0
Maximum of Months | 720133000000 | 438550.962 |  | 115409.094 | 92719.3 | 36758.874 | 0 | 138819.268 | 3472 | 7475.122 | 0 | 48888.791 | 0 | 0 | 0 | 3162.95 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 213503.81 | 55137.86 | 0 | 268641.67
Cost per Total Building Area ($/m2) | 18.82 | 4.86 | 0 | 23.68
Cost per Net Conditioned Building Area ($/m2) | 18.82 | 4.86 | 0 | 23.68

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 12891.59 | 1136.29 | 1136.29
Net Site Energy | 12891.59 | 1136.29 | 1136.29
Total Source Energy | 28616.06 | 2522.29 | 2522.29
Net Source Energy | 28616.06 | 2522.29 | 2522.29
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0.71 | 473.61 | 0 | 0 | 0 | 0
Cooling | 1305.52 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 54.6 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1135.87 | 0 | 0 | 0 | 0 | 0
Pumps | 93.68 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 4159.32 | 0 | 0 | 0 | 44332.9
Refrigeration | 76.55 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7020.01 | 5871.58 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 10.76 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 13.99 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 5.38 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 5.38 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 12.91 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 6.46 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 11.84 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 16.14 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 16.14 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 16.14 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 11.84 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 9.68 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.857 | 0.984 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.251 | 0.11 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.62 | 65.62 | 5.835 | 0.251 | 0.11 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.15 | 8.58 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.15 | 8.59 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.83 | 5.83 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.21 | 5.21 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.251 | 0.11 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.251 | 0.11 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.251 | 0.11 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.251 | 0.11 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 85.24 | 85.24 | 5.835 | 0.251 | 0.11 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 23.3 | 23.3 | 5.835 | 0.251 | 0.11 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 5.838 | 0.251 | 0.11 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 5.838 | 0.251 | 0.11 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 4.6 | 5.838 | 0.251 | 0.11 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.59 | 8.59 | 5.838 | 0.251 | 0.11 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 5.838 | 0.251 | 0.11 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 5.838 | 0.251 | 0.11 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 4.6 | 5.838 | 0.251 | 0.11 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.59 | 8.59 | 5.838 | 0.251 | 0.11 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 3.68 | 279.51 | 5.838 | 0.251 | 0.11 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 6.75 | 60.74 | 5.838 | 0.251 | 0.11 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 3.68 | 279.6 | 5.838 | 0.251 | 0.11 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 5.838 | 0.251 | 0.11 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 5.838 | 0.251 | 0.11 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 5.838 | 0.251 | 0.11 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 5.838 | 0.251 | 0.11 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 5.84 | 0.251 | 0.11
North Total or Average |  |  | 432.93 | 5.84 | 0.251 | 0.11
Non-North Total or Average |  |  | 781.15 | 5.84 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2830165.01 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 2392025.7 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 30281.46 | 20789.54 | 9491.92 | 0.69 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 8312.37 | 5730.14 | 2582.23 | 0.69 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 30268.76 | 20781.78 | 9486.98 | 0.69 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 8330.7 | 5743.33 | 2587.37 | 0.69 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 521470.29 | 330124.04 | 191346.25 | 0.63 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 40075.51 | 25000.54 | 15074.96 | 0.62 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 521470.29 | 330124.04 | 191346.25 | 0.63 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 24710.79 | 16920.6 | 7790.2 | 0.68 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 24938.87 | 17041.39 | 7897.47 | 0.68 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 76119.51 | 47335.03 | 28784.48 | 0.62 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 4211.6 | 2646.07 | 1565.53 | 0.63 | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 818404.46 | 536631.57 | 281772.89 | 0.66 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 36885.03 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 35648.63 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19477.45 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 4037.74 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 2921.09 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 6814.97 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 37879.06 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 15742.6 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 46454.46 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 84270.26 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 1052.63 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4966.35 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5756.38 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 10536.45 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 2878.15 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 10557.38 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 2886.98 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 740650.98 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 42991.85 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 740650.98 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 9913.86 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 10336.72 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 594.3 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 34545.72 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 2261.92 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | 155168.78 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.18 | 17.21 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.31 | 833.04 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.36 | 230.68 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.31 | 832.86 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.36 | 231.26 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.32 | 837.64 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.06 | 676.25 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.07 | 679.85 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 35.83 | 59611.2 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 25934.55 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 13171.51 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 137404.6977 | 203.25 | 568.6133 | 0 | 0.0016 | 4198910 | 55496.7073
February | 123751.6301 | 183.7631 | 517.2409 | 0 | 0.0015 | 3819600 | 50054.0084
March | 137771.7737 | 209.1204 | 608.6714 | 0 | 0.0017 | 4495070 | 56183.6882
April | 133999.0618 | 207.1505 | 619.1789 | 0 | 0.0017 | 4572900 | 55025.0387
May | 141629.4256 | 222.5666 | 680.6258 | 0 | 0.0019 | 5026930 | 58524.4355
June | 148288.5707 | 236.7711 | 739.682 | 0 | 0.002 | 5463320 | 61654.3273
July | 158548.4235 | 254.8144 | 802.8786 | 0 | 0.0022 | 5930180 | 66088.1035
August | 155701.8824 | 249.5292 | 783.3255 | 0 | 0.0022 | 5785720 | 64829.7459
September | 145945.1249 | 231.605 | 717.6887 | 0 | 0.002 | 5300800 | 60535.9519
October | 139094.7761 | 216.5631 | 653.8298 | 0 | 0.0018 | 4828910 | 57272.7603
November | 130654.5098 | 199.1732 | 583.4194 | 0 | 0.0016 | 4308640 | 53367.803
December | 137465.4774 | 203.1887 | 567.771 | 0 | 0.0016 | 4192680 | 55505.9649
Annual Sum or Average | 1690260 | 2617.4952 | 7842.9252 | 0 | 0.0219 | 57923700 | 694538.5348
Minimum of Months | 123751.6301 | 183.7631 | 517.2409 | 0 | 0.0015 | 3819600 | 50054.0084
Maximum of Months | 158548.4235 | 254.8144 | 802.8786 | 0 | 0.0022 | 5930180 | 66088.1035
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 508883000000 | 326989.338 | 27-JAN-20:10 | 115409.094 | 92719.3 | 36435.207 | 0 | 25632.924 | 3472 | 2098.754 | 0 | 48888.791 | 0 | 0 | 0 | 2333.268 | 0 | 0
February | 462913000000 | 331720.618 | 27-FEB-20:10 | 115409.094 | 92719.3 | 36503.04 | 0 | 29668.358 | 3472 | 2195.534 | 0 | 48888.791 | 0 | 0 | 0 | 2864.502 | 0 | 0
March | 544776000000 | 367875.962 | 17-MAR-19:10 | 115409.094 | 92719.3 | 37047.39 | 0 | 63838.923 | 3472 | 3987.372 | 0 | 48888.791 | 0 | 0 | 0 | 2513.091 | 0 | 0
April | 554209000000 | 366409.267 | 26-APR-19:10 | 115409.094 | 92719.3 | 37045.276 | 0 | 62276.969 | 3472 | 3519.73 | 0 | 48888.791 | 0 | 0 | 0 | 3078.107 | 0 | 0
May | 609235000000 | 395573.031 | 28-MAY-19:10 | 108704.857 | 91473.541 | 37513.845 | 0 | 101307.55 | 0 | 4514.221 | 0 | 48888.791 | 0 | 0 | 0 | 3170.226 | 0 | 0
June | 662123000000 | 456867.351 | 27-JUN-19:10 | 115409.094 | 92719.3 | 38504.789 | 0 | 152112.625 | 0 | 6620.761 | 0 | 48888.791 | 0 | 0 | 0 | 2611.991 | 0 | 0
July | 718704000000 | 443679.863 | 11-JUL-19:10 | 115409.094 | 92719.3 | 38309.389 | 0 | 140247.756 | 0 | 5468.462 | 0 | 48888.791 | 0 | 0 | 0 | 2637.072 | 0 | 0
August | 701196000000 | 445469.031 | 01-AUG-19:10 | 115409.094 | 92719.3 | 38248.591 | 0 | 141583.739 | 0 | 5999.512 | 0 | 48888.791 | 0 | 0 | 0 | 2620.004 | 0 | 0
September | 642426000000 | 409935.23 | 08-SEP-19:10 | 115409.094 | 92719.3 | 37736.353 | 0 | 104176.157 | 3472 | 4897.623 | 0 | 48888.791 | 0 | 0 | 0 | 2635.911 | 0 | 0
October | 585235000000 | 373675.503 | 02-OCT-19:10 | 115409.094 | 92719.3 | 37182.468 | 0 | 68224.465 | 3472 | 4652.671 | 0 | 48888.791 | 0 | 0 | 0 | 3126.714 | 0 | 0
November | 522182000000 | 334887.702 | 02-NOV-19:10 | 115409.094 | 92719.3 | 36615.562 | 0 | 32247.722 | 3472 | 2651.224 | 0 | 48888.791 | 0 | 0 | 0 | 2884.009 | 0 | 0
December | 508128000000 | 325801.362 | 13-DEC-20:00 | 115409.094 | 92719.3 | 36402.05 | 0 | 23336.043 | 3472 | 2750.419 | 0 | 48888.791 | 0 | 0 | 0 | 2823.665 | 0 | 0
Annual Sum or Average | 7020010000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 462913000000 | 325801.362 |  | 108704.857 | 91473.541 | 36402.05 | 0 | 23336.043 | 0 | 2098.754 | 0 | 48888.791 | 0 | 0 | 0 | 2333.268 | 0 | 0
Maximum of Months | 718704000000 | 456867.351 |  | 115409.094 | 92719.3 | 38504.789 | 0 | 152112.625 | 3472 | 6620.761 | 0 | 48888.791 | 0 | 0 | 0 | 3170.226 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 147918.07 | 50171.33 | 0 | 198089.4
Cost per Total Building Area ($/m2) | 13.04 | 4.42 | 0 | 17.46
Cost per Net Conditioned Building Area ($/m2) | 13.04 | 4.42 | 0 | 17.46

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 14908.78 | 1314.09 | 1314.09
Net Site Energy | 14908.78 | 1314.09 | 1314.09
Total Source Energy | 31346.7 | 2762.97 | 2762.97
Net Source Energy | 31346.7 | 2762.97 | 2762.97
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1341.91 | 0 | 0 | 0 | 0
Cooling | 940.39 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 54.59 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1123.98 | 0 | 0 | 0 | 0 | 0
Pumps | 85.47 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 5696.91 | 0 | 0 | 0 | 44332.9
Refrigeration | 73.78 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6631.3 | 8277.48 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 10.76 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 13.99 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 5.38 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 5.38 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 12.91 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 6.46 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 11.84 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 16.14 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 16.14 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 16.14 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 11.84 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 9.68 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 32.21 | 32.21 | 3.241 | 0.252 | 0.162 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.62 | 65.62 | 3.241 | 0.252 | 0.162 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.82 | 23.29 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.15 | 8.58 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.15 | 8.59 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.82 | 23.29 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.83 | 5.83 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.21 | 5.21 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 17.18 | 17.18 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 32.21 | 32.21 | 3.241 | 0.252 | 0.162 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.6 | 4.6 | 3.241 | 0.252 | 0.162 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 17.18 | 17.18 | 3.241 | 0.252 | 0.162 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.6 | 4.6 | 3.241 | 0.252 | 0.162 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 85.24 | 85.24 | 3.241 | 0.252 | 0.162 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 23.3 | 23.3 | 3.241 | 0.252 | 0.162 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 4.6 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.59 | 8.59 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 4.6 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.59 | 8.59 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 3.68 | 279.51 | 3.808 | 0.389 | 0.274 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 6.75 | 60.74 | 3.808 | 0.389 | 0.274 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 3.68 | 279.6 | 3.808 | 0.389 | 0.274 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 3.64 | 0.349 | 0.241
North Total or Average |  |  | 432.93 | 3.66 | 0.353 | 0.245
Non-North Total or Average |  |  | 781.15 | 3.63 | 0.346 | 0.239
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3112889.51 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 3077353.35 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 30110.92 | 20701.31 | 9409.61 | 0.69 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 8415.09 | 5818.2 | 2596.89 | 0.69 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 30041.22 | 20652.36 | 9388.86 | 0.69 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 8417.15 | 5819.68 | 2597.48 | 0.69 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 675084.69 | 418435.83 | 256648.86 | 0.62 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 38826.99 | 23959.44 | 14867.55 | 0.62 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 675084.69 | 418435.83 | 256648.86 | 0.62 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 24744.48 | 16979.6 | 7764.89 | 0.69 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 24986.35 | 17089.66 | 7896.69 | 0.68 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 78273.92 | 48552.3 | 29721.62 | 0.62 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 5215.17 | 3222.51 | 1992.66 | 0.62 | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 725377.54 | 476340.58 | 249036.97 | 0.66 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 36331 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 44638.34 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16651.06 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 3222.68 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 2263.44 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 10523.67 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 37363.28 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 15559.15 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 46490.79 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 83446.54 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 927.74 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4533.81 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5356 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 13235.82 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 3626.38 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 13243.79 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 3637.62 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 840547.16 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 47220.03 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 840547.16 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 12325.41 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 12955.91 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 596.01 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 51475.21 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 3370.4 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | 244774.83 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.27 | 25.25 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.29 | 822.34 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.37 | 232.52 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.29 | 820.35 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.37 | 232.59 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.15 | 733.52 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.06 | 673.46 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.06 | 675.76 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 35.93 | 59781.42 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 28525.32 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 16945.22 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 150631.7088 | 235.4735 | 484.7052 | 0 | 0.0019 | 861699.5959 | 61253.283
February | 134470.9388 | 212.2666 | 442.7829 | 0 | 0.0017 | 787199.7598 | 54871.5298
March | 141735.5987 | 230.7161 | 500.9297 | 0 | 0.0019 | 890670.9281 | 58480.7097
April | 136900.6345 | 228.4905 | 511.5126 | 0 | 0.0019 | 909559.5074 | 57007.0911
May | 143599.5673 | 245.8775 | 566.9661 | 0 | 0.0021 | 1008240 | 60369.777
June | 143976.9165 | 250.6343 | 588.6068 | 0 | 0.0022 | 1046770 | 60908.05
July | 154027.6678 | 270.9186 | 643.3636 | 0 | 0.0024 | 1144180 | 65417.4083
August | 151884.2275 | 266.9767 | 633.5684 | 0 | 0.0024 | 1126760 | 64491.1961
September | 143342.4306 | 249.9202 | 587.927 | 0 | 0.0022 | 1045570 | 60675.6968
October | 137762.5045 | 234.1255 | 535.3046 | 0 | 0.002 | 951916.148 | 57753.5448
November | 134489.1752 | 220.5418 | 483.2672 | 0 | 0.0018 | 859286.9842 | 55640.5454
December | 146233.5778 | 232.3209 | 488.8018 | 0 | 0.0019 | 869034.5377 | 59808.6192
Annual Sum or Average | 1719050 | 2878.2621 | 6467.7358 | 0 | 0.0245 | 11500900 | 716677.4511
Minimum of Months | 134470.9388 | 212.2666 | 442.7829 | 0 | 0.0017 | 787199.7598 | 54871.5298
Maximum of Months | 154027.6678 | 270.9186 | 643.3636 | 0 | 0.0024 | 1144180 | 65417.4083
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 496848000000 | 329275.483 | 24-JAN-20:00 | 115409.094 | 92719.3 | 36285.667 | 0 | 27589.799 | 3472 | 2597.933 | 0 | 48888.791 | 0 | 0 | 0 | 2312.899 | 0 | 0
February | 453892000000 | 313174.717 | 21-FEB-20:00 | 115409.094 | 92719.3 | 36285.667 | 0 | 12379.165 | 3472 | 1750.759 | 0 | 48888.791 | 0 | 0 | 0 | 2269.941 | 0 | 0
March | 513552000000 | 337950.715 | 28-MAR-19:10 | 115409.094 | 92719.3 | 36553.296 | 0 | 35277.831 | 3472 | 3216.924 | 0 | 48888.791 | 0 | 0 | 0 | 2413.479 | 0 | 0
April | 524443000000 | 353461.443 | 14-APR-19:10 | 115409.094 | 92719.3 | 36603.561 | 0 | 49764.535 | 3472 | 4137.216 | 0 | 48888.791 | 0 | 0 | 0 | 2466.946 | 0 | 0
May | 581342000000 | 384257.502 | 31-MAY-19:10 | 115409.094 | 92719.3 | 36817.514 | 0 | 82082.543 | 0 | 5260.144 | 0 | 48888.791 | 0 | 0 | 0 | 3080.116 | 0 | 0
June | 603558000000 | 403502.76 | 08-JUN-19:10 | 115409.094 | 92719.3 | 36908.844 | 0 | 100564.868 | 0 | 5875.94 | 0 | 48888.791 | 0 | 0 | 0 | 3135.923 | 0 | 0
July | 659723000000 | 416073.574 | 03-JUL-19:10 | 115409.094 | 92719.3 | 37297.174 | 0 | 112453.603 | 0 | 6102.32 | 0 | 48888.791 | 0 | 0 | 0 | 3203.292 | 0 | 0
August | 649678000000 | 400402.514 | 14-AUG-19:10 | 115409.094 | 92719.3 | 36961.523 | 0 | 97553.21 | 0 | 5732.712 | 0 | 48888.791 | 0 | 0 | 0 | 3137.884 | 0 | 0
September | 602863000000 | 381569.735 | 11-SEP-19:10 | 115409.094 | 92719.3 | 36725.636 | 0 | 76042.1 | 3472 | 5320.969 | 0 | 48888.791 | 0 | 0 | 0 | 2991.845 | 0 | 0
October | 548866000000 | 356821.656 | 20-OCT-19:10 | 115409.094 | 92719.3 | 36427.515 | 0 | 53883.698 | 3472 | 3601.286 | 0 | 48888.791 | 0 | 0 | 0 | 2419.973 | 0 | 0
November | 495457000000 | 326160.296 | 22-NOV-20:00 | 115409.094 | 92719.3 | 36303.416 | 0 | 24172.419 | 3472 | 2379.557 | 0 | 48888.791 | 0 | 0 | 0 | 2815.719 | 0 | 0
December | 501077000000 | 325669.418 | 04-DEC-20:00 | 115409.094 | 92719.3 | 36285.667 | 0 | 23711.19 | 3472 | 2406.519 | 0 | 48888.791 | 0 | 0 | 0 | 2776.857 | 0 | 0
Annual Sum or Average | 6631300000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 453892000000 | 313174.717 |  | 115409.094 | 92719.3 | 36285.667 | 0 | 12379.165 | 0 | 1750.759 | 0 | 48888.791 | 0 | 0 | 0 | 2269.941 | 0 | 0
Maximum of Months | 659723000000 | 416073.574 |  | 115409.094 | 92719.3 | 37297.174 | 0 | 112453.603 | 3472 | 6102.32 | 0 | 48888.791 | 0 | 0 | 0 | 3203.292 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 182224.42 | 88269.19 | 0 | 270493.6
Cost per Total Building Area ($/m2) | 16.06 | 7.78 | 0 | 23.84
Cost per Net Conditioned Building Area ($/m2) | 16.06 | 7.78 | 0 | 23.84

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 13474.07 | 1187.64 | 1187.64
Net Site Energy | 13474.07 | 1187.64 | 1187.64
Total Source Energy | 27346.18 | 2410.36 | 2410.36
Net Source Energy | 27346.18 | 2410.36 | 2410.36
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 418.97 | 0 | 0 | 0 | 0
Cooling | 650.95 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 54.55 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1105.88 | 0 | 0 | 0 | 0 | 0
Pumps | 68.38 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 5509.67 | 0 | 0 | 0 | 44332.9
Refrigeration | 73.95 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6306.78 | 7167.29 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 10.76 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 13.99 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 5.38 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 5.38 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 12.91 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 6.46 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 11.84 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 16.14 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 16.14 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 16.14 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 11.84 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 9.68 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 32.21 | 32.21 | 3.241 | 0.252 | 0.162 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.62 | 65.62 | 3.241 | 0.252 | 0.162 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.82 | 23.29 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.15 | 8.58 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.15 | 8.59 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.82 | 23.29 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.83 | 5.83 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.21 | 5.21 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 17.18 | 17.18 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 32.21 | 32.21 | 3.241 | 0.252 | 0.162 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.6 | 4.6 | 3.241 | 0.252 | 0.162 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 17.18 | 17.18 | 3.241 | 0.252 | 0.162 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.6 | 4.6 | 3.241 | 0.252 | 0.162 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 85.24 | 85.24 | 3.241 | 0.252 | 0.162 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 23.3 | 23.3 | 3.241 | 0.252 | 0.162 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 4.6 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.59 | 8.59 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 4.6 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.59 | 8.59 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 3.68 | 279.51 | 3.808 | 0.389 | 0.274 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 6.75 | 60.74 | 3.808 | 0.389 | 0.274 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 3.68 | 279.6 | 3.808 | 0.389 | 0.274 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 3.64 | 0.349 | 0.241
North Total or Average |  |  | 432.93 | 3.66 | 0.353 | 0.245
Non-North Total or Average |  |  | 781.15 | 3.63 | 0.346 | 0.239
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2133639.32 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 2196364.33 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 28982.93 | 20328.38 | 8654.55 | 0.7 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 8037.92 | 5660.06 | 2377.87 | 0.7 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 28213.54 | 19779.66 | 8433.89 | 0.7 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 7851.89 | 5527.62 | 2324.27 | 0.7 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 599146.61 | 391974.9 | 207171.71 | 0.65 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 31850.24 | 20817.23 | 11033 | 0.65 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 599146.61 | 391974.9 | 207171.71 | 0.65 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 23394.22 | 16379.03 | 7015.19 | 0.7 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 23021.42 | 16073.58 | 6947.85 | 0.7 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 68990.14 | 45258.79 | 23731.36 | 0.66 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 4685.99 | 3044.33 | 1641.65 | 0.65 | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 762622.75 | 520767.01 | 241855.74 | 0.68 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 35310.46 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 44647.98 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16079.03 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 3332.86 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 1574.7 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 4210 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 36387.29 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 15439.86 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 46177.55 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 82318.88 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 766.98 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4337.06 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5272.82 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 7159.97 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 2023.81 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 7151.3 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 2024.52 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 724970.81 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 40666.65 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 724970.81 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 6711.55 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 7044.28 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 616.38 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 28369.63 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 1857.54 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | 116498.92 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.1 | 9.61 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.17 | 742.83 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.33 | 207.86 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.13 | 722.36 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.32 | 202.94 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.15 | 730.08 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.94 | 597.63 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.92 | 584.51 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 34.15 | 56810.29 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 19551.85 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 12094.12 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 79282.7876 | 69.6663 | 414.0976 | 0 | 0.0003 | 2497520 | 28703.3017
February | 71486.5789 | 62.8128 | 373.9063 | 0 | 0.0002 | 2255120 | 25882.3986
March | 78499.1549 | 68.9435 | 416.1365 | 0 | 0.0003 | 2509850 | 28438.3057
April | 75218.8575 | 66.0182 | 406.6782 | 0 | 0.0002 | 2452850 | 27274.1324
May | 77353.7882 | 67.8264 | 429.9514 | 0 | 0.0003 | 2593290 | 28084.0409
June | 74433.1019 | 65.2157 | 422.6215 | 0 | 0.0003 | 2549130 | 27050.8234
July | 77811.4282 | 68.0962 | 456.0164 | 0 | 0.0003 | 2750630 | 28321.9543
August | 78478.795 | 68.661 | 463.3668 | 0 | 0.0003 | 2794990 | 28575.3569
September | 75667.8129 | 66.2289 | 441.8998 | 0 | 0.0003 | 2665480 | 27536.9761
October | 77749.7404 | 68.1128 | 443.028 | 0 | 0.0003 | 2672220 | 28260.977
November | 75155.9409 | 65.9287 | 412.4661 | 0 | 0.0003 | 2487800 | 27270.0155
December | 78886.8052 | 69.2765 | 419.526 | 0 | 0.0003 | 2530300 | 28582.8133
Annual Sum or Average | 920024.7916 | 806.787 | 5099.6945 | 0 | 0.0031 | 30759200 | 333981.0958
Minimum of Months | 71486.5789 | 62.8128 | 373.9063 | 0 | 0.0002 | 2255120 | 25882.3986
Maximum of Months | 79282.7876 | 69.6663 | 463.3668 | 0 | 0.0003 | 2794990 | 28703.3017
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 512085000000 | 329230.839 | 26-JAN-20:10 | 115409.094 | 92719.3 | 35778.656 | 0 | 27989.601 | 3472 | 2129.287 | 0 | 48888.791 | 0 | 0 | 0 | 2844.11 | 0 | 0
February | 462384000000 | 322284.277 | 13-FEB-20:00 | 115409.094 | 92719.3 | 35759.467 | 0 | 20826.3 | 3472 | 2434.186 | 0 | 48888.791 | 0 | 0 | 0 | 2775.139 | 0 | 0
March | 514614000000 | 322456.994 | 29-MAR-19:00 | 115409.094 | 92719.3 | 35818.052 | 0 | 21152.492 | 3472 | 2232.969 | 0 | 48888.791 | 0 | 0 | 0 | 2764.297 | 0 | 0
April | 502927000000 | 341074.182 | 11-APR-19:10 | 115409.094 | 92719.3 | 35971.323 | 0 | 39098.834 | 3472 | 3112.106 | 0 | 48888.791 | 0 | 0 | 0 | 2402.735 | 0 | 0
May | 531722000000 | 340652.594 | 30-MAY-19:10 | 115409.094 | 92719.3 | 36019.489 | 0 | 38771.807 | 3472 | 2974.085 | 0 | 48888.791 | 0 | 0 | 0 | 2398.028 | 0 | 0
June | 522667000000 | 339209.089 | 28-JUN-19:10 | 115409.094 | 92719.3 | 36006.223 | 0 | 36928.362 | 3472 | 2880.677 | 0 | 48888.791 | 0 | 0 | 0 | 2904.643 | 0 | 0
July | 563983000000 | 342477.272 | 28-JUL-19:00 | 115409.094 | 92719.3 | 35849.761 | 0 | 40700.903 | 3472 | 3012.711 | 0 | 48888.791 | 0 | 0 | 0 | 2424.712 | 0 | 0
August | 573078000000 | 352870.276 | 16-AUG-19:10 | 115409.094 | 92719.3 | 36041.338 | 0 | 49969.382 | 3472 | 3448.339 | 0 | 48888.791 | 0 | 0 | 0 | 2922.032 | 0 | 0
September | 546523000000 | 345237.015 | 25-SEP-19:10 | 115409.094 | 92719.3 | 36098.135 | 0 | 42526.686 | 3472 | 3186.139 | 0 | 48888.791 | 0 | 0 | 0 | 2936.87 | 0 | 0
October | 547906000000 | 338889.882 | 05-OCT-19:00 | 115409.094 | 92719.3 | 35927.868 | 0 | 36688.154 | 3472 | 2934.814 | 0 | 48888.791 | 0 | 0 | 0 | 2849.861 | 0 | 0
November | 510091000000 | 329893.915 | 09-NOV-20:00 | 115409.094 | 92719.3 | 35750.89 | 0 | 28215.153 | 3472 | 2621.48 | 0 | 48888.791 | 0 | 0 | 0 | 2817.208 | 0 | 0
December | 518807000000 | 330403.014 | 18-DEC-20:10 | 115409.094 | 92719.3 | 35734.359 | 0 | 28801.164 | 3472 | 2533.622 | 0 | 48888.791 | 0 | 0 | 0 | 2844.684 | 0 | 0
Annual Sum or Average | 6306780000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 462384000000 | 322284.277 |  | 115409.094 | 92719.3 | 35734.359 | 0 | 20826.3 | 3472 | 2129.287 | 0 | 48888.791 | 0 | 0 | 0 | 2398.028 | 0 | 0
Maximum of Months | 573078000000 | 352870.276 |  | 115409.094 | 92719.3 | 36098.135 | 0 | 49969.382 | 3472 | 3448.339 | 0 | 48888.791 | 0 | 0 | 0 | 2936.87 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 214025.48 | 60221.89 | 0 | 274247.37
Cost per Total Building Area ($/m2) | 18.86 | 5.31 | 0 | 24.17
Cost per Net Conditioned Building Area ($/m2) | 18.86 | 5.31 | 0 | 24.17

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 13562.78 | 1195.46 | 1195.46
Net Site Energy | 13562.78 | 1195.46 | 1195.46
Total Source Energy | 31484.03 | 2775.08 | 2775.08
Net Source Energy | 31484.03 | 2775.08 | 2775.08
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0.55 | 762.89 | 0 | 0 | 0 | 0
Cooling | 1009.48 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 54.54 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1138.01 | 0 | 0 | 0 | 0 | 0
Pumps | 79.13 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 4851.59 | 0 | 0 | 0 | 44332.9
Refrigeration | 74.86 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6709.65 | 6853.13 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 10.76 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 13.99 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 5.38 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 5.38 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 12.91 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 6.46 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 11.84 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 16.14 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 16.14 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 16.14 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 11.84 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 9.68 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 32.21 | 32.21 | 3.241 | 0.252 | 0.162 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.62 | 65.62 | 3.241 | 0.252 | 0.162 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.82 | 23.29 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.15 | 8.58 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.15 | 8.59 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.82 | 23.29 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.83 | 5.83 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.21 | 5.21 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 17.18 | 17.18 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 32.21 | 32.21 | 3.241 | 0.252 | 0.162 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.6 | 4.6 | 3.241 | 0.252 | 0.162 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 17.18 | 17.18 | 3.241 | 0.252 | 0.162 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.6 | 4.6 | 3.241 | 0.252 | 0.162 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 85.24 | 85.24 | 3.241 | 0.252 | 0.162 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 23.3 | 23.3 | 3.241 | 0.252 | 0.162 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 4.6 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.59 | 8.59 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 4.6 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.59 | 8.59 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 3.68 | 279.51 | 3.808 | 0.389 | 0.274 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 6.75 | 60.74 | 3.808 | 0.389 | 0.274 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 3.68 | 279.6 | 3.808 | 0.389 | 0.274 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 3.64 | 0.349 | 0.241
North Total or Average |  |  | 432.93 | 3.66 | 0.353 | 0.245
Non-North Total or Average |  |  | 781.15 | 3.63 | 0.346 | 0.239
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2123538.44 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 2591327.27 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 29344.11 | 20079.86 | 9264.25 | 0.68 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 8145.07 | 5590.6 | 2554.47 | 0.69 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 29157.24 | 19951.97 | 9205.27 | 0.68 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 8121.4 | 5574.76 | 2546.64 | 0.69 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 499372.21 | 316191.2 | 183181.01 | 0.63 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 35145.93 | 21840.01 | 13305.92 | 0.62 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 499372.21 | 316191.2 | 183181.01 | 0.63 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 23141.85 | 15816.31 | 7325.54 | 0.68 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 23211.27 | 15839.01 | 7372.26 | 0.68 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 51673.85 | 32897.62 | 18776.22 | 0.64 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 4016.08 | 2508.99 | 1507.09 | 0.62 | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 718777.26 | 474113.67 | 244663.59 | 0.66 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 36332.2 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 32654.44 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16721.76 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 3433.24 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 2372.24 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 7881.37 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 37380.46 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 16244.49 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 46450.35 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 82222.8 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 860.02 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4513.01 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5281.94 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 10548.7 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 2953.95 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 10557.8 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 2959.27 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 757424.29 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 43617.92 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 757424.29 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 9879.35 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 10380.91 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 571.63 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 40987.52 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 2683.71 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | 189884.68 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.21 | 19.92 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.39 | 887.95 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.39 | 248.01 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.39 | 882.4 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.39 | 247.35 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.26 | 802.63 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.1 | 701.15 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.1 | 701.36 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 35.91 | 59743.61 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 19459.29 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 14268.95 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 157639.0158 | 224.75 | 768.1172 | 0 | 0.0015 | 3829630 | 63046.5045
February | 138524.6393 | 200.8748 | 706.7176 | 0 | 0.0014 | 3523670 | 55752.8147
March | 151789.4109 | 221.2612 | 785.2114 | 0 | 0.0016 | 3915100 | 61211.2162
April | 147499.2977 | 220.6152 | 815.7263 | 0 | 0.0016 | 4067510 | 60064.0119
May | 153253.1211 | 232.6398 | 879.6793 | 0 | 0.0017 | 4386550 | 62762.3779
June | 159030.9867 | 245.495 | 951.2347 | 0 | 0.0018 | 4743530 | 65553.1315
July | 168578.2029 | 262.1098 | 1025.9815 | 0 | 0.002 | 5116350 | 69683.5989
August | 167352.6237 | 259.9115 | 1015.7716 | 0 | 0.0019 | 5065420 | 69146.5728
September | 154729.5057 | 238.0356 | 917.8054 | 0 | 0.0018 | 4576800 | 63694.8965
October | 149745.6615 | 226.3302 | 850.2862 | 0 | 0.0016 | 4239940 | 61223.5543
November | 143439.3135 | 211.5494 | 765.138 | 0 | 0.0015 | 3815120 | 58099.6053
December | 154337.477 | 222.2219 | 772.511 | 0 | 0.0015 | 3851640 | 61952.5596
Annual Sum or Average | 1845920 | 2765.7944 | 10254.1803 | 0 | 0.02 | 51131200 | 752190.8442
Minimum of Months | 138524.6393 | 200.8748 | 706.7176 | 0 | 0.0014 | 3523670 | 55752.8147
Maximum of Months | 168578.2029 | 262.1098 | 1025.9815 | 0 | 0.002 | 5116350 | 69683.5989
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 502539000000 | 312142.414 | 18-JAN-20:40 | 115409.094 | 92719.3 | 36562.713 | 0 | 10988.091 | 3472 | 1535.433 | 0 | 48888.791 | 0 | 0 | 0 | 2566.991 | 0 | 0
February | 462391000000 | 318512.222 | 27-FEB-20:10 | 115409.094 | 92719.3 | 36632.511 | 0 | 16895.088 | 3472 | 1799.42 | 0 | 48888.791 | 0 | 0 | 0 | 2696.017 | 0 | 0
March | 513755000000 | 329179.172 | 30-MAR-19:10 | 115409.094 | 92719.3 | 36799.994 | 0 | 26917.606 | 3472 | 2157.172 | 0 | 48888.791 | 0 | 0 | 0 | 2815.216 | 0 | 0
April | 533754000000 | 360798.928 | 21-APR-19:10 | 115409.094 | 92719.3 | 37202.37 | 0 | 56918.783 | 3472 | 3688.199 | 0 | 48888.791 | 0 | 0 | 0 | 2500.392 | 0 | 0
May | 575620000000 | 374488.204 | 31-MAY-19:10 | 115409.094 | 92719.3 | 37457.324 | 0 | 69935.051 | 3472 | 3461.21 | 0 | 48888.791 | 0 | 0 | 0 | 3145.434 | 0 | 0
June | 622465000000 | 423756.236 | 27-JUN-19:10 | 115409.094 | 92719.3 | 38101.87 | 0 | 117939.64 | 3472 | 4636.248 | 0 | 48888.791 | 0 | 0 | 0 | 2589.293 | 0 | 0
July | 671388000000 | 419882.074 | 24-JUL-19:10 | 115409.094 | 92719.3 | 37993.346 | 0 | 113702.304 | 3472 | 4498.723 | 0 | 48888.791 | 0 | 0 | 0 | 3198.516 | 0 | 0
August | 664705000000 | 407443.673 | 04-AUG-19:10 | 115409.094 | 92719.3 | 37913.457 | 0 | 101032.317 | 3472 | 5395.244 | 0 | 48888.791 | 0 | 0 | 0 | 2613.471 | 0 | 0
September | 600586000000 | 381691.245 | 01-SEP-19:00 | 115409.094 | 92719.3 | 37655.266 | 0 | 76910.303 | 3472 | 4049.33 | 0 | 48888.791 | 0 | 0 | 0 | 2587.162 | 0 | 0
October | 556382000000 | 353182.902 | 03-OCT-19:10 | 115409.094 | 92719.3 | 37113.026 | 0 | 49957.383 | 3472 | 3158.975 | 0 | 48888.791 | 0 | 0 | 0 | 2464.334 | 0 | 0
November | 500636000000 | 323741.558 | 09-NOV-20:10 | 115409.094 | 92719.3 | 36595.554 | 0 | 21519.57 | 3472 | 2372.473 | 0 | 48888.791 | 0 | 0 | 0 | 2764.776 | 0 | 0
December | 505428000000 | 317178.319 | 05-DEC-20:10 | 115409.094 | 92719.3 | 36562.713 | 0 | 16127.46 | 3472 | 1748.904 | 0 | 48888.791 | 0 | 0 | 0 | 2250.057 | 0 | 0
Annual Sum or Average | 6709650000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 462391000000 | 312142.414 |  | 115409.094 | 92719.3 | 36562.713 | 0 | 10988.091 | 3472 | 1535.433 | 0 | 48888.791 | 0 | 0 | 0 | 2250.057 | 0 | 0
Maximum of Months | 671388000000 | 423756.236 |  | 115409.094 | 92719.3 | 38101.87 | 0 | 117939.64 | 3472 | 5395.244 | 0 | 48888.791 | 0 | 0 | 0 | 3198.516 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 167430.63 | 55381.68 | 0 | 222812.31
Cost per Total Building Area ($/m2) | 14.76 | 4.88 | 0 | 19.64
Cost per Net Conditioned Building Area ($/m2) | 14.76 | 4.88 | 0 | 19.64

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 14498.37 | 1277.92 | 1277.92
Net Site Energy | 14498.37 | 1277.92 | 1277.92
Total Source Energy | 28072.86 | 2474.41 | 2474.41
Net Source Energy | 28072.86 | 2474.41 | 2474.41
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 814.69 | 0 | 0 | 0 | 0
Cooling | 420.33 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 54.57 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1152.94 | 0 | 0 | 0 | 0 | 0
Pumps | 58.14 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 6333.89 | 0 | 0 | 0 | 44332.9
Refrigeration | 72.09 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6111.15 | 8387.22 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 10.76 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 13.99 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 5.38 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 5.38 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 12.91 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 6.46 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 11.84 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 16.14 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 16.14 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 16.14 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 11.84 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 9.68 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.698 | 0.78 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.39 | 0.223 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.62 | 65.62 | 5.835 | 0.39 | 0.223 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.39 | 0.223 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.15 | 8.58 | 5.835 | 0.39 | 0.223 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.15 | 8.59 | 5.835 | 0.39 | 0.223 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.39 | 0.223 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.83 | 5.83 | 5.835 | 0.39 | 0.223 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.21 | 5.21 | 5.835 | 0.39 | 0.223 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.39 | 0.223 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.39 | 0.223 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.39 | 0.223 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.39 | 0.223 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.39 | 0.223 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 85.24 | 85.24 | 5.835 | 0.39 | 0.223 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 23.3 | 23.3 | 5.835 | 0.39 | 0.223 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 5.838 | 0.61 | 0.474 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 5.838 | 0.61 | 0.474 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 4.6 | 5.838 | 0.61 | 0.474 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.59 | 8.59 | 5.838 | 0.61 | 0.474 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 5.838 | 0.61 | 0.474 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 5.838 | 0.61 | 0.474 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 4.6 | 5.838 | 0.61 | 0.474 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.59 | 8.59 | 5.838 | 0.61 | 0.474 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 3.68 | 279.51 | 5.838 | 0.61 | 0.474 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 6.75 | 60.74 | 5.838 | 0.61 | 0.474 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 3.68 | 279.6 | 5.838 | 0.61 | 0.474 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 5.838 | 0.61 | 0.474 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 5.838 | 0.61 | 0.474 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 5.838 | 0.61 | 0.474 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 5.838 | 0.61 | 0.474 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 5.84 | 0.545 | 0.4
North Total or Average |  |  | 432.93 | 5.84 | 0.553 | 0.409
Non-North Total or Average |  |  | 781.15 | 5.84 | 0.541 | 0.395
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1555682.62 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 2428935.17 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 42021.2 | 29597.96 | 12423.24 | 0.7 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 11501.95 | 8111.56 | 3390.39 | 0.71 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 36184.9 | 25460.63 | 10724.27 | 0.7 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 10028.43 | 7068.69 | 2959.74 | 0.7 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 578349.13 | 385016.19 | 193332.94 | 0.67 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 64093.46 | 43692.31 | 20401.15 | 0.68 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 493229.57 | 344991.2 | 148238.36 | 0.7 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 33593.16 | 23622.26 | 9970.9 | 0.7 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 28011.59 | 19660.55 | 8351.04 | 0.7 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 54150.7 | 37488.2 | 16662.5 | 0.69 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 3819.52 | 2598.72 | 1220.8 | 0.68 | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 736467.29 | 513646.16 | 222821.13 | 0.7 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 33797.35 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 30913.69 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 24403.36 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 3894.51 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 2161.21 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 6518.85 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 34864.93 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 14769.64 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 45890.66 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 80732.93 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 617.81 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6691.97 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5063.79 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 10295.84 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 2817.39 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 10227.77 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 2803.04 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 767298.31 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 49311.96 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 767298.31 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 9686.58 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 10000.42 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 618.36 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 35365.36 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 2315.59 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | 146520.29 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.17 | 15.52 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.72 | 1092.07 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.47 | 299.78 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.47 | 938.17 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.41 | 261.09 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 2.41 | 1536.41 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.37 | 870.09 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.14 | 722.59 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 33.13 | 55109.59 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 14255.68 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 13374.75 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 87534.2756 | 77.1974 | 407.0133 | 0 | 0.0003 | 2454490 | 31537.5416
February | 76141.4035 | 67.0422 | 373.3185 | 0 | 0.0002 | 2251420 | 27491.6478
March | 84423.1207 | 74.3548 | 410.2339 | 0 | 0.0003 | 2474030 | 30470.5918
April | 79893.6524 | 70.2906 | 401.6368 | 0 | 0.0003 | 2422270 | 28876.7057
May | 80890.27 | 71.0942 | 419.7509 | 0 | 0.0003 | 2531600 | 29276.9021
June | 77252.7784 | 67.8474 | 409.786 | 0 | 0.0003 | 2471550 | 27987.5575
July | 79217.4776 | 69.5145 | 430.6523 | 0 | 0.0003 | 2597460 | 28731.2056
August | 79010.8182 | 69.3286 | 430.3539 | 0 | 0.0003 | 2595670 | 28658.7699
September | 77134.0636 | 67.6664 | 422.8837 | 0 | 0.0003 | 2550630 | 27986.4306
October | 80084.5546 | 70.3156 | 428.1653 | 0 | 0.0003 | 2582420 | 29023.7145
November | 78780.0446 | 69.2789 | 401.7503 | 0 | 0.0003 | 2422990 | 28491.6304
December | 86265.1968 | 76.049 | 406.3452 | 0 | 0.0003 | 2450500 | 31096.2731
Annual Sum or Average | 966627.6559 | 849.9796 | 4941.8901 | 0 | 0.0031 | 29805000 | 349628.9707
Minimum of Months | 76141.4035 | 67.0422 | 373.3185 | 0 | 0.0002 | 2251420 | 27491.6478
Maximum of Months | 87534.2756 | 77.1974 | 430.6523 | 0 | 0.0003 | 2597460 | 31537.5416
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 503263000000 | 312744.844 | 27-JAN-20:19 | 115409.094 | 92719.3 | 37413.114 | 0 | 10857.31 | 3472 | 1796.965 | 0 | 48888.791 | 0 | 0 | 0 | 2188.27 | 0 | 0
February | 461626000000 | 323958.341 | 15-FEB-20:10 | 115409.094 | 92719.3 | 37524.37 | 0 | 20815.013 | 3472 | 2352.581 | 0 | 48888.791 | 0 | 0 | 0 | 2777.193 | 0 | 0
March | 507269000000 | 314313.416 | 30-MAR-19:19 | 115409.094 | 92719.3 | 37456.652 | 0 | 11961.141 | 3472 | 1734.852 | 0 | 48888.791 | 0 | 0 | 0 | 2671.586 | 0 | 0
April | 496656000000 | 325019.576 | 13-APR-19:10 | 115409.094 | 92719.3 | 37717.954 | 0 | 21747.051 | 3472 | 2312.354 | 0 | 48888.791 | 0 | 0 | 0 | 2753.033 | 0 | 0
May | 519072000000 | 327451.811 | 25-MAY-19:19 | 115409.094 | 92719.3 | 37675.415 | 0 | 24093.254 | 3472 | 2374.827 | 0 | 48888.791 | 0 | 0 | 0 | 2819.129 | 0 | 0
June | 506761000000 | 331033.523 | 16-JUN-19:30 | 115409.094 | 92719.3 | 37843.752 | 0 | 27502.563 | 3472 | 2851.385 | 0 | 48888.791 | 0 | 0 | 0 | 2346.638 | 0 | 0
July | 532577000000 | 352475.332 | 02-JUL-19:30 | 108704.857 | 91473.541 | 37960.012 | 0 | 55247.056 | 3472 | 3679.312 | 0 | 48888.791 | 0 | 0 | 0 | 3049.763 | 0 | 0
August | 532209000000 | 328743.737 | 14-AUG-19:10 | 115409.094 | 92719.3 | 37760.307 | 0 | 25149.238 | 3472 | 2530.514 | 0 | 48888.791 | 0 | 0 | 0 | 2814.493 | 0 | 0
September | 522974000000 | 353075.375 | 28-SEP-19:00 | 115409.094 | 92719.3 | 37937.286 | 0 | 48439.79 | 3472 | 3185.166 | 0 | 48888.791 | 0 | 0 | 0 | 3023.948 | 0 | 0
October | 529493000000 | 334744.07 | 16-OCT-19:10 | 115409.094 | 92719.3 | 37611.145 | 0 | 30960.844 | 3472 | 2799.704 | 0 | 48888.791 | 0 | 0 | 0 | 2883.192 | 0 | 0
November | 496804000000 | 319248.144 | 15-NOV-20:00 | 115409.094 | 92719.3 | 37439.052 | 0 | 16502.812 | 3472 | 2072.121 | 0 | 48888.791 | 0 | 0 | 0 | 2744.975 | 0 | 0
December | 502444000000 | 312058.64 | 07-DEC-20:19 | 115409.094 | 92719.3 | 37413.114 | 0 | 9881.482 | 3472 | 1696.67 | 0 | 48888.791 | 0 | 0 | 0 | 2578.189 | 0 | 0
Annual Sum or Average | 6111150000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 461626000000 | 312058.64 |  | 108704.857 | 91473.541 | 37413.114 | 0 | 9881.482 | 3472 | 1696.67 | 0 | 48888.791 | 0 | 0 | 0 | 2188.27 | 0 | 0
Maximum of Months | 532577000000 | 353075.375 |  | 115409.094 | 92719.3 | 37960.012 | 0 | 55247.056 | 3472 | 3679.312 | 0 | 48888.791 | 0 | 0 | 0 | 3049.763 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 243705.12 | 70570.51 | 0 | 314275.63
Cost per Total Building Area ($/m2) | 21.48 | 6.22 | 0 | 27.7
Cost per Net Conditioned Building Area ($/m2) | 21.48 | 6.22 | 0 | 27.7

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 16390.47 | 1444.69 | 1444.69
Net Site Energy | 16390.47 | 1444.69 | 1444.69
Total Source Energy | 33882.56 | 2986.49 | 2986.49
Net Source Energy | 33882.56 | 2986.49 | 2986.49
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0.12 | 2263.01 | 0 | 0 | 0 | 0
Cooling | 765.25 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 54.54 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1112.29 | 0 | 0 | 0 | 0 | 0
Pumps | 77.46 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 6453.97 | 0 | 0 | 0 | 44332.9
Refrigeration | 72.13 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6434.85 | 9955.62 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 10.76 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 13.99 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 5.38 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 5.38 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 12.91 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 6.46 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 11.84 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 16.14 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 16.14 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 16.14 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 11.84 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 9.68 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 32.21 | 32.21 | 3.241 | 0.385 | 0.305 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.62 | 65.62 | 3.241 | 0.385 | 0.305 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.82 | 23.29 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.15 | 8.58 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.15 | 8.59 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.82 | 23.29 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.83 | 5.83 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.21 | 5.21 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 17.18 | 17.18 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 32.21 | 32.21 | 3.241 | 0.385 | 0.305 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.6 | 4.6 | 3.241 | 0.385 | 0.305 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 17.18 | 17.18 | 3.241 | 0.385 | 0.305 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.6 | 4.6 | 3.241 | 0.385 | 0.305 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 85.24 | 85.24 | 3.241 | 0.385 | 0.305 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 23.3 | 23.3 | 3.241 | 0.385 | 0.305 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 4.6 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.59 | 8.59 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 4.6 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.59 | 8.59 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 3.68 | 279.51 | 3.808 | 0.389 | 0.274 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 6.75 | 60.74 | 3.808 | 0.389 | 0.274 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 3.68 | 279.6 | 3.808 | 0.389 | 0.274 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 3.64 | 0.388 | 0.283
North Total or Average |  |  | 432.93 | 3.66 | 0.388 | 0.282
Non-North Total or Average |  |  | 781.15 | 3.63 | 0.388 | 0.284
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3166967.6 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 3412504.18 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 31818.41 | 22044.91 | 9773.5 | 0.69 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 8779.95 | 6116.82 | 2663.12 | 0.7 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 31490.7 | 21812.45 | 9678.24 | 0.69 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 8715.22 | 6070.82 | 2644.4 | 0.7 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 686556.49 | 433580.94 | 252975.55 | 0.63 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 39706.68 | 24938.88 | 14767.8 | 0.63 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 686556.49 | 433580.94 | 252975.55 | 0.63 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 25930.95 | 17949.91 | 7981.05 | 0.69 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 26060.81 | 17973.69 | 8087.11 | 0.69 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 79597.12 | 50305.89 | 29291.22 | 0.63 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 5329.97 | 3352.18 | 1977.8 | 0.63 | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 734525.24 | 490441.1 | 244084.13 | 0.67 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 36504.38 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 43706.63 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17068.25 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 3331.45 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 2560.07 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 12179.61 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 37580.91 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 16609.1 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 46471.65 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 83984.62 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 902.25 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4656.24 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5383.8 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 14264.15 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 3904.8 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 14252.27 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 3907.4 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 898860.19 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 50507.46 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 898860.19 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 13230.18 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 13941.69 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 615.29 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 58511.62 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 3831.12 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | 274867.8 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.3 | 27.95 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.25 | 798.42 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.35 | 223.15 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.24 | 789.74 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.35 | 221.43 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.15 | 733.86 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.02 | 649.92 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.02 | 647.78 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 35.01 | 58250.26 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 29020.87 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18790.7 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 151476.8814 | 227.6148 | 498.2361 | 0 | 0.0022 | 30965.871 | 60666.6648
February | 133935.02 | 203.0998 | 450.72 | 0 | 0.0019 | 28013.6889 | 53809.7495
March | 137473.0774 | 216.5845 | 507.4586 | 0 | 0.0022 | 31544.4378 | 55973.6215
April | 124455.6784 | 203.0288 | 497.7977 | 0 | 0.0021 | 30947.2353 | 51309.1991
May | 128232.2421 | 217.0882 | 556.5152 | 0 | 0.0023 | 34601.0914 | 53588.3725
June | 129839.9484 | 226.5884 | 600.9206 | 0 | 0.0025 | 37364.7381 | 54880.0435
July | 137568.738 | 243.5185 | 655.6972 | 0 | 0.0027 | 40772.0181 | 58461.5542
August | 136922.9615 | 242.7545 | 654.7129 | 0 | 0.0027 | 40710.9539 | 58221.7947
September | 122621.6382 | 213.5764 | 565.2213 | 0 | 0.0023 | 35144.831 | 51791.0966
October | 125817.248 | 212.3355 | 542.3666 | 0 | 0.0023 | 33721.1381 | 52518.4062
November | 127214.1774 | 205.8704 | 499.6738 | 0 | 0.0021 | 31063.1372 | 52294.797
December | 144828.5991 | 221.5943 | 498.2864 | 0 | 0.0021 | 30971.1289 | 58366.9775
Annual Sum or Average | 1600390 | 2633.6541 | 6527.6063 | 0 | 0.0274 | 405820.2698 | 661882.2772
Minimum of Months | 122621.6382 | 203.0288 | 450.72 | 0 | 0.0019 | 28013.6889 | 51309.1991
Maximum of Months | 151476.8814 | 243.5185 | 655.6972 | 0 | 0.0027 | 40772.0181 | 60666.6648
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 491007000000 | 308486.204 | 05-JAN-20:00 | 115409.094 | 92719.3 | 36031.744 | 0 | 7951.535 | 3472 | 1546.442 | 0 | 48888.791 | 0 | 0 | 0 | 2467.298 | 0 | 0
February | 444196000000 | 308957.719 | 15-FEB-20:30 | 115409.094 | 92719.3 | 36031.744 | 0 | 8433.843 | 3472 | 1459.31 | 0 | 48888.791 | 0 | 0 | 0 | 2543.636 | 0 | 0
March | 500181000000 | 333998.4 | 09-MAR-20:00 | 115409.094 | 92719.3 | 36046.055 | 0 | 31776.047 | 3472 | 2762.798 | 0 | 48888.791 | 0 | 0 | 0 | 2924.316 | 0 | 0
April | 490712000000 | 334399.514 | 05-APR-19:10 | 115409.094 | 92719.3 | 36218.43 | 0 | 31692.248 | 3472 | 3105.016 | 0 | 48888.791 | 0 | 0 | 0 | 2894.636 | 0 | 0
May | 548649000000 | 368144.943 | 15-MAY-19:10 | 115409.094 | 92719.3 | 36341.948 | 0 | 63651.553 | 3472 | 4685.175 | 0 | 48888.791 | 0 | 0 | 0 | 2977.083 | 0 | 0
June | 592470000000 | 406829.471 | 30-JUN-19:10 | 115409.094 | 92719.3 | 36744.931 | 0 | 104532.363 | 0 | 5968.839 | 0 | 48888.791 | 0 | 0 | 0 | 2566.154 | 0 | 0
July | 646498000000 | 428662.329 | 24-JUL-19:10 | 115409.094 | 92719.3 | 36698.583 | 0 | 124857.876 | 0 | 6941.406 | 0 | 48888.791 | 0 | 0 | 0 | 3147.28 | 0 | 0
August | 645529000000 | 428323.943 | 17-AUG-19:10 | 115409.094 | 92719.3 | 36700.265 | 0 | 121098.097 | 3472 | 6904.241 | 0 | 48888.791 | 0 | 0 | 0 | 3132.155 | 0 | 0
September | 557271000000 | 357317.801 | 27-SEP-19:10 | 115409.094 | 92719.3 | 36079.738 | 0 | 54239.568 | 3472 | 3593.631 | 0 | 48888.791 | 0 | 0 | 0 | 2915.679 | 0 | 0
October | 534696000000 | 361881.395 | 02-OCT-19:00 | 115409.094 | 92719.3 | 36062.61 | 0 | 58582.67 | 3472 | 3809.451 | 0 | 48888.791 | 0 | 0 | 0 | 2937.479 | 0 | 0
November | 492550000000 | 338279.715 | 03-NOV-19:10 | 115409.094 | 92719.3 | 36050.48 | 0 | 36459.199 | 3472 | 2899.837 | 0 | 48888.791 | 0 | 0 | 0 | 2381.015 | 0 | 0
December | 491091000000 | 307733.818 | 06-DEC-20:00 | 115409.094 | 92719.3 | 36031.744 | 0 | 7200.494 | 3472 | 1567.804 | 0 | 48888.791 | 0 | 0 | 0 | 2444.591 | 0 | 0
Annual Sum or Average | 6434850000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 444196000000 | 307733.818 |  | 115409.094 | 92719.3 | 36031.744 | 0 | 7200.494 | 0 | 1459.31 | 0 | 48888.791 | 0 | 0 | 0 | 2381.015 | 0 | 0
Maximum of Months | 646498000000 | 428662.329 |  | 115409.094 | 92719.3 | 36744.931 | 0 | 124857.876 | 3472 | 6941.406 | 0 | 48888.791 | 0 | 0 | 0 | 3147.28 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 123201.48 | 99808.32 | 0 | 223009.8
Cost per Total Building Area ($/m2) | 10.86 | 8.8 | 0 | 19.66
Cost per Net Conditioned Building Area ($/m2) | 10.86 | 8.8 | 0 | 19.66

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 15393.23 | 1356.8 | 1356.8
Net Site Energy | 15393.23 | 1356.8 | 1356.8
Total Source Energy | 30819.28 | 2716.48 | 2716.48
Net Source Energy | 30819.28 | 2716.48 | 2716.48
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0.01 | 1550.4 | 0 | 0 | 0 | 0
Cooling | 603.85 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 54.56 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1144.33 | 0 | 0 | 0 | 0 | 0
Pumps | 65.68 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 6310.44 | 0 | 0 | 0 | 44332.9
Refrigeration | 72.23 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6293.74 | 9099.49 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 10.76 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 13.99 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 5.38 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 5.38 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 12.91 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 6.46 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 11.84 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 16.14 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 16.14 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 16.14 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 11.84 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 9.68 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 32.21 | 32.21 | 3.241 | 0.385 | 0.305 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.62 | 65.62 | 3.241 | 0.385 | 0.305 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.82 | 23.29 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.15 | 8.58 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.15 | 8.59 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.82 | 23.29 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.83 | 5.83 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.21 | 5.21 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 17.18 | 17.18 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 32.21 | 32.21 | 3.241 | 0.385 | 0.305 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.6 | 4.6 | 3.241 | 0.385 | 0.305 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 17.18 | 17.18 | 3.241 | 0.385 | 0.305 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.6 | 4.6 | 3.241 | 0.385 | 0.305 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 85.24 | 85.24 | 3.241 | 0.385 | 0.305 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 23.3 | 23.3 | 3.241 | 0.385 | 0.305 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 4.6 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.59 | 8.59 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 4.6 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.59 | 8.59 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 3.68 | 279.51 | 3.808 | 0.389 | 0.274 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 6.75 | 60.74 | 3.808 | 0.389 | 0.274 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 3.68 | 279.6 | 3.808 | 0.389 | 0.274 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 3.64 | 0.388 | 0.283
North Total or Average |  |  | 432.93 | 3.66 | 0.388 | 0.282
Non-North Total or Average |  |  | 781.15 | 3.63 | 0.388 | 0.284
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1510573.99 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 2776681.15 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 23578.7 | 15284.29 | 8294.4 | 0.65 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 6625.93 | 4306.43 | 2319.5 | 0.65 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 23491.68 | 15227.22 | 8264.46 | 0.65 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 6621.58 | 4303.59 | 2317.98 | 0.65 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 364749.29 | 225820.75 | 138928.54 | 0.62 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 28198.97 | 16801.78 | 11397.19 | 0.6 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 364749.29 | 225820.75 | 138928.54 | 0.62 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 18394.09 | 11891.05 | 6503.04 | 0.65 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 18325.06 | 11827.42 | 6497.64 | 0.65 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 43411.35 | 26954.84 | 16456.51 | 0.62 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 3605.43 | 2161.78 | 1443.65 | 0.6 | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 772802.28 | 489148.67 | 283653.61 | 0.63 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 34428.73 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 36094.22 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15148.27 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 2752.47 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 2362.93 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 10704.11 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 35543.23 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 16329.04 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 46072.86 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 78563.04 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 727.47 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3962.99 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5038.95 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 12813.49 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 3550.68 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 12799.03 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 3554.71 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 730040.18 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 41381.37 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 730040.18 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 11908.22 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 12434.44 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 509.05 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 46044.69 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 3014.83 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | 240208.29 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.33 | 31.18 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.38 | 879.06 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.39 | 247.98 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.38 | 875.76 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.39 | 247.82 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.19 | 754.39 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.08 | 687.57 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.07 | 683.8 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 39.17 | 65168.8 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 13842.32 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 15289.59 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 188536.5125 | 282.7306 | 604.8109 | 0 | 0.0025 | 628606.4899 | 76199.0168
February | 167620.794 | 253.5183 | 549.3685 | 0 | 0.0022 | 571002.2241 | 67956.9049
March | 181943.5278 | 278.0495 | 611.8377 | 0 | 0.0025 | 635956.7008 | 74045.0282
April | 171925.8799 | 268.5258 | 609.4642 | 0 | 0.0025 | 633539.585 | 70535.6672
May | 179168.2646 | 285.3337 | 664.8861 | 0 | 0.0027 | 691195.6607 | 74046.1025
June | 176116.2054 | 284.0683 | 673.0187 | 0 | 0.0027 | 699678.1895 | 73137.402
July | 185952.5222 | 302.2945 | 723.3848 | 0 | 0.0029 | 752057.289 | 77453.7769
August | 182158.0899 | 295.9935 | 707.9064 | 0 | 0.0028 | 735964.3995 | 75860.3008
September | 171230.5074 | 276.5547 | 656.3342 | 0 | 0.0026 | 682335.5269 | 71144.463
October | 173537.2009 | 275.1548 | 637.4342 | 0 | 0.0026 | 662647.9997 | 71600.1145
November | 172625.4482 | 266.1344 | 593.0866 | 0 | 0.0024 | 616486.4505 | 70480.9262
December | 187334.0141 | 281.7148 | 605.2155 | 0 | 0.0025 | 629034.0342 | 75790.2542
Annual Sum or Average | 2138150 | 3350.0729 | 7636.7478 | 0 | 0.0307 | 7938500 | 878249.9572
Minimum of Months | 167620.794 | 253.5183 | 549.3685 | 0 | 0.0022 | 571002.2241 | 67956.9049
Maximum of Months | 188536.5125 | 302.2945 | 723.3848 | 0 | 0.0029 | 752057.289 | 77453.7769
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 498367000000 | 311922.894 | 26-JAN-20:19 | 115409.094 | 92719.3 | 36949.152 | 0 | 10397.507 | 3472 | 1535.35 | 0 | 48888.791 | 0 | 0 | 0 | 2551.701 | 0 | 0
February | 452697000000 | 313275.387 | 13-FEB-20:19 | 115409.094 | 92719.3 | 37000.187 | 0 | 11644.746 | 3472 | 1538.846 | 0 | 48888.791 | 0 | 0 | 0 | 2602.423 | 0 | 0
March | 504194000000 | 319657.658 | 20-MAR-19:10 | 115409.094 | 92719.3 | 37159.775 | 0 | 17465.589 | 3472 | 1831.811 | 0 | 48888.791 | 0 | 0 | 0 | 2711.298 | 0 | 0
April | 502278000000 | 336526.347 | 21-APR-19:10 | 115409.094 | 92719.3 | 37603.016 | 0 | 33672.849 | 3472 | 2389.157 | 0 | 48888.791 | 0 | 0 | 0 | 2372.141 | 0 | 0
May | 547988000000 | 350762.413 | 30-MAY-19:10 | 115409.094 | 92719.3 | 37746.493 | 0 | 46711.788 | 3472 | 3345.829 | 0 | 48888.791 | 0 | 0 | 0 | 2469.118 | 0 | 0
June | 554713000000 | 363156.615 | 28-JUN-19:19 | 115409.094 | 92719.3 | 38103.536 | 0 | 58425.908 | 3472 | 3044.906 | 0 | 48888.791 | 0 | 0 | 0 | 3093.081 | 0 | 0
July | 596240000000 | 372424.327 | 18-JUL-19:10 | 115409.094 | 92719.3 | 38186.243 | 0 | 70463.507 | 0 | 4161.294 | 0 | 48888.791 | 0 | 0 | 0 | 2596.098 | 0 | 0
August | 583481000000 | 369408.633 | 01-AUG-19:10 | 115409.094 | 92719.3 | 38154.84 | 415.577 | 63791.18 | 3472 | 4017.702 | 0 | 48888.791 | 0 | 0 | 0 | 2540.15 | 0 | 0
September | 540964000000 | 346269.388 | 13-SEP-19:10 | 115409.094 | 92719.3 | 37754.798 | 0 | 41914.195 | 3472 | 3120.642 | 0 | 48888.791 | 0 | 0 | 0 | 2990.567 | 0 | 0
October | 525355000000 | 338673.225 | 02-OCT-19:10 | 115409.094 | 92719.3 | 37462.695 | 0 | 34701.236 | 3472 | 3099.824 | 0 | 48888.791 | 0 | 0 | 0 | 2920.285 | 0 | 0
November | 488758000000 | 319781.523 | 09-NOV-20:00 | 115409.094 | 92719.3 | 37028.236 | 0 | 17702.263 | 3472 | 1829.998 | 0 | 48888.791 | 0 | 0 | 0 | 2731.841 | 0 | 0
December | 498706000000 | 310847.99 | 07-DEC-20:19 | 115409.094 | 92719.3 | 36949.152 | 0 | 9352.62 | 3472 | 1535.645 | 0 | 48888.791 | 0 | 0 | 0 | 2521.388 | 0 | 0
Annual Sum or Average | 6293740000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 452697000000 | 310847.99 |  | 115409.094 | 92719.3 | 36949.152 | 0 | 9352.62 | 0 | 1535.35 | 0 | 48888.791 | 0 | 0 | 0 | 2372.141 | 0 | 0
Maximum of Months | 596240000000 | 372424.327 |  | 115409.094 | 92719.3 | 38186.243 | 415.577 | 70463.507 | 3472 | 4161.294 | 0 | 48888.791 | 0 | 0 | 0 | 3093.081 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 64751.97 | 65218.96 | 0 | 129970.94
Cost per Total Building Area ($/m2) | 5.71 | 5.75 | 0 | 11.46
Cost per Net Conditioned Building Area ($/m2) | 5.71 | 5.75 | 0 | 11.46

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 16035 | 1413.36 | 1413.36
Net Site Energy | 16035 | 1413.36 | 1413.36
Total Source Energy | 21399.52 | 1886.2 | 1886.2
Net Source Energy | 21399.52 | 1886.2 | 1886.2
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1965.01 | 0 | 0 | 0 | 0
Cooling | 339.38 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 54.45 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1110.5 | 0 | 0 | 0 | 0 | 0
Pumps | 55.35 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 6847.79 | 0 | 0 | 0 | 44332.9
Refrigeration | 70.8 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5983.55 | 10051.44 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 10.76 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 13.99 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 5.38 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 5.38 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 12.91 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 6.46 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 11.84 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 16.14 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 16.14 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 16.14 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 11.84 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 9.68 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.591 | 0.648 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 32.21 | 32.21 | 3.241 | 0.385 | 0.305 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.62 | 65.62 | 3.241 | 0.385 | 0.305 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.82 | 23.29 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.15 | 8.58 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.15 | 8.59 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.82 | 23.29 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.83 | 5.83 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.21 | 5.21 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 17.18 | 17.18 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 32.21 | 32.21 | 3.241 | 0.385 | 0.305 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.6 | 4.6 | 3.241 | 0.385 | 0.305 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 17.18 | 17.18 | 3.241 | 0.385 | 0.305 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.6 | 4.6 | 3.241 | 0.385 | 0.305 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 85.24 | 85.24 | 3.241 | 0.385 | 0.305 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 23.3 | 23.3 | 3.241 | 0.385 | 0.305 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 4.6 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.59 | 8.59 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 4.6 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.59 | 8.59 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 3.68 | 279.51 | 3.808 | 0.389 | 0.274 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 6.75 | 60.74 | 3.808 | 0.389 | 0.274 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 3.68 | 279.6 | 3.808 | 0.389 | 0.274 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 3.64 | 0.388 | 0.283
North Total or Average |  |  | 432.93 | 3.66 | 0.388 | 0.282
Non-North Total or Average |  |  | 781.15 | 3.63 | 0.388 | 0.284
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1678985.85 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 2925322.66 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 29409.54 | 20556.27 | 8853.27 | 0.7 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 8054.08 | 5639.85 | 2414.23 | 0.7 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 27676.76 | 19334.01 | 8342.75 | 0.7 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 7630.03 | 5339.93 | 2290.1 | 0.7 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 587767.28 | 383499.85 | 204267.43 | 0.65 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 44797.31 | 29597.25 | 15200.06 | 0.66 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 508911.94 | 345522.77 | 163389.17 | 0.68 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 23962.05 | 16713.42 | 7248.64 | 0.7 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 22449.76 | 15643.33 | 6806.44 | 0.7 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 56548.53 | 38101.21 | 18447.32 | 0.67 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 3965 | 2631.59 | 1333.41 | 0.66 | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 751096.98 | 517802.43 | 233294.55 | 0.69 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 35182.42 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 35125.73 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 21077.06 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 3297.49 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 2085.93 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 9119.27 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 36282.34 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 15982.9 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 46148.3 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 81893.16 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 721.4 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5559.54 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5232.49 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 11563.82 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 3196.85 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 11500.06 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 3187.86 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 834899.41 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 51172.83 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 834899.41 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 10752.49 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 11245.87 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 609.84 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 48342.5 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 3165.28 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | 215920.1 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.23 | 21.07 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.23 | 784.39 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.34 | 215.72 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.16 | 737.25 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.32 | 204.12 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.62 | 1029.32 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1 | 636.65 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.94 | 595.43 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 34.15 | 56817.76 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 15385.58 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 16108.07 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 81301.0303 | 90.2942 | 105.6624 | 0 | 0.0005 | 1392770 | 29905.097
February | 69475.4257 | 78.0386 | 95.8998 | 0 | 0.0005 | 1264380 | 25649.3094
March | 75438.4105 | 85.1173 | 106.5623 | 0 | 0.0005 | 1405080 | 27891.5431
April | 67479.9575 | 77.4753 | 103.8604 | 0 | 0.0005 | 1369860 | 25092.3477
May | 64261.9237 | 75.5184 | 110.0029 | 0 | 0.0005 | 1451370 | 24081.8437
June | 59572.3457 | 71.0254 | 108.4753 | 0 | 0.0005 | 1431470 | 22433.4793
July | 60022.9793 | 72.5153 | 115.378 | 0 | 0.0005 | 1522790 | 22705.2006
August | 59579.5598 | 72.1935 | 115.8914 | 0 | 0.0005 | 1529610 | 22560.3764
September | 58636.6558 | 70.302 | 109.2753 | 0 | 0.0005 | 1442120 | 22123.1216
October | 64174.6389 | 75.1499 | 108.1554 | 0 | 0.0005 | 1426930 | 24020.6513
November | 71072.9216 | 80.5479 | 102.6698 | 0 | 0.0005 | 1353860 | 26315.6542
December | 80233.9027 | 89.3054 | 105.5292 | 0 | 0.0005 | 1391080 | 29533.6026
Annual Sum or Average | 811249.7515 | 937.4832 | 1287.3622 | 0 | 0.0061 | 16981300 | 302312.2268
Minimum of Months | 58636.6558 | 70.302 | 95.8998 | 0 | 0.0005 | 1264380 | 22123.1216
Maximum of Months | 81301.0303 | 90.2942 | 115.8914 | 0 | 0.0005 | 1529610 | 29905.097
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 490757000000 | 308113.128 | 02-JAN-20:00 | 115409.094 | 92719.3 | 36042.866 | 0 | 6855.213 | 3472 | 2304.114 | 0 | 48888.791 | 0 | 0 | 0 | 2421.75 | 0 | 0
February | 445517000000 | 312069.962 | 21-FEB-20:10 | 115409.094 | 92719.3 | 36042.866 | 0 | 11465.789 | 3472 | 1847.391 | 0 | 48888.791 | 0 | 0 | 0 | 2224.731 | 0 | 0
March | 495094000000 | 322657.773 | 29-MAR-19:10 | 115409.094 | 92719.3 | 36178.417 | 0 | 20600.356 | 3472 | 2614.086 | 0 | 48888.791 | 0 | 0 | 0 | 2775.729 | 0 | 0
April | 482686000000 | 319207.322 | 14-APR-19:10 | 115409.094 | 92719.3 | 36116.501 | 0 | 18457.151 | 3472 | 1849.978 | 0 | 48888.791 | 0 | 0 | 0 | 2294.508 | 0 | 0
May | 511405000000 | 334508.785 | 04-MAY-19:19 | 115409.094 | 92719.3 | 36390.766 | 0 | 31825.46 | 3472 | 2906.203 | 0 | 48888.791 | 0 | 0 | 0 | 2897.171 | 0 | 0
June | 504395000000 | 340354.882 | 27-JUN-19:10 | 115409.094 | 92719.3 | 36569.553 | 0 | 41230.472 | 0 | 3098.097 | 0 | 48888.791 | 0 | 0 | 0 | 2439.576 | 0 | 0
July | 536571000000 | 350677.928 | 24-JUL-19:10 | 115409.094 | 92719.3 | 36619.939 | 0 | 50381.643 | 0 | 3598.307 | 0 | 48888.791 | 0 | 0 | 0 | 3060.854 | 0 | 0
August | 538976000000 | 344260.756 | 18-AUG-19:19 | 115409.094 | 92719.3 | 36424.941 | 0 | 41587.671 | 3472 | 3317.715 | 0 | 48888.791 | 0 | 0 | 0 | 2441.244 | 0 | 0
September | 508148000000 | 359258.981 | 02-SEP-17:10 | 87035.739 | 86260.044 | 36673.258 | 0 | 81247.431 | 0 | 4434.503 | 0 | 61110.989 | 0 | 0 | 0 | 2497.018 | 0 | 0
October | 502793000000 | 323111.465 | 17-OCT-19:10 | 115409.094 | 92719.3 | 36101.615 | 0 | 21953.557 | 3472 | 2253.114 | 0 | 48888.791 | 0 | 0 | 0 | 2313.994 | 0 | 0
November | 477048000000 | 310987.031 | 03-NOV-19:00 | 115409.094 | 92719.3 | 36042.866 | 0 | 10511.042 | 3472 | 1678.527 | 0 | 48888.791 | 0 | 0 | 0 | 2265.411 | 0 | 0
December | 490161000000 | 307511.438 | 28-DEC-20:00 | 115409.094 | 92719.3 | 36042.866 | 0 | 6836.21 | 3472 | 1606.753 | 0 | 48888.791 | 0 | 0 | 0 | 2536.424 | 0 | 0
Annual Sum or Average | 5983550000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 445517000000 | 307511.438 |  | 87035.739 | 86260.044 | 36042.866 | 0 | 6836.21 | 0 | 1606.753 | 0 | 48888.791 | 0 | 0 | 0 | 2224.731 | 0 | 0
Maximum of Months | 538976000000 | 359258.981 |  | 115409.094 | 92719.3 | 36673.258 | 0 | 81247.431 | 3472 | 4434.503 | 0 | 61110.989 | 0 | 0 | 0 | 3060.854 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 118228.07 | 83435.21 | 0 | 201663.28
Cost per Total Building Area ($/m2) | 10.42 | 7.35 | 0 | 17.78
Cost per Net Conditioned Building Area ($/m2) | 10.42 | 7.35 | 0 | 17.78

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 17806.58 | 1569.51 | 1569.51
Net Site Energy | 17806.58 | 1569.51 | 1569.51
Total Source Energy | 34771.86 | 3064.87 | 3064.87
Net Source Energy | 34771.86 | 3064.87 | 3064.87
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0.67 | 3203.72 | 0 | 0 | 0 | 0
Cooling | 582 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 54.54 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1113.67 | 0 | 0 | 0 | 0 | 0
Pumps | 70.82 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 7118.45 | 0 | 0 | 0 | 44332.9
Refrigeration | 70.97 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6245.75 | 11560.83 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 10.76 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 13.99 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 5.38 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 5.38 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 12.91 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 6.46 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 11.84 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 16.14 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 16.14 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 16.14 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 11.84 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 9.68 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 32.21 | 32.21 | 3.241 | 0.385 | 0.305 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.62 | 65.62 | 3.241 | 0.385 | 0.305 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.82 | 23.29 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.15 | 8.58 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.15 | 8.59 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.82 | 23.29 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.83 | 5.83 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.21 | 5.21 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 17.18 | 17.18 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 32.21 | 32.21 | 3.241 | 0.385 | 0.305 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.6 | 4.6 | 3.241 | 0.385 | 0.305 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 17.18 | 17.18 | 3.241 | 0.385 | 0.305 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.6 | 4.6 | 3.241 | 0.385 | 0.305 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 85.24 | 85.24 | 3.241 | 0.385 | 0.305 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 23.3 | 23.3 | 3.241 | 0.385 | 0.305 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 4.6 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.59 | 8.59 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 4.6 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.59 | 8.59 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 3.68 | 279.51 | 3.808 | 0.389 | 0.274 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 6.75 | 60.74 | 3.808 | 0.389 | 0.274 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 3.68 | 279.6 | 3.808 | 0.389 | 0.274 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 3.64 | 0.388 | 0.283
North Total or Average |  |  | 432.93 | 3.66 | 0.388 | 0.282
Non-North Total or Average |  |  | 781.15 | 3.63 | 0.388 | 0.284
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3136138.02 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 4011374.01 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 30550.45 | 21222.63 | 9327.82 | 0.69 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 8361.59 | 5840.02 | 2521.57 | 0.7 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 30133.04 | 20925.74 | 9207.29 | 0.69 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 8275.5 | 5778.66 | 2496.83 | 0.7 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 677490.23 | 425361.55 | 252128.69 | 0.63 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 40763.52 | 25482.88 | 15280.65 | 0.63 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 677490.23 | 425361.55 | 252128.69 | 0.63 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 24729.32 | 17164.34 | 7564.98 | 0.69 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 24751.84 | 17114.3 | 7637.54 | 0.69 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 78548.85 | 49354.64 | 29194.21 | 0.63 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 5263.28 | 3290.07 | 1973.22 | 0.63 | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 664255.3 | 442229.35 | 222025.95 | 0.67 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 36465.17 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 42064.46 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17107.62 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 3340.33 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 3398.37 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 16185.31 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 37552.83 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 16807.24 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 46549.17 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 83632.29 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 884.74 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4631.63 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5343.02 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 17299.1 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 4778.88 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 17271.09 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 4778.8 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 952901.87 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 54448.27 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 952901.87 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 15970.35 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 16932.01 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 604.94 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 69468.24 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 4548.52 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | 339437.15 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.4 | 37.74 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.27 | 807.95 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.35 | 223.7 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.25 | 796.34 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.35 | 221.3 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.21 | 768.12 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.03 | 653.89 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.02 | 649.39 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 35.38 | 58861.37 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 28738.36 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 22088.33 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 247335.1591 | 377.184 | 916.284 | 0 | 0.0029 | 210844.0235 | 100200.6226
February | 219185.5219 | 336.8926 | 827.8055 | 0 | 0.0026 | 190489.4958 | 89048.6999
March | 234473.3453 | 366.3443 | 921.236 | 0 | 0.0029 | 212000.3568 | 95828.9612
April | 214252.0094 | 345.3075 | 905.0752 | 0 | 0.0028 | 208300.4287 | 88573.9139
May | 222054.4337 | 367.4491 | 995.3844 | 0 | 0.0031 | 229100.9254 | 92714.1804
June | 226815.0098 | 382.2119 | 1057.9987 | 0 | 0.0033 | 243523.3336 | 95360.1494
July | 243180.9101 | 413.4387 | 1156.209 | 0 | 0.0036 | 266134.3167 | 102589.6971
August | 237929.8372 | 404.5492 | 1131.4702 | 0 | 0.0035 | 260440.0308 | 100378.078
September | 215799.6624 | 363.8956 | 1008.0914 | 0 | 0.0031 | 232036.3747 | 90752.4733
October | 216091.8556 | 356.6189 | 962.8804 | 0 | 0.003 | 221618.1704 | 90132.5076
November | 218107.9829 | 347.6262 | 898.0092 | 0 | 0.0028 | 206667.6559 | 89795.5205
December | 241266.4721 | 371.4155 | 914.7005 | 0 | 0.0029 | 210486.3516 | 98075.3882
Annual Sum or Average | 2736490 | 4432.9335 | 11695.1446 | 0 | 0.0365 | 2691640 | 1133450
Minimum of Months | 214252.0094 | 336.8926 | 827.8055 | 0 | 0.0026 | 190489.4958 | 88573.9139
Maximum of Months | 247335.1591 | 413.4387 | 1156.209 | 0 | 0.0036 | 266134.3167 | 102589.6971
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 489248000000 | 308385.68 | 17-JAN-20:00 | 115409.094 | 92719.3 | 36157.825 | 0 | 7871.921 | 3472 | 1754.718 | 0 | 48888.791 | 0 | 0 | 0 | 2112.032 | 0 | 0
February | 442017000000 | 308047.923 | 27-FEB-20:00 | 115409.094 | 92719.3 | 36157.825 | 0 | 7424.489 | 3472 | 1452.101 | 0 | 48888.791 | 0 | 0 | 0 | 2524.322 | 0 | 0
March | 491931000000 | 321876.291 | 31-MAR-19:10 | 115409.094 | 92719.3 | 36157.973 | 0 | 20648.838 | 3472 | 2266.959 | 0 | 48888.791 | 0 | 0 | 0 | 2313.337 | 0 | 0
April | 483345000000 | 317233.326 | 28-APR-19:00 | 115409.094 | 92719.3 | 36272.567 | 0 | 16082.012 | 3472 | 2126.228 | 0 | 48888.791 | 0 | 0 | 0 | 2263.334 | 0 | 0
May | 531611000000 | 346375.439 | 30-MAY-19:19 | 115409.094 | 92719.3 | 36403.677 | 0 | 43056.529 | 3472 | 3977.509 | 0 | 48888.791 | 0 | 0 | 0 | 2448.539 | 0 | 0
June | 565078000000 | 380121.425 | 19-JUN-19:30 | 115409.094 | 92719.3 | 36432.241 | 0 | 74963.588 | 3472 | 5191.25 | 0 | 48888.791 | 0 | 0 | 0 | 3045.161 | 0 | 0
July | 617545000000 | 399903.367 | 14-JUL-19:30 | 115409.094 | 92719.3 | 36695.566 | 0 | 93990.708 | 3472 | 6203.255 | 0 | 48888.791 | 0 | 0 | 0 | 2524.654 | 0 | 0
August | 604331000000 | 418850.47 | 04-AUG-19:10 | 115409.094 | 92719.3 | 36708.661 | 0 | 111907.816 | 3472 | 7202.001 | 0 | 48888.791 | 0 | 0 | 0 | 2542.807 | 0 | 0
September | 538423000000 | 366876.282 | 06-SEP-19:10 | 115409.094 | 92719.3 | 36522.433 | 0 | 62659.183 | 3472 | 4245.841 | 0 | 48888.791 | 0 | 0 | 0 | 2959.641 | 0 | 0
October | 514248000000 | 338879.76 | 30-OCT-19:10 | 115409.094 | 92719.3 | 36175.383 | 0 | 36414.344 | 3472 | 2930.848 | 0 | 48888.791 | 0 | 0 | 0 | 2870 | 0 | 0
November | 479557000000 | 336107.576 | 02-NOV-19:00 | 115409.094 | 92719.3 | 36193 | 0 | 33677.098 | 3472 | 2820.069 | 0 | 48888.791 | 0 | 0 | 0 | 2928.224 | 0 | 0
December | 488418000000 | 308583.053 | 11-DEC-20:00 | 115409.094 | 92719.3 | 36157.825 | 0 | 7949.407 | 3472 | 1458.835 | 0 | 48888.791 | 0 | 0 | 0 | 2527.801 | 0 | 0
Annual Sum or Average | 6245750000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 442017000000 | 308047.923 |  | 115409.094 | 92719.3 | 36157.825 | 0 | 7424.489 | 3472 | 1452.101 | 0 | 48888.791 | 0 | 0 | 0 | 2112.032 | 0 | 0
Maximum of Months | 617545000000 | 418850.47 |  | 115409.094 | 92719.3 | 36708.661 | 0 | 111907.816 | 3472 | 7202.001 | 0 | 48888.791 | 0 | 0 | 0 | 3045.161 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 168063.24 | 102093.37 | 0 | 270156.61
Cost per Total Building Area ($/m2) | 14.81 | 9 | 0 | 23.81
Cost per Net Conditioned Building Area ($/m2) | 14.81 | 9 | 0 | 23.81

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 16814.93 | 1482.11 | 1482.11
Net Site Energy | 16814.93 | 1482.11 | 1482.11
Total Source Energy | 32054.19 | 2825.33 | 2825.33
Net Source Energy | 32054.19 | 2825.33 | 2825.33
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0.52 | 2341.42 | 0 | 0 | 0 | 0
Cooling | 474.39 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 54.51 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1136.35 | 0 | 0 | 0 | 0 | 0
Pumps | 61.29 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 7083.79 | 0 | 0 | 0 | 44332.9
Refrigeration | 70.93 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6151.07 | 10663.86 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 10.76 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 13.99 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 5.38 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 5.38 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 12.91 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 6.46 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 11.84 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 16.14 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 16.14 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 16.14 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 11.84 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 9.68 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 32.21 | 32.21 | 3.241 | 0.385 | 0.305 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.62 | 65.62 | 3.241 | 0.385 | 0.305 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.82 | 23.29 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.15 | 8.58 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.15 | 8.59 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.82 | 23.29 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.83 | 5.83 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.21 | 5.21 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 17.18 | 17.18 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 32.21 | 32.21 | 3.241 | 0.385 | 0.305 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.6 | 4.6 | 3.241 | 0.385 | 0.305 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 17.18 | 17.18 | 3.241 | 0.385 | 0.305 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.6 | 4.6 | 3.241 | 0.385 | 0.305 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 85.24 | 85.24 | 3.241 | 0.385 | 0.305 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 23.3 | 23.3 | 3.241 | 0.385 | 0.305 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 4.6 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.59 | 8.59 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 4.6 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.59 | 8.59 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 3.68 | 279.51 | 3.808 | 0.389 | 0.274 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 6.75 | 60.74 | 3.808 | 0.389 | 0.274 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 3.68 | 279.6 | 3.808 | 0.389 | 0.274 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 3.64 | 0.388 | 0.283
North Total or Average |  |  | 432.93 | 3.66 | 0.388 | 0.282
Non-North Total or Average |  |  | 781.15 | 3.63 | 0.388 | 0.284
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1499326.83 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 3324500.13 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 23330.92 | 14913.73 | 8417.19 | 0.64 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 6482.46 | 4154.96 | 2327.5 | 0.64 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 23046.54 | 14729.64 | 8316.9 | 0.64 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 6423.87 | 4117.02 | 2306.85 | 0.64 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 474406.98 | 288058.67 | 186348.31 | 0.61 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 28638.2 | 16837.03 | 11801.17 | 0.59 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 474406.98 | 288058.67 | 186348.31 | 0.61 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 17948.6 | 11447.03 | 6501.57 | 0.64 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 17729.26 | 11284.83 | 6444.43 | 0.64 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 54526.07 | 33234.89 | 21291.19 | 0.61 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 3571.12 | 2113.38 | 1457.74 | 0.59 | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 761046.68 | 475657.84 | 285388.83 | 0.63 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 34070.37 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 35673.07 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14974.22 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 2747.4 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 3191.45 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 14537.45 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 35197.88 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 16326 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 46158 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 78148.43 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 708.89 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3855.04 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4974.11 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 15538.13 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 4343.62 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 15540.37 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 4348.36 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 789447.48 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 45037.11 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 789447.48 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 14351.05 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 15118.48 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 508.11 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 56417.29 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 3693.99 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | 301762.06 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.45 | 42.2 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.36 | 865.86 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.38 | 241.5 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.34 | 855.13 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.38 | 239.29 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.2 | 765.53 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.05 | 669.64 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.04 | 660.09 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 38.95 | 64803.38 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 13739.26 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18306.11 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 196698.1974 | 289.704 | 602.4912 | 0 | 0.0025 | 626147.9423 | 78981.1176
February | 175630.6116 | 259.8471 | 544.3053 | 0 | 0.0022 | 565688.4293 | 70636.7355
March | 189804.1853 | 284.3194 | 607.1876 | 0 | 0.0025 | 631073.8684 | 76680.7344
April | 176529.6444 | 270.5523 | 597.8338 | 0 | 0.0024 | 621407.4629 | 71917.905
May | 179364.5448 | 279.8046 | 633.9965 | 0 | 0.0026 | 659038.1392 | 73554.2163
June | 173942.3676 | 275.8644 | 639.2862 | 0 | 0.0026 | 664573.8099 | 71773.8757
July | 185773.1456 | 298.3226 | 702.7672 | 0 | 0.0028 | 730595.0102 | 77018.0601
August | 180805.1707 | 290.1825 | 683.0953 | 0 | 0.0027 | 710142.9388 | 74942.5126
September | 171429.4433 | 272.8657 | 635.3907 | 0 | 0.0025 | 660532.0735 | 70833.7473
October | 177676.0249 | 277.4296 | 629.4302 | 0 | 0.0025 | 654293.6544 | 72887.1947
November | 178788.541 | 270.6273 | 587.1519 | 0 | 0.0024 | 610275.4142 | 72505.9534
December | 195488.5771 | 288.3633 | 601.1725 | 0 | 0.0025 | 624781.6306 | 78538.6612
Annual Sum or Average | 2181930 | 3357.8828 | 7464.1085 | 0 | 0.0302 | 7758550 | 890270.7137
Minimum of Months | 171429.4433 | 259.8471 | 544.3053 | 0 | 0.0022 | 565688.4293 | 70636.7355
Maximum of Months | 196698.1974 | 298.3226 | 702.7672 | 0 | 0.0028 | 730595.0102 | 78981.1176
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 496418000000 | 310899.758 | 23-JAN-20:10 | 115409.094 | 92719.3 | 36860.94 | 0 | 9511.596 | 3472 | 1470.216 | 0 | 48888.791 | 0 | 0 | 0 | 2567.82 | 0 | 0
February | 448485000000 | 310773.635 | 10-FEB-20:00 | 115409.094 | 92719.3 | 36860.94 | 0 | 9770.17 | 3472 | 1504.816 | 0 | 48888.791 | 0 | 0 | 0 | 2148.525 | 0 | 0
March | 500323000000 | 322713.244 | 30-MAR-19:10 | 115409.094 | 92719.3 | 37235.878 | 0 | 20345.976 | 3472 | 1894.574 | 0 | 48888.791 | 0 | 0 | 0 | 2747.632 | 0 | 0
April | 492659000000 | 332842.245 | 26-APR-19:10 | 115409.094 | 92719.3 | 37315.1 | 0 | 29583.086 | 3472 | 2609.296 | 0 | 48888.791 | 0 | 0 | 0 | 2845.579 | 0 | 0
May | 522493000000 | 345454.664 | 23-MAY-19:19 | 115409.094 | 92719.3 | 37654.552 | 0 | 41646.642 | 3472 | 3219.025 | 0 | 48888.791 | 0 | 0 | 0 | 2445.26 | 0 | 0
June | 526882000000 | 350497.232 | 27-JUN-19:10 | 115409.094 | 92719.3 | 37857.924 | 0 | 49904.046 | 0 | 3228.419 | 0 | 48888.791 | 0 | 0 | 0 | 2489.658 | 0 | 0
July | 579225000000 | 363930.612 | 10-JUL-19:10 | 115409.094 | 92719.3 | 37978.355 | 0 | 62342.209 | 0 | 3474.714 | 0 | 48888.791 | 0 | 0 | 0 | 3118.149 | 0 | 0
August | 563010000000 | 355193.562 | 29-AUG-19:10 | 115409.094 | 92719.3 | 37857.433 | 0 | 50235.672 | 3472 | 4106.438 | 0 | 48888.791 | 0 | 0 | 0 | 2504.834 | 0 | 0
September | 523678000000 | 346347.515 | 01-SEP-19:10 | 115409.094 | 92719.3 | 37597.027 | 0 | 42682.847 | 3472 | 3126.867 | 0 | 48888.791 | 0 | 0 | 0 | 2451.59 | 0 | 0
October | 518732000000 | 325804.01 | 05-OCT-19:10 | 115409.094 | 92719.3 | 37351.39 | 0 | 23158.222 | 3472 | 2026.543 | 0 | 48888.791 | 0 | 0 | 0 | 2778.67 | 0 | 0
November | 483834000000 | 312345.039 | 01-NOV-19:40 | 115409.094 | 92719.3 | 36860.94 | 0 | 10884.436 | 3472 | 1561.207 | 0 | 48888.791 | 0 | 0 | 0 | 2549.271 | 0 | 0
December | 495334000000 | 309832.728 | 21-DEC-20:19 | 115409.094 | 92719.3 | 36860.94 | 0 | 8464.573 | 3472 | 1514.33 | 0 | 48888.791 | 0 | 0 | 0 | 2503.7 | 0 | 0
Annual Sum or Average | 6151070000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 448485000000 | 309832.728 |  | 115409.094 | 92719.3 | 36860.94 | 0 | 8464.573 | 0 | 1470.216 | 0 | 48888.791 | 0 | 0 | 0 | 2148.525 | 0 | 0
Maximum of Months | 579225000000 | 363930.612 |  | 115409.094 | 92719.3 | 37978.355 | 0 | 62342.209 | 3472 | 4106.438 | 0 | 48888.791 | 0 | 0 | 0 | 3118.149 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 63288.51 | 76419.5 | 0 | 139708.01
Cost per Total Building Area ($/m2) | 5.58 | 6.74 | 0 | 12.31
Cost per Net Conditioned Building Area ($/m2) | 5.58 | 6.74 | 0 | 12.31

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 19303.99 | 1701.5 | 1701.5
Net Site Energy | 19303.99 | 1701.5 | 1701.5
Total Source Energy | 35626.8 | 3140.23 | 3140.23
Net Source Energy | 35626.8 | 3140.23 | 3140.23
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 3.25 | 4169.37 | 0 | 0 | 0 | 0
Cooling | 535.1 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 54.51 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1115.63 | 0 | 0 | 0 | 0 | 0
Pumps | 71.37 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 7692.62 | 0 | 0 | 0 | 44332.9
Refrigeration | 70.41 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6203.34 | 13100.65 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 10.76 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 13.99 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 5.38 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 5.38 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 12.91 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 6.46 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 11.84 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 16.14 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 16.14 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 16.14 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 11.84 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 9.68 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 32.21 | 32.21 | 3.241 | 0.385 | 0.305 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.62 | 65.62 | 3.241 | 0.385 | 0.305 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.82 | 23.29 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.15 | 8.58 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.15 | 8.59 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.82 | 23.29 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.83 | 5.83 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.21 | 5.21 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 17.18 | 17.18 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 32.21 | 32.21 | 3.241 | 0.385 | 0.305 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.6 | 4.6 | 3.241 | 0.385 | 0.305 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 17.18 | 17.18 | 3.241 | 0.385 | 0.305 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.6 | 4.6 | 3.241 | 0.385 | 0.305 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 85.24 | 85.24 | 3.241 | 0.385 | 0.305 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 23.3 | 23.3 | 3.241 | 0.385 | 0.305 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 4.6 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.59 | 8.59 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 4.6 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.59 | 8.59 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 3.68 | 279.51 | 3.808 | 0.389 | 0.274 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 6.75 | 60.74 | 3.808 | 0.389 | 0.274 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 3.68 | 279.6 | 3.808 | 0.389 | 0.274 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 3.64 | 0.388 | 0.283
North Total or Average |  |  | 432.93 | 3.66 | 0.388 | 0.282
Non-North Total or Average |  |  | 781.15 | 3.63 | 0.388 | 0.284
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3103411.87 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 4344714.7 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 30212.41 | 20697.58 | 9514.83 | 0.69 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 8194.84 | 5640.91 | 2553.92 | 0.69 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 29609.71 | 20275.71 | 9334 | 0.68 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 8059.01 | 5546.13 | 2512.88 | 0.69 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 690165.47 | 426199.41 | 263966.05 | 0.62 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 43068.88 | 26693.18 | 16375.71 | 0.62 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 670916.42 | 416855.26 | 254061.16 | 0.62 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 24698.5 | 16901.46 | 7797.04 | 0.68 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 24620.78 | 16788.93 | 7831.85 | 0.68 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 78859.61 | 48886.21 | 29973.4 | 0.62 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 5219.23 | 3227.99 | 1991.24 | 0.62 | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 681175.11 | 447448.11 | 233727 | 0.66 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 36363 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 41406.91 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16941.71 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 3411.34 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 3892.12 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 18506.8 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 37443.7 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 16595.9 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 46615.03 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 83358.89 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 879.92 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4544.91 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5310.28 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 18862.03 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 5232.94 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 18825.05 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 5236.22 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 978860.92 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 57483.77 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 978860.92 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 17488.34 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 18545.34 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 600.28 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 74682.8 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 4889.94 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | 373643 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.47 | 43.56 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.27 | 809.39 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.35 | 221.79 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.24 | 792.47 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.34 | 218.02 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.3 | 826.25 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.04 | 660.94 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.03 | 654.14 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 35.46 | 58998.15 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 28438.47 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 23923.85 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 205047.9407 | 284.5038 | 321.2886 | 0 | 0.0025 | 210866.8904 | 80371.322
February | 178167.5783 | 250.531 | 289.9923 | 0 | 0.0023 | 190350.0395 | 70152.8988
March | 179757.4321 | 262.0378 | 322.7688 | 0 | 0.0025 | 211927.2096 | 71665.1075
April | 159310.5302 | 242.5384 | 319.6149 | 0 | 0.0024 | 209919.7334 | 64498.584
May | 161775.306 | 255.3703 | 354.124 | 0 | 0.0027 | 232634.8224 | 66364.3481
June | 159593.9482 | 257.8875 | 368.7576 | 0 | 0.0028 | 242278.1521 | 66039.2519
July | 167258.4549 | 273.5299 | 397.0738 | 0 | 0.003 | 260897.7326 | 69522.1512
August | 164448.2557 | 269.441 | 392.0524 | 0 | 0.0029 | 257600.81 | 68402.5122
September | 147971.512 | 238.7106 | 340.6126 | 0 | 0.0026 | 223784.6276 | 61192.0641
October | 156322.9814 | 243.3828 | 331.1806 | 0 | 0.0025 | 217545.5781 | 63804.5095
November | 167424.7983 | 247.7094 | 312.507 | 0 | 0.0024 | 205211.8442 | 67097.1906
December | 195237.7032 | 275.3553 | 320.4499 | 0 | 0.0025 | 210347.878 | 76952.6902
Annual Sum or Average | 2042320 | 3100.9977 | 4070.4225 | 0 | 0.0311 | 2673370 | 826062.6302
Minimum of Months | 147971.512 | 238.7106 | 289.9923 | 0 | 0.0023 | 190350.0395 | 61192.0641
Maximum of Months | 205047.9407 | 284.5038 | 397.0738 | 0 | 0.003 | 260897.7326 | 80371.322
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 489301000000 | 306960.687 | 30-JAN-20:00 | 115409.094 | 92719.3 | 36242.666 | 0 | 6262.957 | 3472 | 1520.959 | 0 | 48888.791 | 0 | 0 | 0 | 2444.921 | 0 | 0
February | 441693000000 | 307202.463 | 27-FEB-20:00 | 115409.094 | 92719.3 | 36242.666 | 0 | 6521.328 | 3472 | 1477.422 | 0 | 48888.791 | 0 | 0 | 0 | 2471.863 | 0 | 0
March | 491761000000 | 311470.59 | 28-MAR-19:00 | 115409.094 | 92719.3 | 36242.666 | 0 | 10545.062 | 3472 | 1953.769 | 0 | 48888.791 | 0 | 0 | 0 | 2239.908 | 0 | 0
April | 487103000000 | 328295.646 | 02-APR-19:49 | 108704.857 | 91473.541 | 36242.666 | 0 | 33849.67 | 3472 | 2830.886 | 0 | 48888.791 | 0 | 0 | 0 | 2833.235 | 0 | 0
May | 539812000000 | 382893.553 | 27-MAY-17:10 | 87035.739 | 86260.044 | 36868.797 | 0 | 103354.611 | 0 | 5765.773 | 0 | 61110.989 | 0 | 0 | 0 | 2497.599 | 0 | 0
June | 562188000000 | 396784.76 | 29-JUN-19:10 | 115409.094 | 92719.3 | 36952.175 | 0 | 93775.561 | 0 | 5926.989 | 0 | 48888.791 | 0 | 0 | 0 | 3112.851 | 0 | 0
July | 605394000000 | 411548.527 | 13-JUL-19:10 | 115409.094 | 92719.3 | 36722.97 | 0 | 108169.211 | 0 | 6501.324 | 0 | 48888.791 | 0 | 0 | 0 | 3137.838 | 0 | 0
August | 597743000000 | 407487.238 | 25-AUG-19:10 | 115409.094 | 92719.3 | 36764.538 | 0 | 101231.162 | 3472 | 6473.347 | 0 | 48888.791 | 0 | 0 | 0 | 2529.005 | 0 | 0
September | 519275000000 | 352511.974 | 13-SEP-19:10 | 115409.094 | 92719.3 | 36473.018 | 0 | 48407.724 | 3472 | 4162.806 | 0 | 48888.791 | 0 | 0 | 0 | 2979.242 | 0 | 0
October | 504798000000 | 326839.213 | 08-OCT-19:10 | 108704.857 | 91473.541 | 36278.886 | 0 | 32402.712 | 3472 | 2776.303 | 0 | 48888.791 | 0 | 0 | 0 | 2842.122 | 0 | 0
November | 476179000000 | 312128.586 | 02-NOV-19:10 | 115409.094 | 92719.3 | 36242.666 | 0 | 10942.851 | 3472 | 1805.872 | 0 | 48888.791 | 0 | 0 | 0 | 2648.012 | 0 | 0
December | 488096000000 | 306744.008 | 01-DEC-20:00 | 115409.094 | 92719.3 | 36242.666 | 0 | 6441.122 | 3472 | 1554.78 | 0 | 48888.791 | 0 | 0 | 0 | 2016.256 | 0 | 0
Annual Sum or Average | 6203340000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 441693000000 | 306744.008 |  | 87035.739 | 86260.044 | 36242.666 | 0 | 6262.957 | 0 | 1477.422 | 0 | 48888.791 | 0 | 0 | 0 | 2016.256 | 0 | 0
Maximum of Months | 605394000000 | 411548.527 |  | 115409.094 | 92719.3 | 36952.175 | 0 | 108169.211 | 3472 | 6501.324 | 0 | 61110.989 | 0 | 0 | 0 | 3137.838 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 93643.33 | 104345.85 | 0 | 197989.18
Cost per Total Building Area ($/m2) | 8.25 | 9.2 | 0 | 17.45
Cost per Net Conditioned Building Area ($/m2) | 8.25 | 9.2 | 0 | 17.45

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 18553.06 | 1635.31 | 1635.31
Net Site Energy | 18553.06 | 1635.31 | 1635.31
Total Source Energy | 34648.11 | 3053.96 | 3053.96
Net Source Energy | 34648.11 | 3053.96 | 3053.96
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 2.37 | 3482.22 | 0 | 0 | 0 | 0
Cooling | 366.69 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 54.5 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1129.22 | 0 | 0 | 0 | 0 | 0
Pumps | 59.69 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 7796.88 | 0 | 0 | 0 | 44332.9
Refrigeration | 69.75 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6035.31 | 12517.75 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 10.76 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 13.99 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 5.38 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 5.38 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 12.91 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 6.46 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 11.84 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 16.14 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 16.14 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 16.14 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 11.84 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 9.68 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.511 | 0.553 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 32.21 | 32.21 | 3.241 | 0.385 | 0.305 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.62 | 65.62 | 3.241 | 0.385 | 0.305 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.82 | 23.29 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.15 | 8.58 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.15 | 8.59 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.82 | 23.29 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.83 | 5.83 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.21 | 5.21 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 17.18 | 17.18 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 32.21 | 32.21 | 3.241 | 0.385 | 0.305 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.6 | 4.6 | 3.241 | 0.385 | 0.305 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 17.18 | 17.18 | 3.241 | 0.385 | 0.305 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.6 | 4.6 | 3.241 | 0.385 | 0.305 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 85.24 | 85.24 | 3.241 | 0.385 | 0.305 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 23.3 | 23.3 | 3.241 | 0.385 | 0.305 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 4.6 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.59 | 8.59 | 3.808 | 0.389 | 0.274 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 4.6 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.59 | 8.59 | 3.808 | 0.389 | 0.274 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 3.68 | 279.51 | 3.808 | 0.389 | 0.274 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 6.75 | 60.74 | 3.808 | 0.389 | 0.274 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 3.68 | 279.6 | 3.808 | 0.389 | 0.274 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.389 | 0.274 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.389 | 0.274 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 3.64 | 0.388 | 0.283
North Total or Average |  |  | 432.93 | 3.66 | 0.388 | 0.282
Non-North Total or Average |  |  | 781.15 | 3.63 | 0.388 | 0.284
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1407222.73 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 4007253.12 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 24785.69 | 16368.28 | 8417.41 | 0.66 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 6840.19 | 4524.44 | 2315.76 | 0.66 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 24102.26 | 15914.61 | 8187.65 | 0.66 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 6677.61 | 4416.96 | 2260.65 | 0.66 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 457489.59 | 283139.7 | 174349.89 | 0.62 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 30555.78 | 19052.66 | 11503.12 | 0.62 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 317500.98 | 207223.1 | 110277.88 | 0.65 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 19639.5 | 12935.11 | 6704.39 | 0.66 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 19192.72 | 12632.71 | 6560.01 | 0.66 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 41762.71 | 26639.82 | 15122.89 | 0.64 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 3082.52 | 1934.11 | 1148.41 | 0.63 | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 596988.99 | 386295.56 | 210693.43 | 0.65 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 34333.02 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 35177.68 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17286.45 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 3159.17 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 4001.18 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 18471.87 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 35446.55 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 16108.97 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 46317.52 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 79199.89 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 739.23 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3955.09 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5041.41 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 18271.53 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 5142.09 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 18200.59 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 5131.15 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 881855.12 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 53129.91 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 881855.12 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 16980.41 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 17887.72 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 536.56 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 67921.02 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 4447.21 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | 360112.29 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.54 | 50.1 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.33 | 847.27 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.37 | 234.48 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.29 | 823.93 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.36 | 229 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.4 | 889.22 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.05 | 670.77 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.03 | 655.36 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 37.41 | 62233.82 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 12895.25 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 22065.64 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 200159.5492 | 282.1597 | 364.2744 | 0 | 0.0027 | 8631510 | 78987.6991
February | 176260.3946 | 250.997 | 329.9197 | 0 | 0.0024 | 7818090 | 69800.8226
March | 181581.4667 | 266.6397 | 369.0483 | 0 | 0.0027 | 8747220 | 72687.6559
April | 168068.5902 | 251.3218 | 357.9483 | 0 | 0.0026 | 8485110 | 67715.7872
May | 167029.2757 | 256.1051 | 378.6543 | 0 | 0.0027 | 8977260 | 67909.6465
June | 161716.1302 | 253.2674 | 385.8093 | 0 | 0.0028 | 9147930 | 66262.6457
July | 168276.5806 | 267.2633 | 414.9191 | 0 | 0.003 | 9838840 | 69310.494
August | 164851.3803 | 261.7944 | 406.3691 | 0 | 0.0029 | 9636090 | 67896.9141
September | 157331.763 | 247.2894 | 378.5625 | 0 | 0.0027 | 8976270 | 64552.0487
October | 165788.0501 | 253.92 | 374.821 | 0 | 0.0027 | 8886320 | 67377.7469
November | 171468.5407 | 253.6116 | 355.0841 | 0 | 0.0026 | 8416640 | 68815.5454
December | 194578.7746 | 277.1167 | 364.3309 | 0 | 0.0027 | 8633540 | 77058.3756
Annual Sum or Average | 2077110 | 3121.4863 | 4479.7411 | 0 | 0.0324 | 106195000 | 838375.3816
Minimum of Months | 157331.763 | 247.2894 | 329.9197 | 0 | 0.0024 | 7818090 | 64552.0487
Maximum of Months | 200159.5492 | 282.1597 | 414.9191 | 0 | 0.003 | 9838840 | 78987.6991
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 490549000000 | 308135.717 | 30-JAN-20:00 | 115409.094 | 92719.3 | 36708.75 | 0 | 6927.868 | 3472 | 1587.114 | 0 | 48888.791 | 0 | 0 | 0 | 2422.799 | 0 | 0
February | 444321000000 | 310251.502 | 03-FEB-20:40 | 115409.094 | 92719.3 | 36708.75 | 0 | 9430.32 | 3472 | 1469.998 | 0 | 48888.791 | 0 | 0 | 0 | 2153.249 | 0 | 0
March | 497125000000 | 319360.855 | 30-MAR-19:10 | 115409.094 | 92719.3 | 36814.121 | 0 | 17505.77 | 3472 | 1831.722 | 0 | 48888.791 | 0 | 0 | 0 | 2720.056 | 0 | 0
April | 482229000000 | 322033.977 | 06-APR-19:10 | 115409.094 | 92719.3 | 36801.363 | 0 | 20050.115 | 3472 | 1934.037 | 0 | 48888.791 | 0 | 0 | 0 | 2759.277 | 0 | 0
May | 510199000000 | 331472.58 | 25-MAY-19:10 | 115409.094 | 92719.3 | 37179.195 | 0 | 31639.72 | 0 | 2741.735 | 0 | 48888.791 | 0 | 0 | 0 | 2894.746 | 0 | 0
June | 519899000000 | 361256.959 | 29-JUN-19:10 | 115409.094 | 92719.3 | 37561.684 | 0 | 59952.665 | 0 | 3602.795 | 0 | 48888.791 | 0 | 0 | 0 | 3122.63 | 0 | 0
July | 559165000000 | 361563.34 | 21-JUL-19:10 | 115409.094 | 92719.3 | 37712.267 | 0 | 60571.621 | 0 | 3726.806 | 0 | 48888.791 | 0 | 0 | 0 | 2535.461 | 0 | 0
August | 547642000000 | 353758.522 | 11-AUG-19:10 | 115409.094 | 92719.3 | 37450.902 | 0 | 52044.751 | 0 | 4731.276 | 0 | 48888.791 | 0 | 0 | 0 | 2514.408 | 0 | 0
September | 510143000000 | 346424.77 | 01-SEP-19:10 | 115409.094 | 92719.3 | 37271.826 | 0 | 42887.015 | 3472 | 3321.213 | 0 | 48888.791 | 0 | 0 | 0 | 2455.532 | 0 | 0
October | 505031000000 | 325903.035 | 05-OCT-19:10 | 115409.094 | 92719.3 | 36825.057 | 0 | 23346.005 | 3472 | 2436.436 | 0 | 48888.791 | 0 | 0 | 0 | 2806.353 | 0 | 0
November | 478338000000 | 310231.884 | 20-NOV-20:00 | 115409.094 | 92719.3 | 36708.75 | 0 | 9019.047 | 3472 | 1415.95 | 0 | 48888.791 | 0 | 0 | 0 | 2598.951 | 0 | 0
December | 490665000000 | 307892.601 | 01-DEC-20:00 | 115409.094 | 92719.3 | 36708.75 | 0 | 7116.025 | 3472 | 1523.602 | 0 | 48888.791 | 0 | 0 | 0 | 2055.039 | 0 | 0
Annual Sum or Average | 6035310000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 444321000000 | 307892.601 |  | 115409.094 | 92719.3 | 36708.75 | 0 | 6927.868 | 0 | 1415.95 | 0 | 48888.791 | 0 | 0 | 0 | 2055.039 | 0 | 0
Maximum of Months | 559165000000 | 361563.34 |  | 115409.094 | 92719.3 | 37712.267 | 0 | 60571.621 | 3472 | 4731.276 | 0 | 48888.791 | 0 | 0 | 0 | 3122.63 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 118219.49 | 108503.75 | 0 | 226723.24
Cost per Total Building Area ($/m2) | 10.42 | 9.56 | 0 | 19.98
Cost per Net Conditioned Building Area ($/m2) | 10.42 | 9.56 | 0 | 19.98

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 20969.83 | 1848.33 | 1848.33
Net Site Energy | 20969.83 | 1848.33 | 1848.33
Total Source Energy | 36988.92 | 3260.29 | 3260.29
Net Source Energy | 36988.92 | 3260.29 | 3260.29
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 5.09 | 5083.06 | 0 | 0 | 0 | 0
Cooling | 337.21 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 54.47 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1127.67 | 0 | 0 | 0 | 0 | 0
Pumps | 62.17 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 8639.65 | 0 | 0 | 0 | 44332.9
Refrigeration | 68.8 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6008.47 | 14961.36 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 10.76 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 13.99 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 5.38 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 5.38 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 12.91 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 6.46 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 11.84 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 16.14 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 16.14 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 16.14 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 11.84 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 9.68 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.454 | 0.487 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.454 | 0.487 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.454 | 0.487 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.454 | 0.487 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.454 | 0.487 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.454 | 0.487 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.454 | 0.487 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.454 | 0.487 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.454 | 0.487 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.454 | 0.487 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.454 | 0.487 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.454 | 0.487 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.454 | 0.487 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.454 | 0.487 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.454 | 0.487 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.454 | 0.487 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.454 | 0.487 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.454 | 0.487 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.454 | 0.487 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.454 | 0.487 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.454 | 0.487 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.454 | 0.487 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.454 | 0.487 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.454 | 0.487 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.454 | 0.487 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.454 | 0.487 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.454 | 0.487 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 32.21 | 32.21 | 3.241 | 0.487 | 0.409 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.62 | 65.62 | 3.241 | 0.487 | 0.409 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.82 | 23.29 | 3.241 | 0.487 | 0.409 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.15 | 8.58 | 3.241 | 0.487 | 0.409 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.15 | 8.59 | 3.241 | 0.487 | 0.409 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.82 | 23.29 | 3.241 | 0.487 | 0.409 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.83 | 5.83 | 3.241 | 0.487 | 0.409 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.21 | 5.21 | 3.241 | 0.487 | 0.409 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 17.18 | 17.18 | 3.241 | 0.487 | 0.409 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 32.21 | 32.21 | 3.241 | 0.487 | 0.409 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.6 | 4.6 | 3.241 | 0.487 | 0.409 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 17.18 | 17.18 | 3.241 | 0.487 | 0.409 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.6 | 4.6 | 3.241 | 0.487 | 0.409 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 85.24 | 85.24 | 3.241 | 0.487 | 0.409 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 23.3 | 23.3 | 3.241 | 0.487 | 0.409 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.49 | 0.378 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.49 | 0.378 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 4.6 | 3.808 | 0.49 | 0.378 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.59 | 8.59 | 3.808 | 0.49 | 0.378 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.49 | 0.378 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.49 | 0.378 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 4.6 | 3.808 | 0.49 | 0.378 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.59 | 8.59 | 3.808 | 0.49 | 0.378 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 3.68 | 279.51 | 3.808 | 0.49 | 0.378 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 6.75 | 60.74 | 3.808 | 0.49 | 0.378 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 3.68 | 279.6 | 3.808 | 0.49 | 0.378 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.49 | 0.378 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.49 | 0.378 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 3.808 | 0.49 | 0.378 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 3.808 | 0.49 | 0.378 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 3.64 | 0.489 | 0.387
North Total or Average |  |  | 432.93 | 3.66 | 0.489 | 0.386
Non-North Total or Average |  |  | 781.15 | 3.63 | 0.489 | 0.388
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2427234.01 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 4447748 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 31367.29 | 21659.5 | 9707.79 | 0.69 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 8618.07 | 5973.78 | 2644.29 | 0.69 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 30409.4 | 20985.84 | 9423.56 | 0.69 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 8397.67 | 5819.11 | 2578.57 | 0.69 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 643048.34 | 399508.21 | 243540.14 | 0.62 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 34281.16 | 21966.94 | 12314.22 | 0.64 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 611116.3 | 384501.26 | 226615.05 | 0.63 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 25403.24 | 17520.03 | 7883.21 | 0.69 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 24874.15 | 17103.11 | 7771.04 | 0.69 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 72497.18 | 45387.38 | 27109.8 | 0.63 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 4842.9 | 3016.98 | 1825.92 | 0.62 | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 654868.48 | 435810.47 | 219058.01 | 0.67 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 35405.07 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 33924.49 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19929.43 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 3758.83 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 4170.28 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 19713 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 36534.49 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 16934.87 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 46470.72 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 81526.14 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 772.4 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5149.72 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5165.24 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 19652.51 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 5499.16 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 19584.28 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 5498.57 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 975135.2 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 60573.83 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 975135.2 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 18165.34 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 19269.87 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 587.74 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 76011.74 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 4976.96 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | 382922.3 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.51 | 47.67 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.41 | 900.25 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.39 | 249.2 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.37 | 871.87 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.38 | 242.69 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.53 | 974.29 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.14 | 728.76 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.12 | 709.78 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 35.31 | 58751.38 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 22242.24 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 24491.19 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 209044.3982 | 288.3947 | 322.1643 | 0 | 0.0026 | 211429.9771 | 81779.6684
February | 184901.134 | 257.0694 | 291.4115 | 0 | 0.0023 | 191261.6948 | 72524.142
March | 192145.6043 | 273.3436 | 323.0244 | 0 | 0.0025 | 212053.5734 | 75958.5027
April | 169833.4078 | 250.6056 | 314.8298 | 0 | 0.0024 | 206733.1594 | 67998.6741
May | 163996.9027 | 250.5628 | 331.9138 | 0 | 0.0025 | 218002.422 | 66480.9536
June | 155874.8315 | 245.0189 | 337.8306 | 0 | 0.0026 | 221926.0147 | 63844.6815
July | 165470.053 | 264.4935 | 372.9272 | 0 | 0.0028 | 245003.7997 | 68194.5861
August | 160662.9984 | 256.1015 | 359.7873 | 0 | 0.0027 | 236367.7906 | 66145.7787
September | 152240.9107 | 238.3502 | 326.84 | 0 | 0.0025 | 214701.2116 | 62264.8291
October | 164119.2474 | 249.5921 | 328.392 | 0 | 0.0025 | 215682.9838 | 66419.8963
November | 175879.5375 | 255.3539 | 312.4486 | 0 | 0.0024 | 205144.7455 | 70020.5315
December | 202374.9375 | 282.1751 | 321.5943 | 0 | 0.0025 | 211077.244 | 79455.527
Annual Sum or Average | 2096540 | 3111.0612 | 3943.1638 | 0 | 0.0304 | 2589380 | 841087.771
Minimum of Months | 152240.9107 | 238.3502 | 291.4115 | 0 | 0.0023 | 191261.6948 | 62264.8291
Maximum of Months | 209044.3982 | 288.3947 | 372.9272 | 0 | 0.0028 | 245003.7997 | 81779.6684
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 490607000000 | 307106.007 | 09-JAN-20:10 | 115409.094 | 92719.3 | 36770.062 | 1284.319 | 1780.09 | 3472 | 4427.785 | 0 | 48888.791 | 0 | 0 | 0 | 2354.566 | 0 | 0
February | 443808000000 | 308790.282 | 22-FEB-20:00 | 115409.094 | 92719.3 | 36722.396 | 0 | 7560.794 | 3472 | 1585.568 | 0 | 48888.791 | 0 | 0 | 0 | 2432.34 | 0 | 0
March | 492054000000 | 309751.843 | 22-MAR-19:10 | 115409.094 | 92719.3 | 36722.396 | 0 | 8510.182 | 3472 | 1573.427 | 0 | 48888.791 | 0 | 0 | 0 | 2456.654 | 0 | 0
April | 479709000000 | 313534.529 | 04-APR-19:10 | 115409.094 | 92719.3 | 36722.396 | 0 | 12504.742 | 3472 | 1593.508 | 0 | 48888.791 | 0 | 0 | 0 | 2224.699 | 0 | 0
May | 505858000000 | 329648.423 | 31-MAY-19:10 | 115409.094 | 92719.3 | 37143.554 | 0 | 29990.023 | 0 | 2660.234 | 0 | 48888.791 | 0 | 0 | 0 | 2837.427 | 0 | 0
June | 514963000000 | 367107.26 | 14-JUN-19:10 | 115409.094 | 92719.3 | 37201.372 | 0 | 65343.678 | 0 | 4488.19 | 0 | 48888.791 | 0 | 0 | 0 | 3056.836 | 0 | 0
July | 568513000000 | 384029.732 | 06-JUL-19:10 | 115409.094 | 92719.3 | 37451.901 | 0 | 81362.719 | 0 | 5083.85 | 0 | 48888.791 | 0 | 0 | 0 | 3114.077 | 0 | 0
August | 548474000000 | 374568.568 | 13-AUG-19:19 | 108704.857 | 91473.541 | 37101.048 | 0 | 76960.001 | 3472 | 4927.649 | 0 | 48888.791 | 0 | 0 | 0 | 3040.681 | 0 | 0
September | 498198000000 | 351124.057 | 08-SEP-19:10 | 115409.094 | 92719.3 | 36897.282 | 0 | 47953.454 | 3472 | 3376.32 | 0 | 48888.791 | 0 | 0 | 0 | 2407.816 | 0 | 0
October | 500476000000 | 315492.458 | 06-OCT-19:10 | 115409.094 | 92719.3 | 36722.396 | 0 | 14020.935 | 3472 | 2009.063 | 0 | 48888.791 | 0 | 0 | 0 | 2250.88 | 0 | 0
November | 476023000000 | 310868.81 | 02-NOV-19:00 | 115409.094 | 92719.3 | 36722.396 | 0 | 9303.489 | 3472 | 1810.348 | 0 | 48888.791 | 0 | 0 | 0 | 2543.393 | 0 | 0
December | 489789000000 | 306687.946 | 01-DEC-20:00 | 115409.094 | 92719.3 | 36722.396 | 0 | 5910.964 | 3472 | 1554.033 | 0 | 48888.791 | 0 | 0 | 0 | 2011.369 | 0 | 0
Annual Sum or Average | 6008470000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 443808000000 | 306687.946 |  | 108704.857 | 91473.541 | 36722.396 | 0 | 1780.09 | 0 | 1554.033 | 0 | 48888.791 | 0 | 0 | 0 | 2011.369 | 0 | 0
Maximum of Months | 568513000000 | 384029.732 |  | 115409.094 | 92719.3 | 37451.901 | 1284.319 | 81362.719 | 3472 | 5083.85 | 0 | 48888.791 | 0 | 0 | 0 | 3114.077 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 90160.88 | 119126.16 | 0 | 209287.04
Cost per Total Building Area ($/m2) | 7.95 | 10.5 | 0 | 18.45
Cost per Net Conditioned Building Area ($/m2) | 7.95 | 10.5 | 0 | 18.45

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 25207.79 | 2221.87 | 2221.87
Net Site Energy | 25207.79 | 2221.87 | 2221.87
Total Source Energy | 42522.49 | 3748.03 | 3748.03
Net Source Energy | 42522.49 | 3748.03 | 3748.03
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 11.07 | 8136.52 | 0 | 0 | 0 | 0
Cooling | 305.71 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 54.13 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1187.18 | 0 | 0 | 0 | 0 | 0
Pumps | 67.91 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 9786.01 | 0 | 0 | 0 | 44332.9
Refrigeration | 67.52 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6046.61 | 19161.18 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 10.76 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 13.99 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 5.38 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 5.38 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 12.91 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 6.46 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 11.84 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 16.14 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 16.14 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 16.14 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 11.84 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 9.68 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.269 | 0.283 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.269 | 0.283 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.269 | 0.283 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.269 | 0.283 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.269 | 0.283 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.269 | 0.283 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.269 | 0.283 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.269 | 0.283 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.269 | 0.283 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.269 | 0.283 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.269 | 0.283 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 32.21 | 32.21 | 2.615 | 0.702 | 0.633 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.62 | 65.62 | 2.615 | 0.702 | 0.633 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.82 | 23.29 | 2.615 | 0.702 | 0.633 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.15 | 8.58 | 2.615 | 0.702 | 0.633 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.15 | 8.59 | 2.615 | 0.702 | 0.633 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.82 | 23.29 | 2.615 | 0.702 | 0.633 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.83 | 5.83 | 2.615 | 0.702 | 0.633 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 5.21 | 5.21 | 2.615 | 0.702 | 0.633 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 17.18 | 17.18 | 2.615 | 0.702 | 0.633 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 32.21 | 32.21 | 2.615 | 0.702 | 0.633 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.6 | 4.6 | 2.615 | 0.702 | 0.633 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 17.18 | 17.18 | 2.615 | 0.702 | 0.633 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.6 | 4.6 | 2.615 | 0.702 | 0.633 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 85.24 | 85.24 | 2.615 | 0.702 | 0.633 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 23.3 | 23.3 | 2.615 | 0.702 | 0.633 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 2.672 | 0.702 | 0.633 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 2.672 | 0.702 | 0.633 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 4.6 | 2.672 | 0.702 | 0.633 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.59 | 8.59 | 2.672 | 0.702 | 0.633 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 2.672 | 0.702 | 0.633 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 2.672 | 0.702 | 0.633 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 4.6 | 2.672 | 0.702 | 0.633 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.59 | 8.59 | 2.672 | 0.702 | 0.633 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 3.68 | 279.51 | 2.672 | 0.702 | 0.633 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 6.75 | 60.74 | 2.672 | 0.702 | 0.633 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 3.68 | 279.6 | 2.672 | 0.702 | 0.633 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 2.672 | 0.702 | 0.633 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 2.672 | 0.702 | 0.633 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-OPER | 8.58 | 34.33 | 2.672 | 0.702 | 0.633 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-OPER | 4.6 | 18.39 | 2.672 | 0.702 | 0.633 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 2.65 | 0.702 | 0.633
North Total or Average |  |  | 432.93 | 2.66 | 0.702 | 0.633
Non-North Total or Average |  |  | 781.15 | 2.65 | 0.702 | 0.633
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1321877.02 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 5546104.96 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 41287.17 | 28971.54 | 12315.63 | 0.7 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 11156.58 | 7834.06 | 3322.52 | 0.7 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 37732.35 | 26475.41 | 11256.94 | 0.7 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 10528.91 | 7394.26 | 3134.64 | 0.7 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 519386.41 | 352595.02 | 166791.4 | 0.68 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 65483.82 | 45195.38 | 20288.44 | 0.69 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 361656.15 | 279431.49 | 82224.66 | 0.77 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 36790.91 | 25785.81 | 11005.1 | 0.7 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 33070.78 | 23165.41 | 9905.37 | 0.7 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 46239.12 | 33289.25 | 12949.87 | 0.72 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 3401.32 | 2370.33 | 1030.99 | 0.7 | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 769194.54 | 540019.74 | 229174.8 | 0.7 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 37145.47 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 28347.33 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 31009.17 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8759.98 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 4253.81 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 21874.03 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 38296.64 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 18383.86 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 46540.41 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 83209.54 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 764.77 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9005.72 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5250.79 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 20905.99 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 5673.33 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 20684.18 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 5641.71 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 1077309.31 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 78565.25 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 1077309.31 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 19005.51 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 20324.04 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 608.69 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 90416.75 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 5920.14 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | 495965.86 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.5 | 46.95 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.76 | 1121.23 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.48 | 303.44 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.61 | 1024.85 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.45 | 286.63 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 2.69 | 1709.22 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.57 | 996.68 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.41 | 895.22 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 36.81 | 61243.04 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 12113.17 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 30539.21 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 229629.3803 | 242.22 | 707.1948 | 0 | 0.0027 | 141803.0264 | 84671.8463
February | 200309.2062 | 212.2687 | 637.3262 | 0 | 0.0024 | 127800.1897 | 74010.8109
March | 199038.9054 | 214.5434 | 709.0355 | 0 | 0.0026 | 142204.3404 | 74098.6482
April | 173562.1606 | 190.8756 | 697.6444 | 0 | 0.0025 | 139942.7597 | 65197.8801
May | 160204.8273 | 180.6635 | 737.6316 | 0 | 0.0026 | 147987.9853 | 60869.308
June | 153779.4474 | 175.121 | 743.6859 | 0 | 0.0026 | 149210.6454 | 58690.1487
July | 157158.2438 | 179.9106 | 779.7299 | 0 | 0.0027 | 156446.6043 | 60124.605
August | 153822.9099 | 175.5525 | 751.8882 | 0 | 0.0026 | 150858.0314 | 58765.5226
September | 153435.035 | 172.7665 | 700.9657 | 0 | 0.0025 | 140630.6235 | 58256.7231
October | 178326.6985 | 195.7472 | 709.0919 | 0 | 0.0026 | 142237.0638 | 66930.9917
November | 201325.2666 | 215.1571 | 678.4617 | 0 | 0.0025 | 136061.2206 | 74665.0235
December | 221630.997 | 234.7304 | 702.3806 | 0 | 0.0026 | 140844.3617 | 81868.3585
Annual Sum or Average | 2182220 | 2389.5564 | 8555.0364 | 0 | 0.031 | 1716030 | 818149.8664
Minimum of Months | 153435.035 | 172.7665 | 637.3262 | 0 | 0.0024 | 127800.1897 | 58256.7231
Maximum of Months | 229629.3803 | 242.22 | 779.7299 | 0 | 0.0027 | 156446.6043 | 84671.8463
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 499658000000 | 311926.464 | 12-JAN-20:10 | 115409.094 | 92719.3 | 38613.045 | 4569.049 | 0 | 3472 | 5952.817 | 0 | 48888.791 | 0 | 0 | 0 | 2302.369 | 0 | 0
February | 450318000000 | 311193.968 | 03-FEB-20:10 | 115409.094 | 92719.3 | 38613.045 | 3022.753 | 1325.001 | 3472 | 5827.962 | 0 | 48888.791 | 0 | 0 | 0 | 1916.022 | 0 | 0
March | 501072000000 | 315878.214 | 29-MAR-19:30 | 115409.094 | 92719.3 | 38566.096 | 0 | 12652.034 | 3472 | 1704.164 | 0 | 48888.791 | 0 | 0 | 0 | 2466.734 | 0 | 0
April | 493103000000 | 316801.538 | 25-APR-19:10 | 115409.094 | 92719.3 | 38606.69 | 0 | 17201.09 | 0 | 1797.72 | 0 | 48888.791 | 0 | 0 | 0 | 2178.853 | 0 | 0
May | 521452000000 | 333134.66 | 24-MAY-19:10 | 115409.094 | 92719.3 | 38911.973 | 0 | 31995.721 | 0 | 2406.122 | 0 | 48888.791 | 0 | 0 | 0 | 2803.66 | 0 | 0
June | 525760000000 | 355880.837 | 15-JUN-19:00 | 115409.094 | 92719.3 | 39182.741 | 0 | 53063.899 | 0 | 3637.413 | 0 | 48888.791 | 0 | 0 | 0 | 2979.6 | 0 | 0
July | 551257000000 | 354887.555 | 11-JUL-19:10 | 115409.094 | 92719.3 | 39029.749 | 0 | 52310.989 | 0 | 4058.818 | 0 | 48888.791 | 0 | 0 | 0 | 2470.814 | 0 | 0
August | 531565000000 | 346779.249 | 15-AUG-19:10 | 115409.094 | 92719.3 | 38900.077 | 0 | 44950.626 | 0 | 3458.117 | 0 | 48888.791 | 0 | 0 | 0 | 2453.244 | 0 | 0
September | 495527000000 | 318306.668 | 08-SEP-19:49 | 115409.094 | 92719.3 | 38566.096 | 0 | 14963.606 | 3472 | 2114.302 | 0 | 48888.791 | 0 | 0 | 0 | 2173.479 | 0 | 0
October | 501188000000 | 315096.888 | 03-OCT-19:10 | 115409.094 | 92719.3 | 38566.096 | 0 | 11923.521 | 3472 | 1989.619 | 0 | 48888.791 | 0 | 0 | 0 | 2128.466 | 0 | 0
November | 479426000000 | 309331.015 | 22-NOV-20:00 | 115409.094 | 92719.3 | 38566.096 | 0 | 2923.725 | 3472 | 4981.817 | 0 | 48888.791 | 0 | 0 | 0 | 2370.192 | 0 | 0
December | 496280000000 | 310499.245 | 28-DEC-20:00 | 115409.094 | 92719.3 | 38613.045 | 2775.873 | 552.337 | 3472 | 5742.448 | 0 | 48888.791 | 0 | 0 | 0 | 2326.357 | 0 | 0
Annual Sum or Average | 6046610000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 450318000000 | 309331.015 |  | 115409.094 | 92719.3 | 38566.096 | 0 | 0 | 0 | 1704.164 | 0 | 48888.791 | 0 | 0 | 0 | 1916.022 | 0 | 0
Maximum of Months | 551257000000 | 355880.837 |  | 115409.094 | 92719.3 | 39182.741 | 4569.049 | 53063.899 | 3472 | 5952.817 | 0 | 48888.791 | 0 | 0 | 0 | 2979.6 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 151185.31 | 80183.42 | 0 | 231368.73
Cost per Total Building Area ($/m2) | 13.33 | 7.07 | 0 | 20.39
Cost per Net Conditioned Building Area ($/m2) | 13.33 | 7.07 | 0 | 20.39

## Picture
DOE Commercial Building Benchmark - Large Hotel

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | 8.55 | 58.7 | 3060.79
|  |  | Sat | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | 7.85
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3 | 8.1
GuestRoom_Ltg_Sch_Base | Fraction | Through 12/31 | WD | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33 | 9.51 | 58.28 | 3038.89
|  |  | Sat, Sun, Hol | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41 | 10.73
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Lobby_Ltg_Sch | Fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.6 | 0.5 | 0.5 | 19.7 | 118.2 | 6163.29
|  |  | Sat, Sun, Hol | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.6 | 0.5 | 0.5 | 19.7
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Office_Ltg_Sch_Base | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.61 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.61 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 15.72 | 78.6 | 4098.43
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
EmployeeLounge_Ltg_Sch | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.4 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.4 | 0.15 | 0.15 | 0.05 | 0.05 | 12.6 | 71.2 | 3712.57
|  |  | Sat, Sun, Hol | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.3 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.3 | 0.15 | 0.15 | 0.05 | 0.05 | 8.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MeetingRoom_Ltg_Sch_Base | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0 | 12.05 | 60.25 | 3141.61
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Storage_Ltg_Sch | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9 | 35.4 | 1845.86
|  |  | Sat, Sun, Hol | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MechanicalRoom_Ltg_Sch | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9 | 35.4 | 1845.86
|  |  | Sat, Sun, Hol | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
ExerciseRoom_Ltg_Sch_Base | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | 16 | 112 | 5840
LaundryRoom_Ltg_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 63 | 3285
Corridor_Ltg_Sch | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Exterior_Ltg_Sch | Fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 12 | 84 | 4380
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4 | 10.9 | 75.25 | 3923.75
|  |  | Sat | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4 | 10.25
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4 | 10.5
GuestRoom_Eqp_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | 8.82 | 53.11 | 2769.31
|  |  | Sat, Sun, Hol | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | 9.01
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Lobby_Eqp_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.68 | 1 | 1 | 1 | 1 | 0.32 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.21 | 9.02 | 45.1 | 2351.64
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Office_Eqp_Sch | Fraction | Through 12/31 | WD | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.43 | 0.43 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.75 | 0.63 | 0.63 | 0.48 | 0.48 | 0.33 | 0.33 | 14.27 | 83.07 | 4331.51
|  |  | Sat, Sun, Hol | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.48 | 0.48 | 0.48 | 0.48 | 0.33 | 0.33 | 11.72
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
EmployeeLounge_Eqp_Sch | Fraction | Through 12/31 | WD | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11 | 11.08 | 66.48 | 3466.46
|  |  | Sat, Sun, Hol | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11 | 11.08
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
LaundryRoom_Eqp_Elec_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 2085.71
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
LaundryRoom_Eqp_Gas_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 2085.71
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MeetingRoom_Eqp_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.26 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 3.66 | 25.62 | 1335.9
ExerciseRoom_Eqp_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0 | 10.5 | 73.5 | 3832.5
Kitchen_Elec_Equip_SCH | Fraction | Through 12/31 | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9 | 23.6 | 1230.57
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9
|  |  | SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9
Kitchen_Gas_Equip_SCH | Fraction | Through 12/31 | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65 | 21.9 | 1141.93
|  |  | SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65
Kitchen_Exhaust_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 2.72 | 19.04 | 992.8
BLDG_ELEVATORS | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | 5.9 | 41.3 | 2153.5
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9 | 13.9 | 96.4 | 5026.57
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 13.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 13
GuestRoom_Occ_Sch | Fraction | Through 12/31 | WD | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.28 | 0.28 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.2 | 0.35 | 0.35 | 0.35 | 0.5 | 0.5 | 0.58 | 0.65 | 0.65 | 9.87 | 59.52 | 3103.54
|  |  | Sat, Sun, Hol | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.34 | 0.34 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.34 | 0.35 | 0.65 | 0.65 | 0.5 | 0.5 | 0.5 | 10.17
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Lobby_Occ_Sch | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 6.6 | 38.6 | 2012.71
|  |  | Sat, Sun, Hol | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Office_Occ_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 12.1 | 68.2 | 3556.14
|  |  | Sat, Sun, Hol | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 7.7
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
EmployeeLounge_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 3.1 | 16.85 | 878.61
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 1.35
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MeetingRoom_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 3.2 | 19.2 | 1001.14
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 3.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
LaundryRoom_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.17 | 7.02 | 366.04
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.17
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
ExerciseRoom_Occ_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | 14.5 | 101.5 | 5292.5
INFIL_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84 | 4380
INFIL_QUARTER_ON_SCH | Fraction | Through 12/31 | All | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6 | 42 | 2190
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.5 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | 9 | 63.3 | 3300.64
|  |  | Sat, WinterDesign | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.4 | 0.5 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3 | 9.3
|  |  | Sun, Hol, Other | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.55 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2 | 9
GuestRoom_SWH_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25 | 8 | 40 | 2085.71
|  |  | Other | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35 | 7.8
LaundryRoom_SWH_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 56 | 2920
Hours_of_operation | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | All | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 3528 | 183960
HTGSETP_SCH_KEYCARD | Temperature | Through 12/31 | SummerDesign, WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 0 | 0
|  |  | Other | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 486
CLGSETP_SCH | Temperature | Through 12/31 | All | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 4032 | 210240
CLGSETP_SCH_KEYCARD | Temperature | Through 12/31 | SummerDesign, WinterDesign | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 0 | 0
|  |  | Other | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 25 | 25 | 25 | 26 | 26 | 26 | 26 | 26 | 26 | 25 | 25 | 25 | 24 | 24 | 24 | 24 | 24 | 594
SemiHeated_HtgSP_Sch | Temperature | Through 12/31 | All | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 172.8 | 1209.6 | 63072
Base_OccGuestRoom_HtgSP_Sch | Temperature | Through 12/31 | All | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 506.4 | 3544.8 | 184836
Base_OccGuestRoom_ClgSP_Sch | Temperature | Through 12/31 | All | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 506.4 | 3544.8 | 184836
VacGuestRoom_HtgSP_Sch | Temperature | Through 12/31 | All | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 453.6 | 3175.2 | 165564
VacGuestRoom_ClgSP_Sch | Temperature | Through 12/31 | All | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 559.2 | 3914.4 | 204108
CommonArea_HtgSP_Sch | Temperature | Through 12/31 | All | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 506.4 | 3544.8 | 184836
CommonArea_ClgSP_Sch | Temperature | Through 12/31 | All | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 573.6 | 4015.2 | 209364
UnitHeater_HtgSP_Sch | Temperature | Through 12/31 | All | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4 | 2620.8 | 136656
UnitHeater_ClgSP_Sch | Temperature | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
Off During Unoccupied Period | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 70 | 3650
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Laundry_Flr_1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Laundry_Flr_1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Laundry_Flr_1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Laundry_Flr_1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_1_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_1_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_1_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_1_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_2_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_2_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_2_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_2_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_3_Mult19_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_3_Mult19_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_3_Mult19_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_3_Mult19_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_4_Mult19_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_4_Mult19_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_4_Mult19_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_4_Mult19_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_5_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_5_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_5_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_5_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_6_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_6_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_6_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_6_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_1_Flr_6 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_1_Flr_6 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_1_Flr_6 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_1_Flr_6 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_2_Flr_6 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_2_Flr_6 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_2_Flr_6 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_2_Flr_6 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_3_Mult9_Flr_6 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_3_Mult9_Flr_6 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_3_Mult9_Flr_6 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_3_Mult9_Flr_6 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_Flr_6 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Kitchen_Flr_6 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Kitchen_Flr_6 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Kitchen_Flr_6 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_Flr_6_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Kitchen_Flr_6_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Kitchen_Flr_6_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Kitchen_Flr_6_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Kitchen_Flr_6_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
FLR_3_DOAS_OAminOAFracSchedule | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FLR_6_DOAS_OAminOAFracSchedule | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720