## BuildingSummary
Building Summary Secondary School new construction
|  | Value | Data Source
Program
| Building Name | Benchmark Secondary School New
| Available Fuel Types | gas, electricity
| Principal Building Activity | Education
Form
| Total Floor Area (m2) | 19592 | Pless, S.; Torcellini, P.; Long, N. (2007). Technical Support Document: Development of the Advanced Energy Design Guide for K-12 Schools--30% Energy Savings. 178 pp.; NREL Report No. TP-550-42114. http://www.nrel.gov/docs/fy07osti/42114.pdf
| Building Shape | "E" Shape
Aspect Ratio
| Number of Floors | 2
Window Fraction (Window to Wall Ratio)
| South | 0.35
| East | 0.35
| North | 0.35
| West | 0.28
| Total | 0.34
| Skylight/TDD Percentage | 1.12%
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | See pictures
| Floor to Ceiling Height (m) | 4
| Roof type | Flat built-up | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel-Framed | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 6384
| Net Dimensions - Total Area (m2) | 4088.16
| Wall to Skin Ratio | 0.35
Roof
| Construction Type | Insulation Entirely Above Deck | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 11902
| Net Dimensions - Total Area (m2) | 11768.6976
| Roof to Skin Ratio | 0.65
| Window Dimensions (m2) |  | Pless, S.; Torcellini, P.; Long, N. (2007). Technical Support Document: Development of the Advanced Energy Design Guide for K-12 Schools--30% Energy Savings. 178 pp.; NREL Report No. TP-550-42114. http://www.nrel.gov/docs/fy07osti/42114.pdf
| South | 753.18
| East | 291.61
| North | 753.18
| West | 291.2
| Total Area (m2) | 2089.17
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 133.8
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab w/carpet
| Dimensions - Total Area (m2) | 11902
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 6792
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 39184
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.26 | See Benchmark Technical Report
HVAC
| System Type | MZ VAV, PSZ-AC (gym, aux gym, auditorium, kitchen, & cafeteria) | 2003 CBECS
| Heating Type | Boiler, gas heat (gym, aux gym, auditorium, kitchen, & cafeteria) | 2003 CBECS
| Cooling Type | Air cooled chiller, PACU (gym, aux gym, auditorium, kitchen, & cafeteria) | 2003 CBECS
| Fan Control | Variable, constant (gym, aux gym, auditorium, kitchen, & cafeteria) | 2003 CBECS
Service Water Heating
| SWH Type | Storage Tank
| Fuel | Natural Gas
| Thermal Efficiency (%) | 80 | Standard 90.1-2004
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 815.28

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
First Floor
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 10 | 0 | 0 | 8 | 0 | 198 | 0 | 0.21987
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 10 | 0 | 0 | 8 | 0 | 954 | 0 | 0.12093
CORRIDOR_POD_1_ZN_1_FLR_1 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 5.38 | 4 | 0 | 0 | 0 | 0.5 | 160 | 0 | 0.017006
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 10 | 0 | 0 | 8 | 0 | 198 | 0 | 0.21987
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 10 | 0 | 0 | 8 | 0 | 954 | 0 | 0.12093
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 10 | 0 | 0 | 8 | 0 | 198 | 0 | 0.21987
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 10 | 0 | 0 | 8 | 0 | 954 | 0 | 0.12093
CORRIDOR_POD_2_ZN_1_FLR_1 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 5.38 | 4 | 0 | 0 | 0 | 0.5 | 160 | 0 | 0.017006
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 10 | 0 | 0 | 8 | 0 | 198 | 0 | 0.21987
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 10 | 0 | 0 | 8 | 0 | 954 | 0 | 0.12093
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 10 | 0 | 0 | 8 | 0 | 198 | 0 | 0.21987
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 10 | 0 | 0 | 8 | 0 | 954 | 0 | 0.12093
CORRIDOR_POD_3_ZN_1_FLR_1 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 5.38 | 4 | 0 | 0 | 0 | 0.5 | 160 | 0 | 0.017006
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 10 | 0 | 0 | 8 | 0 | 198 | 0 | 0.21987
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 10 | 0 | 0 | 8 | 0 | 954 | 0 | 0.12093
MAIN_CORRIDOR_ZN_1_FLR_1 | Yes | 1 | 1140 | 4560 | 4 | 200 | 70 | 0 | 0 | 5.38 | 4 | 0 | 0 | 0 | 0.5 | 570 | 0 | 0.047735
LOBBY_ZN_1_FLR_1 | Yes | 1 | 210 | 840 | 4 | 60 | 21 | 0 | 0 | 13.988 | 4 | 0 | 0 | 0 | 0.5 | 105 | 0 | 0.07774
BATHROOMS_ZN_1_FLR_1 | Yes | 1 | 210 | 840 | 4 | 116 | 40.6 | 10 | 21 | 9.684 | 4 | 0 | 197.4991 | 25 | 0 | 300 | 300 | 0.1503
OFFICES_ZN_1_FLR_1 | Yes | 1 | 532 | 2128 | 4 | 208 | 72.8 | 20 | 26.6 | 11.836 | 10.8 | 0 | 0 | 10 | 0 | 266 | 0 | 0.10638
GYM_ZN_1_FLR_1 | Yes | 1 | 1976 | 15808 | 8 | 0 | 80.28 | 1 | 1976 | 15.064 | 5 | 0 | 717.2337 | 10 | 0 | 19760 | 0 | 0.13605
AUX_GYM_ZN_1_FLR_1 | Yes | 1 | 1248 | 9984 | 8 | 608 | 266.35 | 3.33 | 374.7748 | 15.064 | 5 | 0 | 0 | 10 | 0 | 3747.7477 | 0 | 0.20232
AUDITORIUM_ZN_1_FLR_1 | Yes | 1 | 988 | 7904 | 8 | 512 | 106.4 | 1 | 988 | 9.684 | 5 | 0 | 0 | 8 | 0 | 7904 | 0 | 0.20655
KITCHEN_ZN_1_FLR_1 | Yes | 1 | 216 | 864 | 4 | 36 | 12.6 | 6.67 | 32.3838 | 12.912 | 222.194 | 1119.04 | 503.4582 | 8 | 0 | 259.0705 | 1887.788 | 0.045349
CAFETERIA_ZN_1_FLR_1 | Yes | 1 | 624 | 2496 | 4 | 200 | 70 | 1.3935 | 447.7782 | 15.064 | 19.2604 | 0 | 0 | 10 | 0 | 4477.7824 | 0 | 0.087209
MECH_ZN_1_FLR_1 | Yes | 1 | 342 | 1368 | 4 | 0 | 0 | 100 | 3.42 | 16.14 | 4 | 0 | 0 | 0 | 0.25 | 85.5 | 0 | 0
Total Conditioned Zones |  |  | 11902 | 64456 |  | 3752 | 1374.23 |  | 4829.9568
Second Floor
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 10 | 0 | 0 | 8 | 0 | 198 | 0 | 0.49196
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 10 | 0 | 0 | 8 | 0 | 954 | 0 | 0.39302
CORRIDOR_POD_1_ZN_1_FLR_2 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 5.38 | 4 | 0 | 0 | 0 | 0.5 | 160 | 0 | 0.2891
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 10 | 0 | 0 | 8 | 0 | 198 | 0 | 0.49196
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 10 | 0 | 0 | 8 | 0 | 954 | 0 | 0.39302
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 10 | 0 | 0 | 8 | 0 | 198 | 0 | 0.49196
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 10 | 0 | 0 | 8 | 0 | 954 | 0 | 0.39302
CORRIDOR_POD_2_ZN_1_FLR_2 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 5.38 | 4 | 0 | 0 | 0 | 0.5 | 160 | 0 | 0.2891
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 10 | 0 | 0 | 8 | 0 | 198 | 0 | 0.49196
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 10 | 0 | 0 | 8 | 0 | 954 | 0 | 0.39302
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 10 | 0 | 0 | 8 | 0 | 198 | 0 | 0.49196
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 20 | 0 | 0 | 8 | 0 | 954 | 0 | 0.39302
CORRIDOR_POD_3_ZN_1_FLR_2 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 5.38 | 4 | 0 | 0 | 0 | 0.5 | 160 | 0 | 0.2891
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 10 | 0 | 0 | 8 | 0 | 198 | 0 | 0.49196
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 20 | 0 | 0 | 8 | 0 | 954 | 0 | 0.39302
MAIN_CORRIDOR_ZN_1_FLR_2 | Yes | 1 | 1140 | 4560 | 4 | 200 | 70 | 0 | 0 | 5.38 | 4 | 0 | 0 | 0 | 0.5 | 570 | 0 | 0.31983
LOBBY_ZN_1_FLR_2 | Yes | 1 | 210 | 840 | 4 | 60 | 21 | 0 | 0 | 13.988 | 4 | 0 | 0 | 0 | 0.5 | 105 | 0 | 0.34983
BATHROOMS_ZN_1_FLR_2 | Yes | 1 | 210 | 840 | 4 | 116 | 40.6 | 10 | 21 | 9.684 | 4 | 0 | 197.4991 | 25 | 0 | 300 | 300 | 0.42239
OFFICES_ZN_1_FLR_2 | Yes | 1 | 532 | 2128 | 4 | 208 | 72.8 | 20 | 26.6 | 11.836 | 10.8 | 0 | 0 | 10 | 0 | 266 | 0 | 0.37847
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | Yes | 1 | 840 | 3360 | 4 | 236 | 83.01 | 4.35 | 193.1034 | 13.988 | 10 | 0 | 0 | 8 | 0 | 1544.8276 | 0 | 0.34854
MECH_ZN_1_FLR_2 | Yes | 1 | 342 | 1368 | 4 | 0 | 0 | 100 | 3.42 | 16.14 | 4 | 0 | 0 | 0 | 0.25 | 85.5 | 0 | 0
Total Conditioned Zones |  |  | 7690 | 30760 |  | 2632 | 921.61 |  | 1204.1234
Building Total Conditioned Zones |  |  | 19592 | 95216 |  | 6384 | 2295.84 |  | 6034.0803
4088.16
Data Source | [7 empty] | 1 |  | 2 | 4, 5 | 4, 5 | 4, 5 | 3 | 3 | 3 | 4 | 4
Sources
[1] Pless, S.; Torcellini, P.; Long, N. (2007). Technical Support Document: Development of the Advanced Energy Design Guide for K-12 Schools--30% Energy Savings. 178 pp.; NREL Report No. TP-550-42114. http://www.nrel.gov/docs/fy07osti/42114.pdf
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report
[5] Smith, V. A. and D.R. Fisher. (2001). Estimating Food Service Loads and Profiles. ASHRAE Transactions 2001. V. 107. Pt 2. Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 10.0524 | 95.5362 | 14.4042 | 118.7841 |  | 51.3966 | 6.8698 | 126.3091 | 3.9685 | 15.2202 | 143.1615 | 27.465 | 26.0558 | 5.3932 | 4.7269 | 0.77492
Fabric | [6 empty] | weighting factor is for all of 3B
Exterior walls
| Construction Type | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed
| R-value (m2·K / W) | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 2.0964 | 2.0964 | 2.0964 | 2.0964 | 2.7548 | 2.7548
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.849 | 2.849 | 2.849 | 2.849 | 2.7933 | 3.7175
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
| SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.702
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.162 | 0.162 | 0.162 | 0.223 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.633
Skylights/TDD
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
| SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.702
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.162 | 0.162 | 0.162 | 0.223 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.633
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| COOLSYS1 CHILLER | 1433.9093 | 1438.4896 | 1255.6507 | 1253.0038 | 829.4439 | 950.6658 | 999.4819 | 1313.3235 | 707.6172 | 724.9423 | 1281.9685 | 677.6816 | 1202.819 | 585.1249 | 976.9539 | 692.5501
| PSZ-AC_1:5_COOLC DXCOIL | 490.6879 | 490.6879 | 490.6879 | 490.6879 | 490.6879 | 490.6879 | 364.2728 | 490.6879 | 450.4368 | 439.8107 | 490.6879 | 455.1895 | 490.6879 | 381.4056 | 490.6879 | 327.0982
| PSZ-AC_2:6_COOLC DXCOIL | 119.8579 | 125.4336 | 131.4466 | 121.7165 | 99.7408 | 115.6253 | 97.2079 | 128.8688 | 108.593 | 94.3863 | 123.2688 | 103.7373 | 121.2329 | 88.3367 | 134.088 | 96.9804
| PSZ-AC_3:7_COOLC DXCOIL | 196.2751 | 196.2751 | 196.2751 | 196.2751 | 196.2751 | 196.2751 | 146.9377 | 196.2751 | 156.2593 | 155.7642 | 196.2751 | 151.4404 | 196.2751 | 130.8393 | 196.2751 | 130.8393
| PSZ-AC_4:8_COOLC DXCOIL | 14.2129 | 14.0074 | 12.7073 | 13.4446 | 11.759 | 11.0677 | 18.1925 | 13.5531 | 12.057 | 9.5727 | 13.2973 | 11.8567 | 13.4423 | 9.8396 | 12.8498 | 8.8843
| PSZ-AC_5:9_COOLC DXCOIL | 111.4777 | 111.4777 | 111.4777 | 111.4777 | 111.4777 | 111.4777 | 87.2141 | 111.4777 | 102.8655 | 98.2437 | 111.4777 | 103.9805 | 111.4777 | 88.1485 | 111.4777 | 74.3123
Heating (kW)
| HEATSYS1 BOILER | 607.7221 | 778.8929 | 727.8123 | 768.5923 | 528.0386 | 677.4609 | 967.5738 | 874.0718 | 709.0442 | 739.7872 | 958.2435 | 767.6098 | 1009.1919 | 904.572 | 1025.1168 | 1580.3666
| PSZ-AC_1:5_HEATC | 765.0269 | 1009.9404 | 852.0818 | 1089.4655 | 795.6607 | 921.1228 | 879.4681 | 1212.7703 | 963.6127 | 1048.8159 | 1416.7661 | 1150.2765 | 1531.1076 | 1395.2101 | 1567.2052 | 1940.738
| PSZ-AC_2:6_HEATC | 169.8998 | 221.4035 | 195.7425 | 232.1861 | 157.0652 | 193.9999 | 203.9132 | 262.9873 | 210.7146 | 212.1698 | 296.0526 | 238.1714 | 315.6992 | 282.3927 | 333.3228 | 415.837
| PSZ-AC_3:7_HEATC | 306.0108 | 403.9762 | 340.8327 | 435.7862 | 318.2643 | 368.4491 | 351.7872 | 485.1081 | 385.4451 | 419.5263 | 566.7064 | 460.1106 | 612.443 | 558.084 | 626.8821 | 776.2952
| PSZ-AC_4:8_HEATC | 22.1591 | 28.8303 | 22.0663 | 29.8507 | 19.0674 | 20.7764 | 41.6783 | 33.4974 | 25.6599 | 22.9328 | 38.3933 | 29.7987 | 41.9445 | 35.3823 | 41.0408 | 52.7124
| PSZ-AC_5:9_HEATC | 173.8039 | 229.445 | 193.5816 | 247.512 | 180.7635 | 209.2668 | 199.8034 | 275.5253 | 218.92 | 238.277 | 321.8704 | 261.3275 | 347.8472 | 316.9731 | 356.0481 | 440.9098
HVAC Efficiency
Air Conditioning (COP)
| COOLSYS1 CHILLER | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8
| PSZ-AC_1:5_COOLC DXCOIL | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.57 | 3.25 | 3.33 | 3.35 | 3.25 | 3.32 | 3.25 | 3.51 | 3.25 | 3.73
| PSZ-AC_2:6_COOLC DXCOIL | 3.51 | 3.49 | 3.49 | 3.51 | 3.51 | 3.51 | 3.95 | 3.49 | 3.71 | 3.67 | 3.49 | 3.68 | 3.51 | 3.88 | 3.49 | 4.14
| PSZ-AC_3:7_COOLC DXCOIL | 3.49 | 3.49 | 3.49 | 3.49 | 3.49 | 3.49 | 3.9 | 3.49 | 3.79 | 3.79 | 3.49 | 3.84 | 3.49 | 4.14 | 3.49 | 4.14
| PSZ-AC_4:8_COOLC DXCOIL | 3.65 | 3.65 | 3.65 | 3.65 | 3.65 | 3.65 | 3.84 | 3.65 | 3.71 | 3.74 | 3.65 | 3.7 | 3.65 | 3.84 | 3.65 | 4.04
| PSZ-AC_5:9_COOLC DXCOIL | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 3.85 | 3.51 | 3.6 | 3.66 | 3.51 | 3.59 | 3.51 | 3.83 | 3.51 | 4.18
Heating Efficiency (%)
| HEATSYS1 BOILER | 0.75 | 0.78 | 0.75 | 0.78 | 0.75 | 0.75 | 0.78 | 0.78 | 0.75 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_1:5_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_2:6_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_3:7_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_4:8_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_5:9_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
HVAC Control - Economizer
| PSZ-AC_1:5_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC_2:6_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC_3:7_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC_4:8_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC_5:9_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_OTHER_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_POD_1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_POD_2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_POD_3_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
| BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
| CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63
| KITCHEN_ZN_1_FLR_1 EXHAUST FAN | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26
| PSZ-AC_1:5_FAN | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76
| PSZ-AC_2:6_FAN | 4.83 | 5.05 | 5.29 | 4.9 | 4.02 | 4.66 | 5.36 | 5.19 | 5.23 | 4.33 | 4.96 | 4.81 | 4.88 | 4.64 | 5.4 | 5.86
| PSZ-AC_3:7_FAN | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9
| PSZ-AC_4:8_FAN | 0.57 | 0.56 | 0.51 | 0.54 | 0.47 | 0.45 | 0.94 | 0.55 | 0.53 | 0.43 | 0.54 | 0.51 | 0.54 | 0.5 | 0.52 | 0.54
| PSZ-AC_5:9_FAN | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49
| VAV_OTHER_FAN | 13.43 | 13.87 | 14.58 | 13.02 | 11.2 | 12.74 | 16.16 | 13.26 | 13.23 | 11.74 | 12.64 | 12.12 | 12.36 | 11.79 | 11.89 | 13.45
| VAV_POD_1_FAN | 8.56 | 8.87 | 9.67 | 8.24 | 7.26 | 8.53 | 13.73 | 8.62 | 8.73 | 8.55 | 8.31 | 8.11 | 8.17 | 7.97 | 8.25 | 11.12
| VAV_POD_2_FAN | 8.4 | 8.68 | 9.48 | 8.07 | 7.1 | 8.36 | 13.33 | 8.43 | 8.52 | 8.31 | 8.13 | 7.9 | 8 | 7.77 | 8 | 10.72
| VAV_POD_3_FAN | 9.01 | 9.3 | 10.12 | 8.7 | 7.7 | 9.02 | 13.41 | 9.05 | 9.28 | 8.93 | 8.77 | 8.66 | 8.63 | 8.49 | 8.67 | 11.43
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.090028 | 0.11865 | 0.088963 | 0.094959 | 0.13307 | 0.10291 | 0.14816 | 0.083074 | 0.037013 | 0.072186 | 0.082551 | 0.037018 | 0.065498 | 0.078706 | 0.063285 | 0.096854
| Total Cost ($/m2) | 15.1 | 17.53 | 13.2 | 11.79 | 14.63 | 13.72 | 15.33 | 9.94 | 4.29 | 7.35 | 9.4 | 4.04 | 7.28 | 8.28 | 6.62 | 10.08
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011432 | 0.0080786 | 0.008279 | 0.0097228 | 0.0085541 | 0.0077453 | 0.0085698 | 0.0096985 | 0.006922 | 0.0084083 | 0.0083596 | 0.0069423 | 0.0078739 | 0.008142 | 0.0078683 | 0.0041311
| Total Cost ($/m2) | 0.4 | 0.97 | 0.78 | 1.99 | 0.67 | 0.99 | 1.64 | 3.34 | 1.64 | 2.74 | 3.77 | 2.32 | 4.83 | 4.03 | 5.75 | 5.07
Total Utility Costs
| Cost Intensity ($/m2) | 15.5 | 18.51 | 13.98 | 13.78 | 15.3 | 14.71 | 16.96 | 13.28 | 5.93 | 10.1 | 13.17 | 6.37 | 12.12 | 12.31 | 12.36 | 15.16
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 1273541.6667 | 909661.1111 | 902380.5556 | 468644.4444 | 208247.2222 | 631280.5556 | 80869.4444 | 384325 | 294519.4444 | 64327.7778 | 275144.4444 | 184027.7778 | 216294.4444 | 107022.2222 | 83813.8889 | 42683.3333
| Interior Lighting | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333
| Exterior Lighting | 39500 | 39486.1111 | 39477.7778 | 39472.2222 | 39441.6667 | 39433.3333 | 39452.7778 | 39430.5556 | 39444.4444 | 39366.6667 | 39436.1111 | 39413.8889 | 39411.1111 | 39400 | 39377.7778 | 39138.8889
| Interior Equipment | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 339783.3333 | 319591.6667 | 339413.8889 | 303869.4444 | 288472.2222 | 320108.3333 | 292377.7778 | 302341.6667 | 317138.8889 | 278658.3333 | 300550 | 302319.4444 | 307463.8889 | 301605.5556 | 311413.8889 | 343127.7778
| Pumps | 16888.8889 | 12197.2222 | 12377.7778 | 7694.4444 | 5941.6667 | 9138.8889 | 3486.1111 | 6647.2222 | 6205.5556 | 2863.8889 | 5502.7778 | 4769.4444 | 5705.5556 | 4366.6667 | 4936.1111 | 6847.2222
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 43591.6667 | 41700 | 41838.8889 | 39950 | 39983.3333 | 40597.2222 | 38316.6667 | 38786.1111 | 38811.1111 | 37583.3333 | 37983.3333 | 37802.7778 | 37569.4444 | 36941.6667 | 36366.6667 | 35580.5556
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 3285519.4444 | 2894847.2222 | 2907702.7778 | 2431841.6667 | 2154297.2222 | 2612769.4444 | 2026713.8889 | 2343741.6667 | 2268330.5556 | 1995013.8889 | 2230827.7778 | 2140541.6667 | 2178655.5556 | 2061550 | 2048125 | 2039591.6667
Gas (MJ)
| Heating | 149340 | 1759300 | 1260860 | 3354290 | 883230 | 1880800 | 3047230 | 6039840 | 3941540 | 5669440 | 8080300 | 5805100 | 11238990 | 8910750 | 13474180 | 23159040
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 183800 | 250250 | 219890 | 309330 | 289310 | 263310 | 339290 | 356360 | 347290 | 372930 | 396360 | 392600 | 432020 | 435270 | 485250 | 548240
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 686530 | 2362940 | 1834140 | 4017010 | 1525940 | 2497500 | 3739920 | 6749590 | 4642230 | 6395770 | 8830060 | 6551080 | 12024390 | 9699420 | 14312820 | 24060670
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 12514400 | 12784390 | 12301870 | 12771640 | 9281400 | 11903470 | 11036090 | 15187060 | 12808220 | 13577810 | 16861040 | 14257040 | 19867550 | 17121000 | 21686060 | 31403200
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 234.0113 | 167.1488 | 165.811 | 86.1127 | 38.2651 | 115.9968 | 14.8596 | 70.6191 | 54.1175 | 11.8201 | 50.5574 | 33.8148 | 39.7438 | 19.6652 | 15.4007 | 7.843
| Interior Lighting (elec) | 172.6286 | 172.6286 | 172.6286 | 172.6286 | 172.6286 | 172.6286 | 172.6286 | 172.6286 | 172.6286 | 172.6286 | 172.6286 | 172.6286 | 172.6286 | 172.6286 | 172.6286 | 172.6286
| Exterior Lighting (elec) | 7.2581 | 7.2555 | 7.254 | 7.253 | 7.2473 | 7.2458 | 7.2494 | 7.2453 | 7.2479 | 7.2336 | 7.2463 | 7.2422 | 7.2417 | 7.2397 | 7.2356 | 7.1917
| Interior Equipment (elec) | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 62.4347 | 58.7245 | 62.3668 | 55.8355 | 53.0063 | 58.8194 | 53.724 | 55.5548 | 58.2738 | 51.203 | 55.2256 | 55.5507 | 56.496 | 55.4196 | 57.2218 | 63.0492
| Pumps (elec) | 3.1033 | 2.2412 | 2.2744 | 1.4138 | 1.0918 | 1.6793 | 0.64057 | 1.2214 | 1.1403 | 0.52624 | 1.0111 | 0.87638 | 1.0484 | 0.80237 | 0.907 | 1.2582
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 8.0099 | 7.6623 | 7.6878 | 7.3408 | 7.3469 | 7.4597 | 7.0406 | 7.1269 | 7.1315 | 6.9059 | 6.9794 | 6.9462 | 6.9033 | 6.788 | 6.6823 | 6.5379
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 603.7092 | 531.9237 | 534.2859 | 446.8472 | 395.8488 | 480.0924 | 372.4056 | 430.6589 | 416.8023 | 366.5807 | 409.9112 | 393.3213 | 400.3246 | 378.8067 | 376.3398 | 374.7718
Gas (MJ/m2)
| Heating (gas) | 7.6225 | 89.7969 | 64.3559 | 171.2071 | 45.0812 | 95.9984 | 155.5344 | 308.2809 | 201.1811 | 289.3753 | 412.4285 | 296.2995 | 573.652 | 454.8157 | 687.7389 | 1182.0661
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 9.3814 | 12.7731 | 11.2235 | 15.7886 | 14.7667 | 13.4397 | 17.3178 | 18.1891 | 17.7261 | 19.0348 | 20.2307 | 20.0388 | 22.0508 | 22.2167 | 24.7678 | 27.9829
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 35.0413 | 120.6074 | 93.6168 | 205.0332 | 77.8859 | 127.4755 | 190.8902 | 344.5075 | 236.9452 | 326.448 | 450.6972 | 334.3753 | 613.7398 | 495.0704 | 730.5441 | 1228.0865
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 638.7505 | 652.5311 | 627.9027 | 651.8804 | 473.7342 | 607.5679 | 563.2957 | 775.1664 | 653.7474 | 693.0283 | 860.6084 | 727.697 | 1014.0644 | 873.8771 | 1106.8834 | 1602.8583
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 910.1458 | 810.5107 | 621.3848 | 505.7618 | 684.6017 | 502.8217 | 470.8338 | 466.3657 | 477.0237 | 450.5515 | 453.2523 | 487.7132 | 455.0335 | 456.2881 | 456.5181 | 471.8529
| Feb | 944.1209 | 758.8826 | 697.2505 | 488.5087 | 649.4794 | 551.6348 | 558.8721 | 462.906 | 550.8234 | 467.5818 | 453.0219 | 468.5856 | 453.2603 | 471.2401 | 455.9981 | 463.4756
| Mar | 976.068 | 815.7531 | 869.4531 | 637.1148 | 634.598 | 638.1694 | 493.607 | 655.8558 | 564.4382 | 529.5819 | 556.0175 | 587.0283 | 469.6053 | 538.5736 | 453.4308 | 462.1916
| Apr | 1024.1005 | 906.6791 | 898.2005 | 776.3174 | 728.4554 | 883.3844 | 581.1069 | 665.3278 | 709.2847 | 485.5933 | 569.0876 | 656.9223 | 564.0403 | 510.7157 | 476.7873 | 460.3726
| May | 1131.4829 | 1160.0603 | 1065.9412 | 942.8099 | 726.3869 | 1009.2214 | 635.3245 | 924.9866 | 834.0519 | 643.0041 | 884.6536 | 754.7292 | 865.6836 | 632.0114 | 633.3021 | 563.1299
| Jun | 1210.6756 | 1151.1003 | 1305.8871 | 1048.9261 | 728.8704 | 1210.9393 | 650.3655 | 1189.5846 | 941.6976 | 694.8005 | 1173.8255 | 880.1107 | 1098.0793 | 870.9499 | 915.5345 | 711.5821
| Jul | 927.0876 | 1030.7372 | 1137.9673 | 947.2742 | 494.1993 | 1000.44 | 526.5989 | 1010.2391 | 766.0291 | 550.0564 | 895.2166 | 700.8352 | 855.784 | 659.8338 | 742.9717 | 477.4382
| Aug | 995.1848 | 968.4421 | 1100.4196 | 867.4328 | 612.1503 | 960.7206 | 496.3686 | 1012.5176 | 739.0511 | 501.1227 | 912.9574 | 728.8714 | 836.3544 | 591.3865 | 665.2379 | 473.4069
| Sep | 1156.0474 | 1219.7185 | 1188.0174 | 1013.9535 | 835.8015 | 1008.8493 | 898.8242 | 939.5251 | 793.8404 | 753.7599 | 890.278 | 811.8957 | 857.6461 | 700.5847 | 788.5436 | 472.0958
| Oct | 1108.3902 | 1017.6783 | 907.4886 | 844.4446 | 775.9182 | 877.2715 | 629.8135 | 804.8676 | 696.405 | 550.8422 | 681.9765 | 726.7256 | 590.5891 | 593.5958 | 496.5394 | 457.4822
| Nov | 1001.8419 | 896.6705 | 793.9085 | 571.1326 | 689.1085 | 570.612 | 496.6352 | 683.9778 | 526.8955 | 464.3911 | 676.2485 | 538.3663 | 499.2711 | 459.2749 | 453.6289 | 463.2401
| Dec | 892.0957 | 798.5935 | 601.1394 | 497.3817 | 696.1881 | 547.3976 | 472.0313 | 454.0121 | 470.3981 | 450.5606 | 451.8545 | 462.2892 | 452.4679 | 455.4773 | 453.9968 | 470.3203
Time of Peak Electrical Demand
| Jan | 06-JAN-12:00 | 03-JAN-12:30 | 26-JAN-15:00 | 23-JAN-16:19 | 26-JAN-12:00 | 18-JAN-14:00 | 17-JAN-14:00 | 09-JAN-11:39 | 25-JAN-14:00 | 27-JAN-11:39 | 27-JAN-11:09 | 27-JAN-12:00 | 05-JAN-11:09 | 05-JAN-08:09 | 09-JAN-11:09 | 02-JAN-11:09
| Feb | 23-FEB-11:00 | 23-FEB-14:30 | 28-FEB-15:00 | 17-FEB-14:00 | 13-FEB-11:00 | 08-FEB-15:00 | 15-FEB-16:10 | 15-FEB-12:00 | 14-FEB-16:10 | 21-FEB-12:00 | 17-FEB-11:39 | 07-FEB-14:00 | 03-FEB-11:09 | 02-FEB-14:00 | 01-FEB-11:09 | 03-FEB-08:09
| Mar | 13-MAR-14:00 | 29-MAR-11:00 | 17-MAR-15:00 | 28-MAR-15:00 | 30-MAR-11:00 | 31-MAR-15:00 | 01-MAR-12:00 | 09-MAR-15:00 | 02-MAR-14:00 | 29-MAR-15:00 | 31-MAR-15:09 | 30-MAR-15:00 | 23-MAR-13:00 | 30-MAR-15:00 | 01-MAR-11:39 | 14-MAR-07:10
| Apr | 03-APR-13:00 | 21-APR-14:00 | 26-APR-14:00 | 14-APR-15:00 | 11-APR-15:00 | 21-APR-15:09 | 13-APR-14:00 | 04-APR-15:00 | 21-APR-15:00 | 14-APR-13:00 | 07-APR-14:39 | 25-APR-14:00 | 14-APR-15:00 | 06-APR-15:00 | 04-APR-14:00 | 24-APR-11:00
| May | 24-MAY-14:00 | 18-MAY-13:00 | 30-MAY-15:00 | 31-MAY-15:00 | 30-MAY-11:09 | 31-MAY-15:00 | 17-MAY-13:00 | 31-MAY-15:00 | 31-MAY-15:00 | 05-MAY-15:00 | 30-MAY-15:00 | 23-MAY-15:00 | 31-MAY-11:00 | 16-MAY-15:00 | 31-MAY-15:00 | 24-MAY-14:00
| Jun | 27-JUN-14:00 | 13-JUN-14:00 | 08-JUN-15:00 | 08-JUN-14:00 | 28-JUN-12:00 | 27-JUN-13:00 | 15-JUN-12:00 | 30-JUN-14:00 | 29-JUN-13:00 | 28-JUN-14:00 | 08-JUN-12:00 | 28-JUN-11:00 | 29-JUN-14:00 | 30-JUN-15:00 | 14-JUN-15:09 | 20-JUN-14:00
| Jul | 10-JUL-12:00 | 18-JUL-11:00 | 11-JUL-15:00 | 03-JUL-15:00 | 10-JUL-09:00 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-14:00 | 24-JUL-14:00 | 14-JUL-11:00 | 17-JUL-14:00 | 13-JUL-15:00 | 21-JUL-15:00 | 06-JUL-14:00 | 21-JUL-15:00
| Aug | 21-AUG-13:00 | 31-AUG-13:00 | 01-AUG-15:00 | 17-AUG-13:00 | 08-AUG-11:00 | 04-AUG-14:00 | 15-AUG-11:00 | 09-AUG-14:00 | 01-AUG-14:00 | 07-AUG-14:00 | 04-AUG-15:50 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-14:00 | 15-AUG-13:00
| Sep | 07-SEP-13:00 | 15-SEP-14:00 | 08-SEP-13:00 | 11-SEP-13:00 | 25-SEP-15:09 | 20-SEP-15:00 | 28-SEP-14:00 | 08-SEP-14:00 | 20-SEP-15:09 | 13-SEP-14:00 | 06-SEP-11:00 | 05-SEP-13:00 | 14-SEP-14:00 | 12-SEP-13:00 | 07-SEP-15:09 | 07-SEP-14:00
| Oct | 06-OCT-13:00 | 30-OCT-13:00 | 02-OCT-15:00 | 12-OCT-15:00 | 19-OCT-10:00 | 03-OCT-15:09 | 31-OCT-12:00 | 03-OCT-11:00 | 11-OCT-15:00 | 17-OCT-14:00 | 31-OCT-11:00 | 05-OCT-14:00 | 06-OCT-15:09 | 06-OCT-15:00 | 06-OCT-14:00 | 30-OCT-07:10
| Nov | 01-NOV-11:00 | 27-NOV-12:00 | 13-NOV-15:39 | 22-NOV-15:09 | 20-NOV-12:00 | 10-NOV-12:00 | 14-NOV-12:00 | 03-NOV-13:00 | 08-NOV-16:10 | 03-NOV-10:39 | 02-NOV-14:39 | 10-NOV-13:00 | 02-NOV-14:00 | 21-NOV-11:39 | 09-NOV-11:39 | 27-NOV-10:09
| Dec | 15-DEC-16:10 | 19-DEC-15:09 | 11-DEC-16:10 | 13-DEC-16:10 | 19-DEC-12:00 | 05-DEC-14:00 | 07-DEC-14:00 | 06-DEC-11:39 | 08-DEC-14:00 | 28-DEC-11:39 | 12-DEC-11:39 | 21-DEC-14:30 | 20-DEC-11:09 | 18-DEC-08:09 | 20-DEC-11:09 | 29-DEC-11:09
Source Energy
| Total Source Energy (GJ) | 39982.73 | 40431.05 | 35112.32 | 33837.15 | 25669.5 | 36372.43 | 26665.63 | 37542.95 | 32164.08 | 19495.3 | 38120.29 | 32722.14 | 40087.58 | 36389.19 | 40971.44 | 52501.77
| Total Source Energy (MJ/m2) | 2040.77 | 2063.65 | 1792.18 | 1727.09 | 1310.2 | 1856.49 | 1361.05 | 1916.24 | 1641.69 | 995.06 | 1945.71 | 1670.18 | 2046.12 | 1857.35 | 2091.23 | 2679.76
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93
| Total Building | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93
Emissions
| Carbon Equivalent (kg) | 913432.6458 | 1008220 | 910838.7342 | 821534.0737 | 279280.409 | 926258.5983 | 304294.3706 | 754184.9922 | 1010320 | 260638.013 | 1348590 | 992541.1983 | 962570.8825 | 928274.7909 | 959157.344 | 1007790
| CO2 (kg) | 2122200 | 2546100 | 2159800 | 1909440 | 751667.7356 | 2217300 | 827208.6202 | 1769990 | 2400950 | 678388.6146 | 3204230 | 2378770 | 2345690 | 2257580 | 2361910 | 2691230
| NOX (kg) | 3712.1224 | 3296.563 | 3575.6496 | 3472.9913 | 647.3999 | 3540.9643 | 718.0549 | 3155.0897 | 4007.7821 | 857.1174 | 5414.5399 | 3884.6581 | 3706.0176 | 3569.1681 | 3626.2946 | 2939.1922
| SO2 (kg) | 14063.5174 | 13809.059 | 11692.9471 | 8536.8422 | 6269.1543 | 14372.9908 | 5898.4952 | 8557.4044 | 9906.5953 | 1543.6992 | 15036.3686 | 9349.0773 | 5145.1979 | 5507.188 | 4837.7358 | 10388.7853
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0641 | 0.0391 | 0.0319 | 0.0316 | 0.003 | 0.0272 | 0.003 | 0.0352 | 0.0391 | 0.0067 | 0.0463 | 0.0371 | 0.0388 | 0.0392 | 0.0368 | 0.0378
| Water for Electricity (m3) | 1740.53 | 4710.26 | 86371.6 | 15183.4 | 37824.6 | 71678.7 | 35584.5 | 532.1175 | 10300 | 20382.6 | 3461 | 9719.77 | 3380.05 | 130587 | 3177.54 | 2083.81

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 12514.4 | 638.75 | 638.75
Net Site Energy | 12514.4 | 638.75 | 638.75
Total Source Energy | 39982.73 | 2040.77 | 2040.77
Net Source Energy | 39982.73 | 2040.77 | 2040.77
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 149.34 | 0 | 0 | 0 | 0
Cooling | 4584.75 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3382.14 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 142.2 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1223.22 | 0 | 0 | 0 | 0 | 0
Pumps | 60.8 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 183.8 | 0 | 0 | 0 | 2677.93
Refrigeration | 156.93 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 11827.87 | 686.53 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 9.68 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 266.35 | 15.06 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 15.06 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 15.06 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 80.28 | 15.06 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 12.91 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 13.99 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 13.99 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 13.99 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 16.14 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 16.14 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.5266 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.5266 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.251 | 0.11 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.251 | 0.11 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.251 | 0.11 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.251 | 0.11 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.251 | 0.11 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.251 | 0.11 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.251 | 0.11 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 5.835 | 0.251 | 0.11 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.251 | 0.11 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 5.835 | 0.251 | 0.11 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 36.4 | 36.4 | 5.835 | 0.251 | 0.11 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.251 | 0.11 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
GYM_ZN_1_FLR_2_SKYLIGHT_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_10 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_11 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_12 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_13 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_14 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_15 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_16 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_17 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_18 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_19 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_20 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_21 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_22 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_23 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_24 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_25 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_26 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_27 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_28 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_29 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_3 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_30 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_31 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_32 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_33 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_34 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_35 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_36 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_37 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_38 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_39 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_4 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_40 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_41 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_42 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_43 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_44 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_45 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_46 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_47 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_48 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_49 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_5 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_50 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_51 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_52 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_53 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_54 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_6 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_7 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_8 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_9 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 49.41 | 49.41 | 5.835 | 0.251 | 0.11 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.251 | 0.11 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 5.835 | 0.251 | 0.11 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 5.835 | 0.251 | 0.11 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.251 | 0.11 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.251 | 0.11 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.251 | 0.11 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.251 | 0.11 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2233.52 | 5.83 | 0.249 | 0.107
North Total or Average |  |  | 753.18 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 1480.33 | 5.83 | 0.248 | 0.106
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1433909.28 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 607722.1 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 490687.86 | 331745.83 | 158942.03 | 0.68 | 3.25
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 119857.92 | 81033.93 | 38823.99 | 0.68 | 3.51
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 196275.14 | 132698.33 | 63576.81 | 0.68 | 3.49
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14212.85 | 9609.07 | 4603.78 | 0.68 | 3.65
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 111477.74 | 75368.23 | 36109.51 | 0.68 | 3.51
VAV_OTHER_COOLC | Coil:Cooling:Water | 321199.43 | 214059.64 | 107139.8 | 0.67 | -
VAV_POD_1_COOLC | Coil:Cooling:Water | 274165.66 | 176147.02 | 98018.63 | 0.64 | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 269925.65 | 173291.89 | 96633.77 | 0.64 | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 286886.51 | 184577.99 | 102308.52 | 0.64 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6442.07 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7525.38 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5453.68 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7646.21 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5369.05 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7616.11 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5372.56 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7634.59 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5574.34 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7880.66 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5555.08 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7880.16 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5617.11 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7915.23 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5743.06 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9958.28 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4264.54 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9826.15 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4316.97 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9979.05 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 32466.04 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3131.54 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6573.88 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17166.06 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 36597.03 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13351.8 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9827.16 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11706.16 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19413.33 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11706.16 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19211.35 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11706.16 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 22702.5 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11706.16 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19951.83 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11706.16 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19946.46 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11706.16 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 23601.17 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11630.39 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20126.8 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 765026.92 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 169899.83 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 306010.77 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 22159.12 | 0.8
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 173803.92 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 39967.65 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 25467.1 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 24993.69 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 26804.98 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.83 | 9206.56 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.57 | 663.87 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 13.43 | 22760.41 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.56 | 16058.06 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.4 | 15759.56 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 9.01 | 16901.65 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 13139.79 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 3346.38 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 154117.21 | 266.2129 | 994.8167 | 0 | 0.0045 | 123117.9987 | 65997.3689
February | 141294.3497 | 246.3056 | 929.6931 | 0 | 0.0042 | 115060.0783 | 60730.9181
March | 167838.9148 | 292.1164 | 1100.7161 | 0 | 0.005 | 136225.7659 | 72093.9756
April | 168543.0567 | 295.0336 | 1118.648 | 0 | 0.0051 | 138446.3339 | 72565.9331
May | 209820.6999 | 367.9097 | 1397.4936 | 0 | 0.0064 | 172957.3502 | 90400.069
June | 224425.1004 | 393.8603 | 1497.4608 | 0 | 0.0068 | 185329.7946 | 96726.6116
July | 166594.2061 | 292.5025 | 1112.6424 | 0 | 0.0051 | 137703.7288 | 71815.0732
August | 175376.6712 | 307.8894 | 1171.0371 | 0 | 0.0053 | 144930.7994 | 75597.6738
September | 206050.6713 | 361.5431 | 1374.3037 | 0 | 0.0063 | 170087.4939 | 88800.2174
October | 192908.5707 | 338.0764 | 1283.445 | 0 | 0.0059 | 158842.2716 | 83095.6642
November | 170834.927 | 299.0019 | 1133.5166 | 0 | 0.0052 | 140286.468 | 73548.3281
December | 144399.7349 | 251.6705 | 949.7444 | 0 | 0.0043 | 117541.6285 | 62060.8128
Annual Sum or Average | 2122200 | 3712.1224 | 14063.5174 | 0 | 0.0641 | 1740530 | 913432.6458
Minimum of Months | 141294.3497 | 246.3056 | 929.6931 | 0 | 0.0042 | 115060.0783 | 60730.9181
Maximum of Months | 224425.1004 | 393.8603 | 1497.4608 | 0 | 0.0068 | 185329.7946 | 96726.6116
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 836655000000 | 910145.843 | 06-JAN-12:00 | 220879.908 | 151653.867 | 93554.561 | 0 | 433063.474 | 0 | 5677.649 | 0 | 0 | 0 | 0 | 0 | 5316.386 | 0 | 0
February | 781897000000 | 944120.868 | 23-FEB-11:00 | 220879.908 | 151653.867 | 96789.535 | 0 | 463258.921 | 0 | 6200.768 | 0 | 0 | 0 | 0 | 0 | 5337.868 | 0 | 0
March | 925730000000 | 976067.966 | 13-MAR-14:00 | 220879.908 | 137835.548 | 99841.147 | 0 | 505363.722 | 0 | 6779.076 | 0 | 0 | 0 | 0 | 0 | 5368.566 | 0 | 0
April | 940820000000 | 1024100.519 | 03-APR-13:00 | 220879.908 | 145652.643 | 103379.614 | 0 | 541298.04 | 0 | 7502.398 | 0 | 0 | 0 | 0 | 0 | 5387.917 | 0 | 0
May | 1175340000000 | 1131482.858 | 24-MAY-14:00 | 220879.908 | 137835.548 | 105730.368 | 0 | 652861.584 | 0 | 8656.353 | 0 | 0 | 0 | 0 | 0 | 5519.097 | 0 | 0
June | 1259420000000 | 1210675.593 | 27-JUN-14:00 | 220879.908 | 137835.548 | 107721.107 | 0 | 727450.816 | 0 | 11295.993 | 0 | 0 | 0 | 0 | 0 | 5492.222 | 0 | 0
July | 935773000000 | 927087.594 | 10-JUL-12:00 | 122711.06 | 84617.158 | 84450.289 | 0 | 623786.244 | 0 | 6297.791 | 0 | 0 | 0 | 0 | 0 | 5225.052 | 0 | 0
August | 984885000000 | 995184.781 | 21-AUG-13:00 | 122711.06 | 84617.158 | 89530.435 | 0 | 685583.064 | 0 | 7477.274 | 0 | 0 | 0 | 0 | 0 | 5265.789 | 0 | 0
September | 1155840000000 | 1156047.418 | 07-SEP-13:00 | 220879.908 | 145652.643 | 105201.973 | 0 | 669275.587 | 0 | 9567.085 | 0 | 0 | 0 | 0 | 0 | 5470.221 | 0 | 0
October | 1079420000000 | 1108390.204 | 06-OCT-13:00 | 220879.908 | 145652.643 | 105727.705 | 0 | 621759.715 | 0 | 8943.913 | 0 | 0 | 0 | 0 | 0 | 5426.32 | 0 | 0
November | 953325000000 | 1001841.864 | 01-NOV-11:00 | 220879.908 | 151653.867 | 98322.349 | 0 | 518633.718 | 0 | 6995.148 | 0 | 0 | 0 | 0 | 0 | 5356.874 | 0 | 0
December | 798761000000 | 892095.651 | 15-DEC-16:10 | 220879.908 | 133019.064 | 91368.941 | 0 | 436257.814 | 0 | 5303.185 | 0 | 0 | 0 | 0 | 0 | 5266.739 | 0 | 0
Annual Sum or Average | 11827900000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 781897000000 | 892095.651 |  | 122711.06 | 84617.158 | 84450.289 | 0 | 433063.474 | 0 | 5303.185 | 0 | 0 | 0 | 0 | 0 | 5225.052 | 0 | 0
Maximum of Months | 1259420000000 | 1210675.593 |  | 220879.908 | 151653.867 | 107721.107 | 0 | 727450.816 | 0 | 11295.993 | 0 | 0 | 0 | 0 | 0 | 5519.097 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 295789.6 | 7848.28 | 0 | 303637.89
Cost per Total Building Area ($/m2) | 15.1 | 0.4 | 0 | 15.5
Cost per Net Conditioned Building Area ($/m2) | 15.1 | 0.4 | 0 | 15.5

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 12784.39 | 652.53 | 652.53
Net Site Energy | 12784.39 | 652.53 | 652.53
Total Source Energy | 40431.05 | 2063.65 | 2063.65
Net Source Energy | 40431.05 | 2063.65 | 2063.65
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1759.3 | 0 | 0 | 0 | 0
Cooling | 3274.78 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3382.14 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 142.15 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1150.53 | 0 | 0 | 0 | 0 | 0
Pumps | 43.91 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 250.25 | 0 | 0 | 0 | 2677.93
Refrigeration | 150.12 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 10421.45 | 2362.94 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 9.68 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 266.35 | 15.06 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 15.06 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 15.06 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 80.28 | 15.06 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 12.91 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 13.99 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 13.99 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 13.99 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 16.14 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 16.14 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.5266 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.5266 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.251 | 0.11 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.251 | 0.11 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.251 | 0.11 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.251 | 0.11 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.251 | 0.11 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.251 | 0.11 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.251 | 0.11 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 5.835 | 0.251 | 0.11 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.251 | 0.11 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 5.835 | 0.251 | 0.11 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 36.4 | 36.4 | 5.835 | 0.251 | 0.11 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.251 | 0.11 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
GYM_ZN_1_FLR_2_SKYLIGHT_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_10 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_11 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_12 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_13 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_14 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_15 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_16 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_17 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_18 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_19 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_20 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_21 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_22 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_23 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_24 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_25 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_26 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_27 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_28 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_29 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_3 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_30 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_31 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_32 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_33 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_34 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_35 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_36 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_37 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_38 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_39 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_4 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_40 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_41 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_42 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_43 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_44 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_45 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_46 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_47 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_48 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_49 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_5 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_50 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_51 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_52 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_53 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_54 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_6 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_7 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_8 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_9 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 49.41 | 49.41 | 5.835 | 0.251 | 0.11 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.251 | 0.11 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 5.835 | 0.251 | 0.11 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 5.835 | 0.251 | 0.11 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.251 | 0.11 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.251 | 0.11 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.251 | 0.11 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.251 | 0.11 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2233.52 | 5.83 | 0.249 | 0.107
North Total or Average |  |  | 753.18 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 1480.33 | 5.83 | 0.248 | 0.106
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1438489.65 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 778892.86 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 490687.86 | 331745.83 | 158942.03 | 0.68 | 3.25
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 125433.57 | 84803.53 | 40630.04 | 0.68 | 3.49
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 196275.14 | 132698.33 | 63576.81 | 0.68 | 3.49
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14007.44 | 9470.19 | 4537.24 | 0.68 | 3.65
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 111477.74 | 75368.23 | 36109.51 | 0.68 | 3.51
VAV_OTHER_COOLC | Coil:Cooling:Water | 339064.47 | 225320.78 | 113743.69 | 0.66 | -
VAV_POD_1_COOLC | Coil:Cooling:Water | 281006.96 | 180240.29 | 100766.66 | 0.64 | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 276027.02 | 176894.59 | 99132.44 | 0.64 | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 292706.09 | 188037.31 | 104668.78 | 0.64 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6418.5 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7678.38 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5695.37 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8060.88 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5609.13 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8029.61 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5612.67 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8048.31 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5632.43 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8102.97 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5612.8 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8102.4 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5678.28 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8138.82 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5676.57 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10287.49 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4198.06 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10151.34 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4250.21 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10303.98 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 33327.05 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3341.31 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6931.99 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17245.65 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 37922.91 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13164.77 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10006.65 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12386.14 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20634.73 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12055.18 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20423.47 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12115.32 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 23921.01 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11663.33 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20284.38 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11663.33 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20277.41 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11663.33 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 23937.74 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12351.49 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 21241.69 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 1009940.45 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 221403.55 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 403976.18 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 28830.3 | 0.8
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 229445.01 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 81545.66 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 52122.33 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 51015.91 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 54643.92 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.05 | 9476.02 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.56 | 654.28 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 13.87 | 23508.11 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.87 | 16637.3 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.68 | 16284.13 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 9.3 | 17442.19 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 13181.77 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 4288.92 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 190129.7953 | 237.8145 | 914.1573 | 0 | 0.0026 | 311780.2967 | 74211.5999
February | 169528.6841 | 211.3095 | 804.7821 | 0 | 0.0023 | 274473.298 | 66075.5469
March | 186253.6777 | 240.1597 | 996.2683 | 0 | 0.0028 | 339821.6785 | 73625.8938
April | 188854.8685 | 246.3759 | 1050.2682 | 0 | 0.003 | 358253.934 | 75023.0724
May | 249747.4336 | 327.0011 | 1405.5179 | 0 | 0.004 | 479437.3789 | 99365.6775
June | 293090.0079 | 384.2511 | 1656.4468 | 0 | 0.0047 | 565034.105 | 116674.6476
July | 223792.8455 | 293.522 | 1266.5092 | 0 | 0.0036 | 432022.1922 | 89104.2161
August | 226642.9968 | 297.2126 | 1281.973 | 0 | 0.0036 | 437296.8669 | 90232.8876
September | 241747.8852 | 316.8125 | 1364.4964 | 0 | 0.0038 | 465445.7282 | 96219.7348
October | 216854.2773 | 283.227 | 1210.5122 | 0 | 0.0034 | 412915.7324 | 86187.6219
November | 183400.0833 | 237.3458 | 993.1277 | 0 | 0.0028 | 338754.4216 | 72609.4461
December | 176054.3393 | 221.5312 | 865 | 0 | 0.0025 | 295021.6177 | 68888.0917
Annual Sum or Average | 2546100 | 3296.563 | 13809.059 | 0 | 0.0391 | 4710260 | 1008220
Minimum of Months | 169528.6841 | 211.3095 | 804.7821 | 0 | 0.0023 | 274473.298 | 66075.5469
Maximum of Months | 293090.0079 | 384.2511 | 1656.4468 | 0 | 0.0047 | 565034.105 | 116674.6476
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 689815000000 | 810510.667 | 03-JAN-12:30 | 220879.908 | 151653.867 | 83128.406 | 0 | 345516.611 | 0 | 4054.407 | 0 | 0 | 0 | 0 | 0 | 5277.467 | 0 | 0
February | 607273000000 | 758882.573 | 23-FEB-14:30 | 220879.908 | 145652.643 | 93755.664 | 0 | 289773.382 | 0 | 3472.667 | 0 | 0 | 0 | 0 | 0 | 5348.309 | 0 | 0
March | 751856000000 | 815753.071 | 29-MAR-11:00 | 220879.908 | 151653.867 | 88744.359 | 0 | 344983.177 | 0 | 4179.221 | 0 | 0 | 0 | 0 | 0 | 5312.539 | 0 | 0
April | 792638000000 | 906679.142 | 21-APR-14:00 | 220879.908 | 137835.548 | 99972.231 | 0 | 437100.092 | 0 | 5527.599 | 0 | 0 | 0 | 0 | 0 | 5363.766 | 0 | 0
May | 1060760000000 | 1160060.306 | 18-MAY-13:00 | 220879.908 | 145652.643 | 104070.193 | 0 | 675153.147 | 0 | 8797.194 | 0 | 0 | 0 | 0 | 0 | 5507.222 | 0 | 0
June | 1250140000000 | 1151100.337 | 13-JUN-14:00 | 220879.908 | 137835.548 | 108901.909 | 0 | 669628.686 | 0 | 8283.211 | 0 | 0 | 0 | 0 | 0 | 5571.076 | 0 | 0
July | 955850000000 | 1030737.243 | 18-JUL-11:00 | 122711.06 | 88818.015 | 84927.688 | 0 | 721769.575 | 0 | 7242.106 | 0 | 0 | 0 | 0 | 0 | 5268.799 | 0 | 0
August | 967520000000 | 968442.061 | 31-AUG-13:00 | 122711.06 | 84617.158 | 92562.406 | 0 | 656791.622 | 0 | 6448.228 | 0 | 0 | 0 | 0 | 0 | 5311.587 | 0 | 0
September | 1029800000000 | 1219718.464 | 15-SEP-14:00 | 220879.908 | 137835.548 | 105291.688 | 0 | 740095.221 | 0 | 10104.785 | 0 | 0 | 0 | 0 | 0 | 5511.315 | 0 | 0
October | 913577000000 | 1017678.297 | 30-OCT-13:00 | 220879.908 | 145652.643 | 95126.542 | 0 | 543711.908 | 0 | 6970.922 | 0 | 0 | 0 | 0 | 0 | 5336.374 | 0 | 0
November | 749495000000 | 896670.452 | 27-NOV-12:00 | 220879.908 | 151653.867 | 89626.25 | 0 | 423860.155 | 0 | 5352.325 | 0 | 0 | 0 | 0 | 0 | 5297.948 | 0 | 0
December | 652736000000 | 798593.475 | 19-DEC-15:09 | 220879.908 | 137835.548 | 88744.747 | 0 | 341677.548 | 0 | 4152.777 | 0 | 0 | 0 | 0 | 0 | 5302.947 | 0 | 0
Annual Sum or Average | 10421500000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 607273000000 | 758882.573 |  | 122711.06 | 84617.158 | 83128.406 | 0 | 289773.382 | 0 | 3472.667 | 0 | 0 | 0 | 0 | 0 | 5268.799 | 0 | 0
Maximum of Months | 1250140000000 | 1219718.464 |  | 220879.908 | 151653.867 | 108901.909 | 0 | 740095.221 | 0 | 10104.785 | 0 | 0 | 0 | 0 | 0 | 5571.076 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 343476.08 | 19089.17 | 0 | 362565.25
Cost per Total Building Area ($/m2) | 17.53 | 0.97 | 0 | 18.51
Cost per Net Conditioned Building Area ($/m2) | 17.53 | 0.97 | 0 | 18.51

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 12301.87 | 627.9 | 627.9
Net Site Energy | 12301.87 | 627.9 | 627.9
Total Source Energy | 35112.32 | 1792.18 | 1792.18
Net Source Energy | 35112.32 | 1792.18 | 1792.18
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1260.86 | 0 | 0 | 0 | 0
Cooling | 3248.57 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3382.14 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 142.12 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1221.89 | 0 | 0 | 0 | 0 | 0
Pumps | 44.56 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 219.89 | 0 | 0 | 0 | 2677.93
Refrigeration | 150.62 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 10467.73 | 1834.14 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 9.68 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 266.35 | 15.06 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 15.06 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 15.06 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 80.28 | 15.06 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 12.91 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 13.99 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 13.99 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 13.99 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 16.14 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 16.14 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.5266 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.5266 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.251 | 0.11 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.251 | 0.11 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.251 | 0.11 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.251 | 0.11 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.251 | 0.11 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.251 | 0.11 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.251 | 0.11 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 5.835 | 0.251 | 0.11 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.251 | 0.11 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 5.835 | 0.251 | 0.11 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 36.4 | 36.4 | 5.835 | 0.251 | 0.11 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.251 | 0.11 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
GYM_ZN_1_FLR_2_SKYLIGHT_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_10 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_11 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_12 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_13 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_14 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_15 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_16 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_17 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_18 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_19 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_20 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_21 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_22 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_23 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_24 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_25 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_26 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_27 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_28 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_29 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_3 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_30 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_31 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_32 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_33 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_34 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_35 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_36 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_37 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_38 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_39 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_4 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_40 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_41 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_42 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_43 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_44 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_45 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_46 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_47 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_48 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_49 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_5 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_50 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_51 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_52 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_53 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_54 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_6 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_7 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_8 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_9 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_2_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 49.41 | 49.41 | 5.835 | 0.251 | 0.11 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.251 | 0.11 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 5.835 | 0.251 | 0.11 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 5.835 | 0.251 | 0.11 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.251 | 0.11 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.251 | 0.11 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.251 | 0.11 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.251 | 0.11 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2233.52 | 5.83 | 0.249 | 0.107
North Total or Average |  |  | 753.18 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 1480.33 | 5.83 | 0.248 | 0.106
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1255650.73 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 727812.25 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 490687.86 | 331745.83 | 158942.03 | 0.68 | 3.25
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 131446.55 | 88868.81 | 42577.74 | 0.68 | 3.49
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 196275.14 | 132698.33 | 63576.81 | 0.68 | 3.49
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12707.31 | 8591.2 | 4116.11 | 0.68 | 3.65
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 111477.74 | 75368.23 | 36109.51 | 0.68 | 3.51
VAV_OTHER_COOLC | Coil:Cooling:Water | 352151.92 | 230687.74 | 121464.18 | 0.66 | -
VAV_POD_1_COOLC | Coil:Cooling:Water | 245897.15 | 158004.1 | 87893.05 | 0.64 | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 241515.14 | 155067.91 | 86447.23 | 0.64 | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 255825.28 | 164581.23 | 91244.04 | 0.64 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6189.6 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8497.37 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5881.19 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8855.21 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5798.02 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8824.9 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5801.75 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8843.32 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5657.66 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8726.48 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5636.41 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8725.27 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5700.27 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8761.25 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4698.15 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10723.61 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3259.16 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10570.1 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3316.8 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10730.98 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 35369.05 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3313.02 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7722.74 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14022.91 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 39302.81 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11568.94 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9832.35 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12995.87 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 23335.59 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12676.62 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 23136.6 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12734.54 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 26625.41 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11247.38 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 21911.85 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11247.38 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 21908.35 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11247.38 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 25595.81 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12523.62 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 23548.99 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 852081.84 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 195742.5 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 340832.73 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 22066.31 | 0.8
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 193581.64 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 63139.07 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 41886.55 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 41060.01 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 43842.35 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.29 | 9930.28 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.51 | 593.55 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 14.58 | 24702.41 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1017.59 | 9.67 | 16639.73 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1017.59 | 9.48 | 16311.38 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1017.59 | 10.12 | 17416.69 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 11506.3 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 4007.64 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 147040.8075 | 232.3642 | 715.9906 | 0 | 0.002 | 5288200 | 60891.3712
February | 133156.8641 | 211.7191 | 657.755 | 0 | 0.0018 | 4858160 | 55272.8421
March | 164848.4297 | 271.6387 | 883.2435 | 0 | 0.0024 | 6524140 | 69391.584
April | 163333.1855 | 272.5783 | 899.984 | 0 | 0.0024 | 6647970 | 69101.2492
May | 199858.8572 | 335.672 | 1116.7103 | 0 | 0.003 | 8248980 | 84770.329
June | 255080.8062 | 429.4216 | 1432.5101 | 0 | 0.0039 | 10581800 | 108294.0815
July | 201936.9881 | 340.1471 | 1135.446 | 0 | 0.0031 | 8387430 | 85751.3555
August | 204130.728 | 343.7643 | 1147.2172 | 0 | 0.0031 | 8474370 | 86675.0343
September | 218199.1891 | 367.1301 | 1223.9229 | 0 | 0.0033 | 9040980 | 92615.6028
October | 176604.7325 | 295.4514 | 978.3563 | 0 | 0.0027 | 7226920 | 74789.3455
November | 149452.778 | 245.9873 | 798.7125 | 0 | 0.0022 | 5899730 | 62882.3609
December | 146151.9627 | 229.7757 | 703.0986 | 0 | 0.002 | 5192920 | 60403.5781
Annual Sum or Average | 2159800 | 3575.6496 | 11692.9471 | 0 | 0.0319 | 86371600 | 910838.7342
Minimum of Months | 133156.8641 | 211.7191 | 657.755 | 0 | 0.0018 | 4858160 | 55272.8421
Maximum of Months | 255080.8062 | 429.4216 | 1432.5101 | 0 | 0.0039 | 10581800 | 108294.0815
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 640899000000 | 621384.765 | 26-JAN-15:00 | 220879.908 | 137835.548 | 85055.127 | 0 | 170563.636 | 0 | 1985.336 | 0 | 0 | 0 | 0 | 0 | 5065.212 | 0 | 0
February | 588780000000 | 697250.5 | 28-FEB-15:00 | 220879.908 | 137835.548 | 92071.174 | 0 | 238443.056 | 0 | 2853.088 | 0 | 0 | 0 | 0 | 0 | 5167.727 | 0 | 0
March | 790687000000 | 869453.063 | 17-MAR-15:00 | 220879.908 | 133019.064 | 98298.198 | 0 | 407630.838 | 0 | 4462.698 | 0 | 0 | 0 | 0 | 0 | 5162.357 | 0 | 0
April | 805695000000 | 898200.523 | 26-APR-14:00 | 220879.908 | 137835.548 | 103039.179 | 0 | 425433.08 | 0 | 5580.464 | 0 | 0 | 0 | 0 | 0 | 5432.345 | 0 | 0
May | 999728000000 | 1065941.188 | 30-MAY-15:00 | 220879.908 | 133019.064 | 111833.815 | 0 | 585408.672 | 0 | 9504.266 | 0 | 0 | 0 | 0 | 0 | 5295.464 | 0 | 0
June | 1282450000000 | 1305887.08 | 08-JUN-15:00 | 220879.908 | 133019.064 | 118959.088 | 0 | 817641.245 | 0 | 10071.374 | 0 | 0 | 0 | 0 | 0 | 5316.402 | 0 | 0
July | 1016510000000 | 1137967.325 | 11-JUL-15:00 | 122711.06 | 73183.824 | 112762.41 | 0 | 814154.521 | 0 | 10023.096 | 0 | 0 | 0 | 0 | 0 | 5132.415 | 0 | 0
August | 1027040000000 | 1100419.623 | 01-AUG-15:00 | 122711.06 | 73183.824 | 113408.282 | 0 | 775881.772 | 0 | 10151.277 | 0 | 0 | 0 | 0 | 0 | 5083.409 | 0 | 0
September | 1095710000000 | 1188017.385 | 08-SEP-13:00 | 220879.908 | 145652.643 | 114155.37 | 0 | 691686.674 | 0 | 10079.42 | 0 | 0 | 0 | 0 | 0 | 5563.369 | 0 | 0
October | 875861000000 | 907488.645 | 02-OCT-15:00 | 220879.908 | 133019.064 | 100380.595 | 0 | 442968.485 | 0 | 5030.773 | 0 | 0 | 0 | 0 | 0 | 5209.821 | 0 | 0
November | 715013000000 | 793908.532 | 13-NOV-15:39 | 220879.908 | 137835.548 | 96578.138 | 0 | 329382.534 | 0 | 3906.776 | 0 | 0 | 0 | 0 | 0 | 5325.629 | 0 | 0
December | 629351000000 | 601139.444 | 11-DEC-16:10 | 220879.908 | 133019.064 | 79343.174 | 0 | 161597.518 | 0 | 1450.064 | 0 | 0 | 0 | 0 | 0 | 4849.716 | 0 | 0
Annual Sum or Average | 10467700000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 588780000000 | 601139.444 |  | 122711.06 | 73183.824 | 79343.174 | 0 | 161597.518 | 0 | 1450.064 | 0 | 0 | 0 | 0 | 0 | 4849.716 | 0 | 0
Maximum of Months | 1282450000000 | 1305887.08 |  | 220879.908 | 145652.643 | 118959.088 | 0 | 817641.245 | 0 | 10151.277 | 0 | 0 | 0 | 0 | 0 | 5563.369 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 258677.67 | 15184.86 | 0 | 273862.54
Cost per Total Building Area ($/m2) | 13.2 | 0.78 | 0 | 13.98
Cost per Net Conditioned Building Area ($/m2) | 13.2 | 0.78 | 0 | 13.98

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 12771.64 | 651.88 | 651.88
Net Site Energy | 12771.64 | 651.88 | 651.88
Total Source Energy | 33837.15 | 1727.09 | 1727.09
Net Source Energy | 33837.15 | 1727.09 | 1727.09
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 3354.29 | 0 | 0 | 0 | 0
Cooling | 1687.12 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3382.14 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 142.1 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1093.93 | 0 | 0 | 0 | 0 | 0
Pumps | 27.7 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 309.33 | 0 | 0 | 0 | 2677.93
Refrigeration | 143.82 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8754.63 | 4017.01 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 9.68 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 266.35 | 15.06 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 15.06 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 15.06 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 80.28 | 15.06 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 12.91 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 13.99 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 13.99 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 13.99 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 16.14 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 16.14 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.5266 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.5266 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.252 | 0.162 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.252 | 0.162 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.252 | 0.162 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 72.8 | 72.8 | 3.241 | 0.252 | 0.162 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.252 | 0.162 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 72.8 | 72.8 | 3.241 | 0.252 | 0.162 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.252 | 0.162 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.252 | 0.162 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.252 | 0.162 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.252 | 0.162 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 36.4 | 36.4 | 3.241 | 0.252 | 0.162 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.252 | 0.162 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
GYM_ZN_1_FLR_2_SKYLIGHT_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_10 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_11 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_12 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_13 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_14 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_15 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_16 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_17 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_18 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_19 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_20 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_21 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_22 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_23 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_24 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_25 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_26 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_27 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_28 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_29 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_3 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_30 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_31 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_32 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_33 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_34 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_35 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_36 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_37 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_38 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_39 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_4 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_40 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_41 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_42 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_43 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_44 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_45 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_46 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_47 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_48 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_49 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_5 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_50 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_51 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_52 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_53 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_54 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_6 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_7 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_8 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_9 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 49.41 | 49.41 | 3.241 | 0.252 | 0.162 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.252 | 0.162 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.252 | 0.162 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.252 | 0.162 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 3.241 | 0.252 | 0.162 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 3.241 | 0.252 | 0.162 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 3.241 | 0.252 | 0.162 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 3.241 | 0.252 | 0.162 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.252 | 0.162 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 19.6 | 19.6 | 3.241 | 0.252 | 0.162 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.252 | 0.162 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 19.6 | 19.6 | 3.241 | 0.252 | 0.162 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2233.52 | 3.22 | 0.252 | 0.157
North Total or Average |  |  | 753.18 | 3.24 | 0.252 | 0.162
Non-North Total or Average |  |  | 1480.33 | 3.21 | 0.251 | 0.155
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1253003.77 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 768592.3 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 490687.86 | 331745.83 | 158942.03 | 0.68 | 3.25
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 121716.51 | 82290.49 | 39426.02 | 0.68 | 3.51
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 196275.14 | 132698.33 | 63576.81 | 0.68 | 3.49
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13444.57 | 9089.64 | 4354.92 | 0.68 | 3.65
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 111477.74 | 75368.23 | 36109.51 | 0.68 | 3.51
VAV_OTHER_COOLC | Coil:Cooling:Water | 293708.94 | 191990.82 | 101718.12 | 0.65 | -
VAV_POD_1_COOLC | Coil:Cooling:Water | 254787.46 | 160313.26 | 94474.19 | 0.63 | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 250622.33 | 157555.44 | 93066.89 | 0.63 | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 267373.53 | 168527.58 | 98845.95 | 0.63 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6207.31 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7017.33 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4590.18 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6932.96 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4516.91 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6904.35 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4520.43 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6922.52 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4383.11 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6782.16 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4362.62 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6780.47 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4416.97 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6815.44 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4869.24 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9439.86 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3402.84 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9297.88 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3453.94 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9452.42 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 31207.68 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2857.29 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6545.97 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13261.24 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 33683.17 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12823.85 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9655.92 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11279.57 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19415.74 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11279.57 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19220.07 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11279.57 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 22726.65 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11279.57 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 18402.22 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11279.57 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 18395.77 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11279.57 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 22051.69 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10755.8 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19910.38 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 1089465.52 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 232186.06 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 435786.21 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 29850.73 | 0.8
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 247512.05 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 88682.73 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 56101.3 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 54986.73 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 59295.77 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.9 | 9349.32 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.54 | 627.99 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 13.02 | 22057.49 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.24 | 15450.13 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.07 | 15143.18 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.7 | 16329.88 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 11482.05 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 4232.2 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 169968.6138 | 279.066 | 612.4407 | 0 | 0.0023 | 1088970 | 70350.7277
February | 153408.8539 | 251.9417 | 553.0884 | 0 | 0.0021 | 983439.3062 | 63502.5424
March | 152120.1357 | 272.5399 | 659.7906 | 0 | 0.0025 | 1173450 | 65066.8406
April | 142340.7142 | 266.2165 | 672.2655 | 0 | 0.0025 | 1195750 | 61917.982
May | 166186.8476 | 316.4001 | 812.2661 | 0 | 0.003 | 1444820 | 72806.7814
June | 198054.8807 | 379.6477 | 980.6471 | 0 | 0.0036 | 1744350 | 87005.9957
July | 145379.9591 | 279.0335 | 721.5851 | 0 | 0.0026 | 1283540 | 63898.7818
August | 152080.2174 | 291.8438 | 754.5974 | 0 | 0.0028 | 1342260 | 66839.1462
September | 177182.3211 | 339.4808 | 876.531 | 0 | 0.0032 | 1559150 | 77822.1618
October | 146481.3999 | 273.3166 | 688.6641 | 0 | 0.0025 | 1224910 | 63659.687
November | 146624.3554 | 257.0605 | 608.3402 | 0 | 0.0023 | 1081880 | 62195.8857
December | 159607.2531 | 266.444 | 596.6259 | 0 | 0.0023 | 1060910 | 66467.5413
Annual Sum or Average | 1909440 | 3472.9913 | 8536.8422 | 0 | 0.0316 | 15183400 | 821534.0737
Minimum of Months | 142340.7142 | 251.9417 | 553.0884 | 0 | 0.0021 | 983439.3062 | 61917.982
Maximum of Months | 198054.8807 | 379.6477 | 980.6471 | 0 | 0.0036 | 1744350 | 87005.9957
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 627891000000 | 505761.774 | 23-JAN-16:19 | 220879.908 | 133019.064 | 78233.016 | 0 | 67354.759 | 0 | 1660.06 | 0 | 0 | 0 | 0 | 0 | 4614.966 | 0 | 0
February | 567042000000 | 488508.701 | 17-FEB-14:00 | 220879.908 | 145652.643 | 77084.021 | 0 | 38315.773 | 0 | 1621.71 | 0 | 0 | 0 | 0 | 0 | 4954.647 | 0 | 0
March | 676599000000 | 637114.82 | 28-MAR-15:00 | 220879.908 | 133019.064 | 84739.127 | 0 | 191986.626 | 0 | 1611.213 | 0 | 0 | 0 | 0 | 0 | 4878.882 | 0 | 0
April | 689459000000 | 776317.36 | 14-APR-15:00 | 220879.908 | 133019.064 | 89817.802 | 0 | 324193.985 | 0 | 3314.576 | 0 | 0 | 0 | 0 | 0 | 5092.024 | 0 | 0
May | 833070000000 | 942809.929 | 31-MAY-15:00 | 220879.908 | 133019.064 | 97961.575 | 0 | 479688.648 | 0 | 5898.614 | 0 | 0 | 0 | 0 | 0 | 5362.12 | 0 | 0
June | 1005780000000 | 1048926.073 | 08-JUN-14:00 | 220879.908 | 137835.548 | 103531.062 | 0 | 573100.308 | 0 | 8171.746 | 0 | 0 | 0 | 0 | 0 | 5407.502 | 0 | 0
July | 740079000000 | 947274.169 | 03-JUL-15:00 | 122711.06 | 73183.824 | 94663.849 | 0 | 644628.083 | 0 | 6783.312 | 0 | 0 | 0 | 0 | 0 | 5304.041 | 0 | 0
August | 773937000000 | 867432.835 | 17-AUG-13:00 | 122711.06 | 84617.158 | 84283.038 | 0 | 565151.454 | 0 | 5430.411 | 0 | 0 | 0 | 0 | 0 | 5239.714 | 0 | 0
September | 898992000000 | 1013953.451 | 11-SEP-13:00 | 220879.908 | 145652.643 | 104261.613 | 0 | 530094.76 | 0 | 7657.487 | 0 | 0 | 0 | 0 | 0 | 5407.04 | 0 | 0
October | 706273000000 | 844444.556 | 12-OCT-15:00 | 220879.908 | 133019.064 | 90216.705 | 0 | 391526.228 | 0 | 3583.109 | 0 | 0 | 0 | 0 | 0 | 5219.542 | 0 | 0
November | 623804000000 | 571132.605 | 22-NOV-15:09 | 220879.908 | 137835.548 | 86267.596 | 0 | 119024.038 | 0 | 2035.983 | 0 | 0 | 0 | 0 | 0 | 5089.533 | 0 | 0
December | 611709000000 | 497381.71 | 13-DEC-16:10 | 220879.908 | 133019.064 | 73546.388 | 0 | 64562.716 | 0 | 686.732 | 0 | 0 | 0 | 0 | 0 | 4686.902 | 0 | 0
Annual Sum or Average | 8754630000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 567042000000 | 488508.701 |  | 122711.06 | 73183.824 | 73546.388 | 0 | 38315.773 | 0 | 686.732 | 0 | 0 | 0 | 0 | 0 | 4614.966 | 0 | 0
Maximum of Months | 1005780000000 | 1048926.073 |  | 220879.908 | 145652.643 | 104261.613 | 0 | 644628.083 | 0 | 8171.746 | 0 | 0 | 0 | 0 | 0 | 5407.502 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 230926.32 | 39056.54 | 0 | 269982.87
Cost per Total Building Area ($/m2) | 11.79 | 1.99 | 0 | 13.78
Cost per Net Conditioned Building Area ($/m2) | 11.79 | 1.99 | 0 | 13.78

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 9281.4 | 473.73 | 473.73
Net Site Energy | 9281.4 | 473.73 | 473.73
Total Source Energy | 25669.5 | 1310.2 | 1310.2
Net Source Energy | 25669.5 | 1310.2 | 1310.2
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 883.23 | 0 | 0 | 0 | 0
Cooling | 749.69 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3382.14 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 141.99 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1038.5 | 0 | 0 | 0 | 0 | 0
Pumps | 21.39 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 289.31 | 0 | 0 | 0 | 2677.93
Refrigeration | 143.94 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7755.47 | 1525.94 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 9.68 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 266.35 | 15.06 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 15.06 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 15.06 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 80.28 | 15.06 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 12.91 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 13.99 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 13.99 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 13.99 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 16.14 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 16.14 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.5266 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.5266 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.252 | 0.162 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.252 | 0.162 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.252 | 0.162 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 72.8 | 72.8 | 3.241 | 0.252 | 0.162 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.252 | 0.162 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 72.8 | 72.8 | 3.241 | 0.252 | 0.162 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.252 | 0.162 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.252 | 0.162 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.252 | 0.162 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.252 | 0.162 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 36.4 | 36.4 | 3.241 | 0.252 | 0.162 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.252 | 0.162 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
GYM_ZN_1_FLR_2_SKYLIGHT_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_10 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_11 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_12 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_13 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_14 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_15 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_16 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_17 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_18 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_19 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_20 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_21 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_22 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_23 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_24 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_25 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_26 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_27 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_28 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_29 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_3 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_30 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_31 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_32 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_33 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_34 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_35 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_36 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_37 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_38 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_39 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_4 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_40 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_41 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_42 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_43 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_44 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_45 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_46 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_47 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_48 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_49 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_5 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_50 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_51 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_52 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_53 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_54 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_6 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_7 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_8 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_9 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 49.41 | 49.41 | 3.241 | 0.252 | 0.162 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.252 | 0.162 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.252 | 0.162 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.252 | 0.162 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 3.241 | 0.252 | 0.162 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 3.241 | 0.252 | 0.162 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 3.241 | 0.252 | 0.162 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 3.241 | 0.252 | 0.162 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.252 | 0.162 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 19.6 | 19.6 | 3.241 | 0.252 | 0.162 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.252 | 0.162 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 19.6 | 19.6 | 3.241 | 0.252 | 0.162 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2233.52 | 3.22 | 0.252 | 0.157
North Total or Average |  |  | 753.18 | 3.24 | 0.252 | 0.162
Non-North Total or Average |  |  | 1480.33 | 3.21 | 0.251 | 0.155
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 829443.93 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 528038.62 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 490687.86 | 331745.83 | 158942.03 | 0.68 | 3.25
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 99740.83 | 67433.1 | 32307.73 | 0.68 | 3.51
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 196275.14 | 132698.33 | 63576.81 | 0.68 | 3.49
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11758.97 | 7950.04 | 3808.93 | 0.68 | 3.65
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 111477.74 | 75368.23 | 36109.51 | 0.68 | 3.51
VAV_OTHER_COOLC | Coil:Cooling:Water | 264973.19 | 180388.09 | 84585.09 | 0.68 | -
VAV_POD_1_COOLC | Coil:Cooling:Water | 166766.21 | 111709.91 | 55056.3 | 0.67 | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 162212.92 | 108586.37 | 53626.55 | 0.67 | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 177883.4 | 119281 | 58602.4 | 0.67 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6419.26 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6419.26 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4280.21 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6296.25 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4212.64 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6269.45 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4215.84 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6286.88 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3834.62 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 5857.55 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3812.97 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 5854.4 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3860.61 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 5887.6 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4588.71 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8247.42 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3126.2 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8098.26 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3165.36 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8240.49 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 26219.44 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2834.12 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 5637.73 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11686.74 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 28790.14 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12611.61 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8591.56 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11664.71 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 17578.58 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11664.71 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 17380.51 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11664.71 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20851.11 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11664.71 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14746.54 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11664.71 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14733.57 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11664.71 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 18331.93 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10390.08 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 17367.08 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 795660.69 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 157065.24 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 318264.28 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 19067.42 | 0.8
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 180763.5 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 38216.95 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 24765.89 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 24224.06 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 26275.39 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.02 | 7661.32 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.47 | 549.25 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 11.2 | 18979.24 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.26 | 13618.17 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.1 | 13320.23 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.7 | 14448.21 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 7600.71 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2907.61 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 68338.8252 | 59.1566 | 516.7602 | 0 | 0.0003 | 3117650 | 25228.7972
February | 61306.1784 | 53.0776 | 462.0215 | 0 | 0.0002 | 2787400 | 22627.7807
March | 69236.2136 | 59.8165 | 544.4582 | 0 | 0.0003 | 3284840 | 25623.8905
April | 61167.5419 | 52.6942 | 508.0951 | 0 | 0.0002 | 3065560 | 22720.3671
May | 65675.3548 | 56.4733 | 564.1981 | 0 | 0.0003 | 3404120 | 24451.6967
June | 66119.6217 | 56.7816 | 581.1932 | 0 | 0.0003 | 3506710 | 24657.3097
July | 45724.7164 | 39.2218 | 410.0163 | 0 | 0.0002 | 2473920 | 17076.3446
August | 52025.3121 | 44.6199 | 467.6643 | 0 | 0.0002 | 2821750 | 19432.8732
September | 66798.1835 | 57.3115 | 596.6158 | 0 | 0.0003 | 3599800 | 24939.2149
October | 66144.8247 | 56.8219 | 578.0775 | 0 | 0.0003 | 3487900 | 24656.5267
November | 64158.8424 | 55.2801 | 531.3406 | 0 | 0.0003 | 3205800 | 23826.5823
December | 64972.121 | 56.1449 | 508.7136 | 0 | 0.0002 | 3069170 | 24039.0255
Annual Sum or Average | 751667.7356 | 647.3999 | 6269.1543 | 0 | 0.003 | 37824600 | 279280.409
Minimum of Months | 45724.7164 | 39.2218 | 410.0163 | 0 | 0.0002 | 2473920 | 17076.3446
Maximum of Months | 69236.2136 | 59.8165 | 596.6158 | 0 | 0.0003 | 3599800 | 25623.8905
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 639235000000 | 684601.698 | 26-JAN-12:00 | 220879.908 | 151653.867 | 87698.995 | 0 | 215650.591 | 0 | 3516.69 | 0 | 0 | 0 | 0 | 0 | 5201.647 | 0 | 0
February | 571522000000 | 649479.36 | 13-FEB-11:00 | 220879.908 | 151653.867 | 84673.263 | 0 | 184419.517 | 0 | 2680.572 | 0 | 0 | 0 | 0 | 0 | 5172.233 | 0 | 0
March | 673515000000 | 634597.966 | 30-MAR-11:00 | 220879.908 | 151653.867 | 86862.197 | 0 | 167323.29 | 0 | 2769.97 | 0 | 0 | 0 | 0 | 0 | 5108.734 | 0 | 0
April | 628555000000 | 728455.42 | 11-APR-15:00 | 220879.908 | 133019.064 | 85261.951 | 0 | 280822.348 | 0 | 3397.5 | 0 | 0 | 0 | 0 | 0 | 5074.649 | 0 | 0
May | 697973000000 | 726386.924 | 30-MAY-11:09 | 220879.908 | 151653.867 | 86886.661 | 0 | 255856.657 | 0 | 5904.511 | 0 | 0 | 0 | 0 | 0 | 5205.32 | 0 | 0
June | 719007000000 | 728870.42 | 28-JUN-12:00 | 220879.908 | 145652.643 | 91461.297 | 0 | 259497.683 | 0 | 6153.707 | 0 | 0 | 0 | 0 | 0 | 5225.183 | 0 | 0
July | 507246000000 | 494199.307 | 10-JUL-09:00 | 122711.06 | 88818.015 | 72381.436 | 0 | 203281.645 | 0 | 2049.867 | 0 | 0 | 0 | 0 | 0 | 4957.284 | 0 | 0
August | 578566000000 | 612150.328 | 08-AUG-11:00 | 122711.06 | 88818.015 | 75760.583 | 0 | 316085.984 | 0 | 3770.433 | 0 | 0 | 0 | 0 | 0 | 5004.252 | 0 | 0
September | 738094000000 | 835801.486 | 25-SEP-15:09 | 220879.908 | 133019.064 | 103009.646 | 0 | 367038.926 | 0 | 6543.554 | 0 | 0 | 0 | 0 | 0 | 5310.389 | 0 | 0
October | 715150000000 | 775918.201 | 19-OCT-10:00 | 220879.908 | 151653.867 | 93436.186 | 0 | 298865.815 | 0 | 5750.098 | 0 | 0 | 0 | 0 | 0 | 5332.327 | 0 | 0
November | 657310000000 | 689108.467 | 20-NOV-12:00 | 220879.908 | 151653.867 | 87638.678 | 0 | 217244.448 | 0 | 6446.222 | 0 | 0 | 0 | 0 | 0 | 5245.345 | 0 | 0
December | 629296000000 | 696188.07 | 19-DEC-12:00 | 220879.908 | 151653.867 | 87532.538 | 0 | 227284.42 | 0 | 3621.693 | 0 | 0 | 0 | 0 | 0 | 5215.645 | 0 | 0
Annual Sum or Average | 7755470000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 507246000000 | 494199.307 |  | 122711.06 | 88818.015 | 72381.436 | 0 | 167323.29 | 0 | 2049.867 | 0 | 0 | 0 | 0 | 0 | 4957.284 | 0 | 0
Maximum of Months | 738094000000 | 835801.486 |  | 220879.908 | 151653.867 | 103009.646 | 0 | 367038.926 | 0 | 6543.554 | 0 | 0 | 0 | 0 | 0 | 5332.327 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 286681.48 | 13053.11 | 0 | 299734.59
Cost per Total Building Area ($/m2) | 14.63 | 0.67 | 0 | 15.3
Cost per Net Conditioned Building Area ($/m2) | 14.63 | 0.67 | 0 | 15.3

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 11903.47 | 607.57 | 607.57
Net Site Energy | 11903.47 | 607.57 | 607.57
Total Source Energy | 36372.43 | 1856.49 | 1856.49
Net Source Energy | 36372.43 | 1856.49 | 1856.49
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1880.8 | 0 | 0 | 0 | 0
Cooling | 2272.61 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3382.14 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 141.96 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1152.39 | 0 | 0 | 0 | 0 | 0
Pumps | 32.9 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 263.31 | 0 | 0 | 0 | 2677.93
Refrigeration | 146.15 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 9405.97 | 2497.5 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 9.68 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 266.35 | 15.06 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 15.06 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 15.06 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 80.28 | 15.06 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 12.91 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 13.99 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 13.99 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 13.99 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 16.14 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 16.14 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.5266 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.5266 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.252 | 0.162 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.252 | 0.162 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.252 | 0.162 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 72.8 | 72.8 | 3.241 | 0.252 | 0.162 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.252 | 0.162 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 72.8 | 72.8 | 3.241 | 0.252 | 0.162 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.252 | 0.162 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.252 | 0.162 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.252 | 0.162 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.252 | 0.162 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 36.4 | 36.4 | 3.241 | 0.252 | 0.162 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.252 | 0.162 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
GYM_ZN_1_FLR_2_SKYLIGHT_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_10 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_11 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_12 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_13 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_14 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_15 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_16 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_17 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_18 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_19 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_20 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_21 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_22 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_23 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_24 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_25 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_26 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_27 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_28 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_29 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_3 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_30 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_31 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_32 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_33 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_34 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_35 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_36 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_37 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_38 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_39 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_4 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_40 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_41 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_42 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_43 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_44 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_45 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_46 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_47 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_48 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_49 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_5 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_50 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_51 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_52 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_53 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_54 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_6 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_7 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_8 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_9 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_2_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 49.41 | 49.41 | 3.241 | 0.252 | 0.162 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.252 | 0.162 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.252 | 0.162 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.252 | 0.162 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 3.241 | 0.252 | 0.162 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 3.241 | 0.252 | 0.162 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 3.241 | 0.252 | 0.162 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 3.241 | 0.252 | 0.162 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.252 | 0.162 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 19.6 | 19.6 | 3.241 | 0.252 | 0.162 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.252 | 0.162 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 19.6 | 19.6 | 3.241 | 0.252 | 0.162 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2233.52 | 3.22 | 0.252 | 0.157
North Total or Average |  |  | 753.18 | 3.24 | 0.252 | 0.162
Non-North Total or Average |  |  | 1480.33 | 3.21 | 0.251 | 0.155
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 950665.83 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 677460.9 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 490687.86 | 331745.83 | 158942.03 | 0.68 | 3.25
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 115625.26 | 78172.3 | 37452.96 | 0.68 | 3.51
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 196275.14 | 132698.33 | 63576.81 | 0.68 | 3.49
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11067.7 | 7482.69 | 3585.02 | 0.68 | 3.65
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 111477.74 | 75368.23 | 36109.51 | 0.68 | 3.51
VAV_OTHER_COOLC | Coil:Cooling:Water | 283327.95 | 184934.1 | 98393.85 | 0.65 | -
VAV_POD_1_COOLC | Coil:Cooling:Water | 201804.5 | 129059.32 | 72745.18 | 0.64 | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 198337.52 | 126719.74 | 71617.78 | 0.64 | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 211589.5 | 135524.68 | 76064.82 | 0.64 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5953.79 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7068.87 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4542.01 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7358.4 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4469.38 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7329.35 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4473.31 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7347.33 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4324.06 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7190.74 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4300.23 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7187.45 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4351.55 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7222.08 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3740.57 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9302.24 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2310.51 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9135.05 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2363.95 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9295.11 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 31022.07 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2282.72 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6536.66 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10203.26 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 32721.52 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11091.99 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8988.12 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10818.89 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19887.52 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10818.89 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19677.44 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10818.89 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 23174.33 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10818.89 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 18767.27 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10818.89 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 18752.29 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10818.89 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 22412.77 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9451.48 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20100.81 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 921122.77 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 193999.88 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 368449.11 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 20776.37 | 0.8
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 209266.82 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 67384.99 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 45111.62 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 44201.88 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 47688.96 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.66 | 8881.44 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.45 | 516.97 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 12.74 | 21591.48 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.53 | 16004.78 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.36 | 15682.02 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 9.02 | 16919.18 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8711.54 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 3730.39 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 172721.1875 | 257.9997 | 952.017 | 0 | 0.0019 | 4747090 | 70299.4197
February | 143168.6679 | 222.8231 | 873.4111 | 0 | 0.0017 | 4355520 | 59203.2329
March | 167521.7095 | 262.2526 | 1036.3336 | 0 | 0.002 | 5168040 | 69432.4619
April | 163510.7132 | 264.2764 | 1089.5627 | 0 | 0.0021 | 5433810 | 68633.024
May | 200809.9348 | 326.8172 | 1359.3076 | 0 | 0.0026 | 6779150 | 84523.6595
June | 256452.0892 | 418.8354 | 1749.6878 | 0 | 0.0033 | 8726110 | 108096.0503
July | 198400.8372 | 324.2499 | 1355.7219 | 0 | 0.0025 | 6761320 | 83650.316
August | 206316.3695 | 337.1467 | 1409.4376 | 0 | 0.0026 | 7029210 | 86983.5584
September | 214170.7695 | 349.5941 | 1459.4506 | 0 | 0.0027 | 7278620 | 90254.7016
October | 178104.1641 | 288.4519 | 1192.3399 | 0 | 0.0022 | 5946400 | 74819.7548
November | 153833.7706 | 242.1466 | 964.085 | 0 | 0.0018 | 4807800 | 63896.6789
December | 162294.3831 | 246.3708 | 931.636 | 0 | 0.0018 | 4645630 | 66465.7403
Annual Sum or Average | 2217300 | 3540.9643 | 14372.9908 | 0 | 0.0272 | 71678700 | 926258.5983
Minimum of Months | 143168.6679 | 222.8231 | 873.4111 | 0 | 0.0017 | 4355520 | 59203.2329
Maximum of Months | 256452.0892 | 418.8354 | 1749.6878 | 0 | 0.0033 | 8726110 | 108096.0503
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 622932000000 | 502821.68 | 18-JAN-14:00 | 220879.908 | 145652.643 | 79305.365 | 0 | 50938.196 | 0 | 1125.768 | 0 | 0 | 0 | 0 | 0 | 4919.8 | 0 | 0
February | 571549000000 | 551634.823 | 08-FEB-15:00 | 220879.908 | 137835.548 | 83699.861 | 0 | 102705.616 | 0 | 1560.376 | 0 | 0 | 0 | 0 | 0 | 4953.514 | 0 | 0
March | 678171000000 | 638169.437 | 31-MAR-15:00 | 220879.908 | 133019.064 | 82641.781 | 0 | 194932.829 | 0 | 1822.635 | 0 | 0 | 0 | 0 | 0 | 4873.221 | 0 | 0
April | 713047000000 | 883384.428 | 21-APR-15:09 | 220879.908 | 133019.064 | 103231.978 | 0 | 414145.927 | 0 | 6871.252 | 0 | 0 | 0 | 0 | 0 | 5236.299 | 0 | 0
May | 889588000000 | 1009221.414 | 31-MAY-15:00 | 220879.908 | 133019.064 | 112873.742 | 0 | 529707.901 | 0 | 7476.428 | 0 | 0 | 0 | 0 | 0 | 5264.371 | 0 | 0
June | 1145080000000 | 1210939.294 | 27-JUN-13:00 | 220879.908 | 145652.643 | 116837.859 | 0 | 713948.347 | 0 | 8070.887 | 0 | 0 | 0 | 0 | 0 | 5549.65 | 0 | 0
July | 887247000000 | 1000439.963 | 24-JUL-15:00 | 122711.06 | 73183.824 | 110971.339 | 0 | 681013.778 | 0 | 7547.024 | 0 | 0 | 0 | 0 | 0 | 5012.938 | 0 | 0
August | 922401000000 | 960720.617 | 04-AUG-14:00 | 122711.06 | 78000.308 | 109653.36 | 0 | 637275.901 | 0 | 7836.859 | 0 | 0 | 0 | 0 | 0 | 5243.129 | 0 | 0
September | 955130000000 | 1008849.298 | 20-SEP-15:00 | 220879.908 | 133019.064 | 112613.312 | 0 | 529652.434 | 0 | 7423.252 | 0 | 0 | 0 | 0 | 0 | 5261.328 | 0 | 0
October | 780310000000 | 877271.464 | 03-OCT-15:09 | 220879.908 | 133019.064 | 101881.484 | 0 | 409657.606 | 0 | 6608.955 | 0 | 0 | 0 | 0 | 0 | 5224.448 | 0 | 0
November | 630899000000 | 570611.999 | 10-NOV-12:00 | 220879.908 | 151653.867 | 86401.991 | 0 | 104934.626 | 0 | 1739.968 | 0 | 0 | 0 | 0 | 0 | 5001.639 | 0 | 0
December | 609618000000 | 547397.621 | 05-DEC-14:00 | 220879.908 | 145652.643 | 80667.152 | 0 | 93786.108 | 0 | 1399.721 | 0 | 0 | 0 | 0 | 0 | 5012.089 | 0 | 0
Annual Sum or Average | 9405970000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 571549000000 | 502821.68 |  | 122711.06 | 73183.824 | 79305.365 | 0 | 50938.196 | 0 | 1125.768 | 0 | 0 | 0 | 0 | 0 | 4873.221 | 0 | 0
Maximum of Months | 1145080000000 | 1210939.294 |  | 220879.908 | 151653.867 | 116837.859 | 0 | 713948.347 | 0 | 8070.887 | 0 | 0 | 0 | 0 | 0 | 5549.65 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 268880.67 | 19343.87 | 0 | 288224.54
Cost per Total Building Area ($/m2) | 13.72 | 0.99 | 0 | 14.71
Cost per Net Conditioned Building Area ($/m2) | 13.72 | 0.99 | 0 | 14.71

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 11036.09 | 563.3 | 563.3
Net Site Energy | 11036.09 | 563.3 | 563.3
Total Source Energy | 26665.63 | 1361.05 | 1361.05
Net Source Energy | 26665.63 | 1361.05 | 1361.05
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 3047.23 | 0 | 0 | 0 | 0
Cooling | 291.13 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3382.14 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 142.03 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1052.56 | 0 | 0 | 0 | 0 | 0
Pumps | 12.55 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 339.29 | 0 | 0 | 0 | 2677.93
Refrigeration | 137.94 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7296.17 | 3739.92 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 9.68 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 266.35 | 15.06 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 15.06 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 15.06 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 80.28 | 15.06 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 12.91 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 13.99 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 13.99 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 13.99 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 16.14 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 16.14 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.5266 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.5266 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.39 | 0.223 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.39 | 0.223 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.39 | 0.223 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.39 | 0.223 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.39 | 0.223 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.39 | 0.223 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.39 | 0.223 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 5.835 | 0.39 | 0.223 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.39 | 0.223 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 5.835 | 0.39 | 0.223 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 36.4 | 36.4 | 5.835 | 0.39 | 0.223 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.39 | 0.223 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.39 | 0.223 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.39 | 0.223 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.39 | 0.223 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.39 | 0.223 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.39 | 0.223 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.39 | 0.223 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.39 | 0.223 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.39 | 0.223 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.39 | 0.223 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.39 | 0.223 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.39 | 0.223 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.39 | 0.223 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.39 | 0.223 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.39 | 0.223 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.39 | 0.223 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.39 | 0.223 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.39 | 0.223 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.39 | 0.223 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.39 | 0.223 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.39 | 0.223 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.39 | 0.223 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.39 | 0.223 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.39 | 0.223 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.39 | 0.223 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 5.835 | 0.39 | 0.223 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 5.835 | 0.39 | 0.223 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 5.835 | 0.39 | 0.223 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 5.835 | 0.39 | 0.223 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 5.835 | 0.39 | 0.223 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 5.835 | 0.39 | 0.223 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
GYM_ZN_1_FLR_2_SKYLIGHT_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_10 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_11 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_12 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_13 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_14 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_15 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_16 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_17 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_18 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_19 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_20 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_21 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_22 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_23 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_24 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_25 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_26 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_27 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_28 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_29 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_3 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_30 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_31 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_32 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_33 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_34 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_35 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_36 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_37 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_38 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_39 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_4 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_40 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_41 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_42 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_43 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_44 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_45 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_46 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_47 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_48 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_49 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_5 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_50 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_51 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_52 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_53 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_54 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_6 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_7 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_8 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_9 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_2_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.39 | 0.223 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 49.41 | 49.41 | 5.835 | 0.39 | 0.223 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.39 | 0.223 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 5.835 | 0.39 | 0.223 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 5.835 | 0.39 | 0.223 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.39 | 0.223 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.39 | 0.223 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.39 | 0.223 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.39 | 0.223 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.39 | 0.223 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.39 | 0.223 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.39 | 0.223 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.39 | 0.223 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.39 | 0.223 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.39 | 0.223 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.39 | 0.223 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.39 | 0.223 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.39 | 0.223 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.39 | 0.223 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.39 | 0.223 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.39 | 0.223 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.39 | 0.223 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.39 | 0.223 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.39 | 0.223 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.39 | 0.223 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2233.52 | 5.83 | 0.39 | 0.219
North Total or Average |  |  | 753.18 | 5.83 | 0.39 | 0.223
Non-North Total or Average |  |  | 1480.33 | 5.83 | 0.39 | 0.217
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 999481.87 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 967573.81 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 364272.8 | 277260.94 | 87011.86 | 0.76 | 3.57
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 97207.88 | 74533.63 | 22674.25 | 0.77 | 3.95
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 146937.69 | 111433.89 | 35503.8 | 0.76 | 3.9
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 18192.54 | 13540.11 | 4652.43 | 0.74 | 3.84
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 87214.12 | 64910.61 | 22303.51 | 0.74 | 3.85
VAV_OTHER_COOLC | Coil:Cooling:Water | 371514.78 | 259905.36 | 111609.42 | 0.7 | -
VAV_POD_1_COOLC | Coil:Cooling:Water | 321478.25 | 222901.06 | 98577.18 | 0.69 | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 312699.5 | 216651.33 | 96048.18 | 0.69 | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 314180.62 | 217751.4 | 96429.22 | 0.69 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6439.78 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6902.46 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9146.36 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11856.92 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9029.59 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11814.38 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9031.88 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11821.62 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6470.59 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8937.37 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6426.67 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8927.88 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6494.68 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8952.48 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8204.69 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11648.8 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5545.62 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11325.46 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5581.44 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11351.6 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 42172.11 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6641.25 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10635.24 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12600.35 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 33496.97 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13603.18 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10705.89 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 31048.22 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 41476.95 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 30109 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 40973.58 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 30137.96 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 41044.48 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15369.1 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 24258.31 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15196.04 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 24220.09 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15579.57 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 24514.58 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22443.15 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 32562.11 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 879468.07 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 203913.24 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 351787.23 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 41678.26 | 0.8
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 199803.42 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 68211.89 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 60731.78 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 58983.22 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 59322.89 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.36 | 10060.26 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.94 | 1066.78 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.16 | 27200.35 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 13.73 | 23262.86 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 13.33 | 22593.09 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 13.41 | 22723.2 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 9158.87 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 5327.87 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 90814.9552 | 79.6323 | 504.2896 | 0 | 0.0003 | 3041660 | 32969.7766
February | 68741.3436 | 59.8349 | 460.7739 | 0 | 0.0002 | 2779640 | 25197.2977
March | 83068.3551 | 72.45 | 530.9735 | 0 | 0.0003 | 3203000 | 30370.0767
April | 68588.0176 | 59.522 | 491.8515 | 0 | 0.0003 | 2967260 | 25239.0477
May | 68656.5169 | 59.3239 | 538.4324 | 0 | 0.0003 | 3248480 | 25404.8719
June | 66621.8731 | 57.492 | 535.6873 | 0 | 0.0003 | 3231970 | 24692.3031
July | 46052.5142 | 39.7348 | 371.4845 | 0 | 0.0002 | 2241290 | 17072.237
August | 49528.6558 | 42.7421 | 398.0888 | 0 | 0.0002 | 2401790 | 18356.5044
September | 63450.3064 | 54.6102 | 536.1044 | 0 | 0.0003 | 3234580 | 23595.8911
October | 67346.0857 | 58.1449 | 536.496 | 0 | 0.0003 | 3236830 | 24945.4215
November | 70450.6682 | 61.1474 | 503.6058 | 0 | 0.0003 | 3038170 | 25919.576
December | 83889.3285 | 73.4204 | 490.7074 | 0 | 0.0003 | 2959880 | 30531.3668
Annual Sum or Average | 827208.6202 | 718.0549 | 5898.4952 | 0 | 0.003 | 35584500 | 304294.3706
Minimum of Months | 46052.5142 | 39.7348 | 371.4845 | 0 | 0.0002 | 2241290 | 17072.237
Maximum of Months | 90814.9552 | 79.6323 | 538.4324 | 0 | 0.0003 | 3248480 | 32969.7766
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 623655000000 | 470833.838 | 17-JAN-14:00 | 220879.908 | 145652.643 | 80048.887 | 0 | 18899.193 | 0 | 733.429 | 0 | 0 | 0 | 0 | 0 | 4619.778 | 0 | 0
February | 569930000000 | 558872.114 | 15-FEB-16:10 | 220879.908 | 133019.064 | 79447.833 | 0 | 118823.569 | 0 | 1857.441 | 0 | 0 | 0 | 0 | 0 | 4844.299 | 0 | 0
March | 656735000000 | 493606.968 | 01-MAR-12:00 | 220879.908 | 151653.867 | 79225.986 | 0 | 35607.516 | 0 | 1336.373 | 0 | 0 | 0 | 0 | 0 | 4903.318 | 0 | 0
April | 608400000000 | 581106.853 | 13-APR-14:00 | 220879.908 | 137835.548 | 85260.483 | 0 | 130336.052 | 0 | 1778.713 | 0 | 0 | 0 | 0 | 0 | 5016.15 | 0 | 0
May | 666060000000 | 635324.511 | 17-MAY-13:00 | 220879.908 | 145652.643 | 81578.766 | 0 | 179241.948 | 0 | 2713.746 | 0 | 0 | 0 | 0 | 0 | 5257.5 | 0 | 0
June | 662675000000 | 650365.534 | 15-JUN-12:00 | 220879.908 | 145652.643 | 81385.431 | 0 | 194530.248 | 0 | 2636.298 | 0 | 0 | 0 | 0 | 0 | 5281.007 | 0 | 0
July | 459548000000 | 526598.914 | 03-JUL-12:00 | 122711.06 | 84617.158 | 77569.329 | 0 | 234425.173 | 0 | 2187.85 | 0 | 0 | 0 | 0 | 0 | 5088.345 | 0 | 0
August | 492458000000 | 496368.562 | 15-AUG-11:00 | 122711.06 | 88818.015 | 76251.516 | 0 | 201702.748 | 0 | 1894.028 | 0 | 0 | 0 | 0 | 0 | 4991.195 | 0 | 0
September | 663211000000 | 898824.155 | 28-SEP-14:00 | 220879.908 | 137835.548 | 100367.199 | 0 | 427626.575 | 0 | 6597.917 | 0 | 0 | 0 | 0 | 0 | 5517.009 | 0 | 0
October | 663671000000 | 629813.484 | 31-OCT-12:00 | 220879.908 | 145652.643 | 85802.476 | 0 | 169475.544 | 0 | 2801.811 | 0 | 0 | 0 | 0 | 0 | 5201.102 | 0 | 0
November | 622938000000 | 496635.247 | 14-NOV-12:00 | 220879.908 | 151653.867 | 80122.552 | 0 | 37224.761 | 0 | 1890.604 | 0 | 0 | 0 | 0 | 0 | 4863.555 | 0 | 0
December | 606887000000 | 472031.251 | 07-DEC-14:00 | 220879.908 | 145652.643 | 78889.148 | 0 | 20698.676 | 0 | 1155.211 | 0 | 0 | 0 | 0 | 0 | 4755.666 | 0 | 0
Annual Sum or Average | 7296170000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 459548000000 | 470833.838 |  | 122711.06 | 84617.158 | 76251.516 | 0 | 18899.193 | 0 | 733.429 | 0 | 0 | 0 | 0 | 0 | 4619.778 | 0 | 0
Maximum of Months | 666060000000 | 898824.155 |  | 220879.908 | 151653.867 | 100367.199 | 0 | 427626.575 | 0 | 6597.917 | 0 | 0 | 0 | 0 | 0 | 5517.009 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 300285.64 | 32050.52 | 0 | 332336.15
Cost per Total Building Area ($/m2) | 15.33 | 1.64 | 0 | 16.96
Cost per Net Conditioned Building Area ($/m2) | 15.33 | 1.64 | 0 | 16.96

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 15187.06 | 775.17 | 775.17
Net Site Energy | 15187.06 | 775.17 | 775.17
Total Source Energy | 37542.95 | 1916.24 | 1916.24
Net Source Energy | 37542.95 | 1916.24 | 1916.24
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 6039.84 | 0 | 0 | 0 | 0
Cooling | 1383.57 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3382.14 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 141.95 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1088.43 | 0 | 0 | 0 | 0 | 0
Pumps | 23.93 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 356.36 | 0 | 0 | 0 | 2677.93
Refrigeration | 139.63 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8437.47 | 6749.59 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 9.68 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 266.35 | 15.06 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 15.06 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 15.06 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 80.28 | 15.06 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 12.91 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 13.99 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 13.99 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 13.99 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 16.14 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 16.14 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.5266 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.5266 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.385 | 0.305 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.385 | 0.305 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 72.8 | 72.8 | 3.241 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 72.8 | 72.8 | 3.241 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 36.4 | 36.4 | 3.241 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
GYM_ZN_1_FLR_2_SKYLIGHT_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_10 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_11 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_12 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_13 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_14 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_15 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_16 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_17 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_18 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_19 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_20 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_21 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_22 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_23 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_24 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_25 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_26 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_27 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_28 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_29 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_3 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_30 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_31 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_32 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_33 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_34 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_35 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_36 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_37 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_38 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_39 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_4 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_40 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_41 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_42 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_43 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_44 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_45 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_46 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_47 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_48 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_49 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_5 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_50 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_51 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_52 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_53 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_54 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_6 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_7 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_8 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_9 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 49.41 | 49.41 | 3.241 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.385 | 0.305 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.385 | 0.305 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 3.241 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 3.241 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 3.241 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 3.241 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 19.6 | 19.6 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 19.6 | 19.6 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2233.52 | 3.22 | 0.386 | 0.303
North Total or Average |  |  | 753.18 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 1480.33 | 3.22 | 0.386 | 0.303
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1313323.51 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 874071.77 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 490687.86 | 331745.83 | 158942.03 | 0.68 | 3.25
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 128868.84 | 87126.06 | 41742.78 | 0.68 | 3.49
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 196275.14 | 132698.33 | 63576.81 | 0.68 | 3.49
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13553.09 | 9163.02 | 4390.07 | 0.68 | 3.65
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 111477.74 | 75368.23 | 36109.51 | 0.68 | 3.51
VAV_OTHER_COOLC | Coil:Cooling:Water | 328550.32 | 218024.09 | 110526.23 | 0.66 | -
VAV_POD_1_COOLC | Coil:Cooling:Water | 270158.78 | 173342.72 | 96816.07 | 0.64 | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 265119.49 | 169947.53 | 95171.97 | 0.64 | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 281846.02 | 181118.87 | 100727.15 | 0.64 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6407.88 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7224.42 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5596.85 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8121.56 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5499.65 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8081.62 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5504.04 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8101.94 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5286.64 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7887.52 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5265.98 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7887.64 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5342.18 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7932.25 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5285.19 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9974.16 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3782.47 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9823.77 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3850.36 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9984.53 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 31868.86 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3136.69 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6850.33 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15134.26 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 36406.69 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12760.93 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9507.77 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11925.64 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20722.55 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11644.03 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20442.67 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11644.03 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 23953.94 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11644.03 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 18793.52 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11644.03 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 18797.05 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11644.03 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 22524.88 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11696.73 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 21022.6 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 1212770.34 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 262987.28 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 485108.14 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 33497.43 | 0.8
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 275525.26 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 104129.67 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 67688.18 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 66164.62 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 71061.42 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.19 | 9735.54 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.55 | 633.06 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 13.26 | 22473.26 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.62 | 16175.09 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.43 | 15811.01 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 9.05 | 16981.17 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 12034.79 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 4813.01 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 190698.0054 | 289.948 | 646.0049 | 0 | 0.0028 | 40151.6771 | 76685.4872
February | 159839.2691 | 249.6307 | 577.9222 | 0 | 0.0025 | 35923.519 | 64879.9208
March | 156356.2345 | 262.6751 | 667.3893 | 0 | 0.0028 | 41493.8165 | 65156.2541
April | 121838.6429 | 222.6568 | 619.2803 | 0 | 0.0025 | 38510.164 | 52415.3714
May | 132318.7079 | 254.9088 | 744.8805 | 0 | 0.003 | 46325.2114 | 58121.7493
June | 168044.1719 | 332.3534 | 993.5926 | 0 | 0.004 | 61795.6936 | 74602.582
July | 126470.3009 | 250.9838 | 752.4955 | 0 | 0.003 | 46801.1063 | 56224.1168
August | 136433.4445 | 270.6046 | 810.9404 | 0 | 0.0033 | 50436.0139 | 60639.5323
September | 133701.3941 | 262.9084 | 782.1263 | 0 | 0.0032 | 48643.2566 | 59216.993
October | 133076.3774 | 248.3052 | 704.6241 | 0 | 0.0029 | 43819.0774 | 57717.2825
November | 138945.6108 | 240.8707 | 634.1824 | 0 | 0.0026 | 39432.3192 | 58581.7123
December | 172270.4394 | 269.2439 | 623.9659 | 0 | 0.0027 | 38785.687 | 69943.9905
Annual Sum or Average | 1769990 | 3155.0897 | 8557.4044 | 0 | 0.0352 | 532117.5421 | 754184.9922
Minimum of Months | 121838.6429 | 222.6568 | 577.9222 | 0 | 0.0025 | 35923.519 | 52415.3714
Maximum of Months | 190698.0054 | 332.3534 | 993.5926 | 0 | 0.004 | 61795.6936 | 76685.4872
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 636661000000 | 466365.699 | 09-JAN-11:39 | 220879.908 | 151653.867 | 73396.305 | 0 | 12842.451 | 0 | 676.984 | 0 | 0 | 0 | 0 | 0 | 6916.184 | 0 | 0
February | 569618000000 | 462906.047 | 15-FEB-12:00 | 220879.908 | 151653.867 | 74273.847 | 0 | 10981.36 | 0 | 472.714 | 0 | 0 | 0 | 0 | 0 | 4644.351 | 0 | 0
March | 657943000000 | 655855.774 | 09-MAR-15:00 | 220879.908 | 137835.548 | 79612.962 | 0 | 209975.066 | 0 | 2311.873 | 0 | 0 | 0 | 0 | 0 | 5240.417 | 0 | 0
April | 610633000000 | 665327.812 | 04-APR-15:00 | 220879.908 | 133019.064 | 80080.676 | 0 | 224255.461 | 0 | 2134.259 | 0 | 0 | 0 | 0 | 0 | 4958.444 | 0 | 0
May | 734551000000 | 924986.57 | 31-MAY-15:00 | 220879.908 | 133019.064 | 85831.809 | 0 | 474900.175 | 0 | 5048.611 | 0 | 0 | 0 | 0 | 0 | 5307.003 | 0 | 0
June | 979858000000 | 1189584.633 | 30-JUN-14:00 | 220879.908 | 137835.548 | 106888.923 | 0 | 709458.444 | 0 | 8967.014 | 0 | 0 | 0 | 0 | 0 | 5554.796 | 0 | 0
July | 742097000000 | 1010239.086 | 25-JUL-12:00 | 122711.06 | 84617.158 | 87487.442 | 0 | 703476.052 | 0 | 6629.322 | 0 | 0 | 0 | 0 | 0 | 5318.052 | 0 | 0
August | 799734000000 | 1012517.644 | 09-AUG-14:00 | 122711.06 | 78000.308 | 88773.284 | 0 | 709812.971 | 0 | 7955.285 | 0 | 0 | 0 | 0 | 0 | 5264.737 | 0 | 0
September | 771307000000 | 939525.116 | 08-SEP-14:00 | 220879.908 | 137835.548 | 105235.651 | 0 | 464828.539 | 0 | 5242.277 | 0 | 0 | 0 | 0 | 0 | 5503.195 | 0 | 0
October | 694813000000 | 804867.617 | 03-OCT-11:00 | 220879.908 | 151653.867 | 88983.148 | 0 | 333890.421 | 0 | 4165.324 | 0 | 0 | 0 | 0 | 0 | 5294.949 | 0 | 0
November | 625255000000 | 683977.774 | 03-NOV-13:00 | 220879.908 | 145652.643 | 87554.672 | 0 | 221397.584 | 0 | 3288.065 | 0 | 0 | 0 | 0 | 0 | 5204.901 | 0 | 0
December | 615002000000 | 454012.104 | 06-DEC-11:39 | 220879.908 | 151653.867 | 75066.025 | 0 | 0 | 0 | 232.01 | 0 | 0 | 0 | 0 | 0 | 6180.295 | 0 | 0
Annual Sum or Average | 8437470000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 569618000000 | 454012.104 |  | 122711.06 | 78000.308 | 73396.305 | 0 | 0 | 0 | 232.01 | 0 | 0 | 0 | 0 | 0 | 4644.351 | 0 | 0
Maximum of Months | 979858000000 | 1189584.633 |  | 220879.908 | 151653.867 | 106888.923 | 0 | 709812.971 | 0 | 8967.014 | 0 | 0 | 0 | 0 | 0 | 6916.184 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 194703.66 | 65460.57 | 0 | 260164.22
Cost per Total Building Area ($/m2) | 9.94 | 3.34 | 0 | 13.28
Cost per Net Conditioned Building Area ($/m2) | 9.94 | 3.34 | 0 | 13.28

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 12808.22 | 653.75 | 653.75
Net Site Energy | 12808.22 | 653.75 | 653.75
Total Source Energy | 32164.08 | 1641.69 | 1641.69
Net Source Energy | 32164.08 | 1641.69 | 1641.69
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 3941.54 | 0 | 0 | 0 | 0
Cooling | 1060.27 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3382.14 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 142 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1141.7 | 0 | 0 | 0 | 0 | 0
Pumps | 22.34 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 347.29 | 0 | 0 | 0 | 2677.93
Refrigeration | 139.72 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8165.99 | 4642.23 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 9.68 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 266.35 | 15.06 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 15.06 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 15.06 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 80.28 | 15.06 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 12.91 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 13.99 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 13.99 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 13.99 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 16.14 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 16.14 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.5266 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.5266 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.385 | 0.305 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.385 | 0.305 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 72.8 | 72.8 | 3.241 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 72.8 | 72.8 | 3.241 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 36.4 | 36.4 | 3.241 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
GYM_ZN_1_FLR_2_SKYLIGHT_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_10 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_11 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_12 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_13 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_14 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_15 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_16 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_17 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_18 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_19 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_20 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_21 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_22 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_23 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_24 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_25 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_26 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_27 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_28 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_29 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_3 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_30 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_31 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_32 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_33 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_34 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_35 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_36 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_37 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_38 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_39 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_4 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_40 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_41 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_42 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_43 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_44 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_45 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_46 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_47 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_48 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_49 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_5 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_50 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_51 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_52 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_53 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_54 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_6 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_7 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_8 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_9 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 49.41 | 49.41 | 3.241 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.385 | 0.305 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.385 | 0.305 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 3.241 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 3.241 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 3.241 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 3.241 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 19.6 | 19.6 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 19.6 | 19.6 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2233.52 | 3.22 | 0.386 | 0.303
North Total or Average |  |  | 753.18 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 1480.33 | 3.22 | 0.386 | 0.303
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 707617.2 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 709044.24 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 450436.85 | 314397.64 | 136039.21 | 0.7 | 3.33
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 108592.95 | 78608.51 | 29984.44 | 0.72 | 3.71
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 156259.33 | 115451.52 | 40807.82 | 0.74 | 3.79
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12057.01 | 8398.94 | 3658.07 | 0.7 | 3.71
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 102865.51 | 71656.36 | 31209.15 | 0.7 | 3.6
VAV_OTHER_COOLC | Coil:Cooling:Water | 218892.44 | 137130.68 | 81761.76 | 0.63 | -
VAV_POD_1_COOLC | Coil:Cooling:Water | 190191.74 | 117272.67 | 72919.07 | 0.62 | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 186174.71 | 114640.09 | 71534.61 | 0.62 | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 201764.97 | 124458.74 | 77306.23 | 0.62 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5302.77 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6595.16 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4544.17 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7119.58 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4440.31 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7075.1 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4445.87 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7097.23 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4341.35 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6994.97 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4314.32 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6991.56 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4393.02 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7039.04 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3976.05 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8679.21 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2523.32 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8504.97 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2587.09 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8668.97 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 28125.86 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2022.34 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 5497.76 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11637.17 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 31073.91 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11429.51 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8371.24 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9635.89 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 17186.56 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9635.89 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16895.6 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9635.89 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20420.58 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9635.89 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16083.26 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9635.89 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16070.42 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9635.89 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19806.3 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8679.58 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 17618.63 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 963612.67 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 210714.64 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 385445.07 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 25659.91 | 0.8
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 218919.96 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 81135.78 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 53546.23 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 52265.48 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 56905.4 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.23 | 9803.77 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.53 | 610.33 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 13.23 | 22417.22 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.73 | 16381 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.52 | 15989.19 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 9.28 | 17408.65 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 6484.33 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 3904.3 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 214464.783 | 334.8825 | 759.8094 | 0 | 0.0031 | 789823.0306 | 87979.8203
February | 185153.9208 | 294.5347 | 685.3047 | 0 | 0.0027 | 712419.6804 | 76487.3258
March | 207954.9092 | 336.6725 | 801.4528 | 0 | 0.0032 | 833209.2906 | 86481.9403
April | 181402.5233 | 305.6311 | 763.7788 | 0 | 0.003 | 794132.2735 | 76611.416
May | 216698.0183 | 375.414 | 968.2241 | 0 | 0.0038 | 1006770 | 92529.6181
June | 240526.2489 | 419.2993 | 1088.7875 | 0 | 0.0042 | 1132150 | 102959.7015
July | 177601.8008 | 310.188 | 807.0998 | 0 | 0.0031 | 839250.3905 | 76081.3698
August | 174724.321 | 304.9701 | 792.9824 | 0 | 0.0031 | 824569.4239 | 74829.8468
September | 205837.7399 | 358.2788 | 928.7895 | 0 | 0.0036 | 965779.8026 | 88057.038
October | 192491.1167 | 325.5437 | 817.1251 | 0 | 0.0032 | 849607.1202 | 81415.1186
November | 193515.969 | 314.5515 | 752.5993 | 0 | 0.003 | 782429.4246 | 80600.3582
December | 210577.6136 | 327.8158 | 740.6418 | 0 | 0.003 | 769890.176 | 86287.3973
Annual Sum or Average | 2400950 | 4007.7821 | 9906.5953 | 0 | 0.0391 | 10300000 | 1010320
Minimum of Months | 174724.321 | 294.5347 | 685.3047 | 0 | 0.0027 | 712419.6804 | 74829.8468
Maximum of Months | 240526.2489 | 419.2993 | 1088.7875 | 0 | 0.0042 | 1132150 | 102959.7015
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 626181000000 | 477023.733 | 25-JAN-14:00 | 220879.908 | 145652.643 | 83435.063 | 0 | 21600.367 | 0 | 777.535 | 0 | 0 | 0 | 0 | 0 | 4678.217 | 0 | 0
February | 564815000000 | 550823.405 | 14-FEB-16:10 | 220879.908 | 133019.064 | 85413.879 | 0 | 105386.063 | 0 | 1395.107 | 0 | 0 | 0 | 0 | 0 | 4729.384 | 0 | 0
March | 660578000000 | 564438.237 | 02-MAR-14:00 | 220879.908 | 145652.643 | 91425.539 | 0 | 99643.921 | 0 | 1825.132 | 0 | 0 | 0 | 0 | 0 | 5011.095 | 0 | 0
April | 629598000000 | 709284.731 | 21-APR-15:00 | 220879.908 | 133019.064 | 100293.422 | 0 | 246809.148 | 0 | 3326.684 | 0 | 0 | 0 | 0 | 0 | 4956.505 | 0 | 0
May | 798182000000 | 834051.936 | 31-MAY-15:00 | 220879.908 | 133019.064 | 108660.495 | 0 | 360607.572 | 0 | 5736.927 | 0 | 0 | 0 | 0 | 0 | 5147.969 | 0 | 0
June | 897585000000 | 941697.559 | 29-JUN-13:00 | 220879.908 | 145652.643 | 113053.948 | 0 | 449959.964 | 0 | 6599 | 0 | 0 | 0 | 0 | 0 | 5552.096 | 0 | 0
July | 665368000000 | 766029.086 | 31-JUL-14:00 | 122711.06 | 78000.308 | 101931.875 | 0 | 452492.902 | 0 | 5741.518 | 0 | 0 | 0 | 0 | 0 | 5151.423 | 0 | 0
August | 653729000000 | 739051.077 | 01-AUG-14:00 | 122711.06 | 78000.308 | 101323.337 | 0 | 425207.361 | 0 | 6572.232 | 0 | 0 | 0 | 0 | 0 | 5236.78 | 0 | 0
September | 765682000000 | 793840.419 | 20-SEP-15:09 | 220879.908 | 133019.064 | 107924.225 | 0 | 321664.287 | 0 | 5207.415 | 0 | 0 | 0 | 0 | 0 | 5145.52 | 0 | 0
October | 673579000000 | 696405.03 | 11-OCT-15:00 | 220879.908 | 133019.064 | 95906.477 | 0 | 237392.514 | 0 | 4249.996 | 0 | 0 | 0 | 0 | 0 | 4957.07 | 0 | 0
November | 620319000000 | 526895.513 | 08-NOV-16:10 | 220879.908 | 133019.064 | 85451.998 | 0 | 81668.691 | 0 | 1220.597 | 0 | 0 | 0 | 0 | 0 | 4655.255 | 0 | 0
December | 610378000000 | 470398.127 | 08-DEC-14:00 | 220879.908 | 145652.643 | 82796.872 | 0 | 15785.024 | 0 | 646.569 | 0 | 0 | 0 | 0 | 0 | 4637.111 | 0 | 0
Annual Sum or Average | 8165990000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 564815000000 | 470398.127 |  | 122711.06 | 78000.308 | 82796.872 | 0 | 15785.024 | 0 | 646.569 | 0 | 0 | 0 | 0 | 0 | 4637.111 | 0 | 0
Maximum of Months | 897585000000 | 941697.559 |  | 220879.908 | 145652.643 | 113053.948 | 0 | 452492.902 | 0 | 6599 | 0 | 0 | 0 | 0 | 0 | 5552.096 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 83956.99 | 32133.55 | 0 | 116090.55
Cost per Total Building Area ($/m2) | 4.29 | 1.64 | 0 | 5.93
Cost per Net Conditioned Building Area ($/m2) | 4.29 | 1.64 | 0 | 5.93

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 13577.81 | 693.03 | 693.03
Net Site Energy | 13577.81 | 693.03 | 693.03
Total Source Energy | 19495.3 | 995.06 | 995.06
Net Source Energy | 19495.3 | 995.06 | 995.06
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 5669.44 | 0 | 0 | 0 | 0
Cooling | 231.58 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3382.14 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 141.72 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1003.17 | 0 | 0 | 0 | 0 | 0
Pumps | 10.31 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 372.93 | 0 | 0 | 0 | 2677.93
Refrigeration | 135.3 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7182.05 | 6395.77 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 9.68 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 266.35 | 15.06 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 15.06 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 15.06 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 80.28 | 15.06 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 12.91 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 13.99 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 13.99 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 13.99 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 16.14 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 16.14 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.5266 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.5266 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.385 | 0.305 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.385 | 0.305 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 72.8 | 72.8 | 3.241 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 72.8 | 72.8 | 3.241 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 36.4 | 36.4 | 3.241 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
GYM_ZN_1_FLR_2_SKYLIGHT_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_10 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_11 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_12 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_13 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_14 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_15 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_16 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_17 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_18 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_19 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_20 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_21 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_22 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_23 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_24 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_25 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_26 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_27 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_28 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_29 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_3 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_30 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_31 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_32 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_33 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_34 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_35 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_36 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_37 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_38 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_39 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_4 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_40 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_41 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_42 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_43 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_44 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_45 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_46 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_47 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_48 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_49 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_5 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_50 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_51 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_52 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_53 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_54 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_6 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_7 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_8 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_9 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 49.41 | 49.41 | 3.241 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.385 | 0.305 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.385 | 0.305 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 3.241 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 3.241 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 3.241 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 3.241 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 19.6 | 19.6 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 19.6 | 19.6 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2233.52 | 3.22 | 0.386 | 0.303
North Total or Average |  |  | 753.18 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 1480.33 | 3.22 | 0.386 | 0.303
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 724942.26 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 739787.2 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 439810.67 | 309817.76 | 129992.91 | 0.7 | 3.35
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 94386.26 | 67046.81 | 27339.44 | 0.71 | 3.67
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 155764.16 | 115238.1 | 40526.07 | 0.74 | 3.79
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9572.69 | 6755.35 | 2817.34 | 0.71 | 3.74
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 98243.74 | 69664.37 | 28579.36 | 0.71 | 3.66
VAV_OTHER_COOLC | Coil:Cooling:Water | 272167.85 | 186794.96 | 85372.89 | 0.69 | -
VAV_POD_1_COOLC | Coil:Cooling:Water | 204136.9 | 138553.44 | 65583.46 | 0.68 | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 198904.37 | 134843.7 | 64060.67 | 0.68 | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 213115.82 | 144589.83 | 68525.98 | 0.68 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6351.23 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6351.23 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5341.7 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7910.03 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5248.2 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7870.39 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5252.46 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7889.99 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4269.35 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6853.91 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4242.12 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6849.43 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4311.13 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6892.46 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4072.07 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8547.55 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2592.17 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8348.03 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2647.71 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8501.09 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 26320.34 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3732.94 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7279.87 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9989.97 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29204.96 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11184.65 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7687.1 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15556.49 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 24409.16 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14865.72 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 24009.66 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14935.57 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 27511.89 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11541.09 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14935.76 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11541.09 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14917.97 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11541.09 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 18594.27 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13188.81 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 22035.27 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 1048815.86 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 212169.81 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 419526.35 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 22932.83 | 0.8
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 238276.99 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 74205.51 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 54057.73 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 52514.8 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 56482.95 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.33 | 8263.55 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.43 | 501.15 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 11.74 | 19885.88 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.55 | 16040.15 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.31 | 15582.33 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.93 | 16759.77 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 6643.09 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 4073.58 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 87674.7854 | 100.4187 | 133.3927 | 0 | 0.0006 | 1759310 | 32575.7706
February | 67459.5769 | 79.9825 | 119.9861 | 0 | 0.0006 | 1583270 | 25355.7924
March | 75609.2781 | 90.4705 | 139.752 | 0 | 0.0006 | 1844290 | 28507.4026
April | 56431.5692 | 71.0979 | 127.128 | 0 | 0.0006 | 1678530 | 21659.5596
May | 46854.2236 | 64.5463 | 140.7639 | 0 | 0.0006 | 1859630 | 18574.2321
June | 41044.104 | 59.7048 | 143.5007 | 0 | 0.0006 | 1896250 | 16609.6584
July | 26534.3846 | 39.8842 | 100.9814 | 0 | 0.0004 | 1334550 | 10875.6133
August | 28032.4925 | 42.1245 | 106.6093 | 0 | 0.0004 | 1408930 | 11488.4094
September | 40121.501 | 57.7846 | 136.5834 | 0 | 0.0006 | 1804770 | 16174.3759
October | 50735.9193 | 67.0296 | 134.1382 | 0 | 0.0006 | 1771690 | 19806.2789
November | 72948.8523 | 86.6721 | 130.9074 | 0 | 0.0006 | 1727420 | 27438.4497
December | 84941.9278 | 97.4016 | 129.9561 | 0 | 0.0006 | 1714020 | 31572.4701
Annual Sum or Average | 678388.6146 | 857.1174 | 1543.6992 | 0 | 0.0067 | 20382600 | 260638.013
Minimum of Months | 26534.3846 | 39.8842 | 100.9814 | 0 | 0.0004 | 1334550 | 10875.6133
Maximum of Months | 87674.7854 | 100.4187 | 143.5007 | 0 | 0.0006 | 1896250 | 32575.7706
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 619912000000 | 450551.512 | 27-JAN-11:39 | 220879.908 | 151653.867 | 71534.701 | 0 | 0 | 0 | 155.801 | 0 | 0 | 0 | 0 | 0 | 6327.235 | 0 | 0
February | 557881000000 | 467581.809 | 21-FEB-12:00 | 220879.908 | 151653.867 | 72886.055 | 0 | 16852.053 | 0 | 579.943 | 0 | 0 | 0 | 0 | 0 | 4729.983 | 0 | 0
March | 649855000000 | 529581.944 | 29-MAR-15:00 | 220879.908 | 133019.064 | 77920.251 | 0 | 91984.113 | 0 | 1100.614 | 0 | 0 | 0 | 0 | 0 | 4677.995 | 0 | 0
April | 591448000000 | 485593.258 | 14-APR-13:00 | 220879.908 | 145652.643 | 78874.803 | 0 | 34386.861 | 0 | 968.883 | 0 | 0 | 0 | 0 | 0 | 4830.161 | 0 | 0
May | 655262000000 | 643004.061 | 05-MAY-15:00 | 220879.908 | 133019.064 | 79967.34 | 0 | 202002.794 | 0 | 2182.601 | 0 | 0 | 0 | 0 | 0 | 4952.354 | 0 | 0
June | 668164000000 | 694800.532 | 28-JUN-14:00 | 220879.908 | 137835.548 | 96416.668 | 0 | 230644.599 | 0 | 3804.384 | 0 | 0 | 0 | 0 | 0 | 5219.426 | 0 | 0
July | 470243000000 | 550056.369 | 24-JUL-14:00 | 122711.06 | 78000.308 | 78754.094 | 0 | 263111.83 | 0 | 2415.813 | 0 | 0 | 0 | 0 | 0 | 5063.264 | 0 | 0
August | 496450000000 | 501122.744 | 07-AUG-14:00 | 122711.06 | 78000.308 | 78527.905 | 0 | 214718.508 | 0 | 2187.816 | 0 | 0 | 0 | 0 | 0 | 4977.147 | 0 | 0
September | 635930000000 | 753759.867 | 13-SEP-14:00 | 220879.908 | 137835.548 | 101219.099 | 0 | 283849.316 | 0 | 4695.114 | 0 | 0 | 0 | 0 | 0 | 5280.882 | 0 | 0
October | 624274000000 | 550842.224 | 17-OCT-14:00 | 220879.908 | 137835.548 | 86710.632 | 0 | 98777.339 | 0 | 1648.193 | 0 | 0 | 0 | 0 | 0 | 4990.605 | 0 | 0
November | 608675000000 | 464391.106 | 03-NOV-10:39 | 220879.908 | 151653.867 | 71896.837 | 0 | 12465.241 | 0 | 600.603 | 0 | 0 | 0 | 0 | 0 | 6894.65 | 0 | 0
December | 603952000000 | 450560.608 | 28-DEC-11:39 | 220879.908 | 151653.867 | 71534.701 | 0 | 0 | 0 | 178.62 | 0 | 0 | 0 | 0 | 0 | 6313.512 | 0 | 0
Annual Sum or Average | 7182050000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 470243000000 | 450551.512 |  | 122711.06 | 78000.308 | 71534.701 | 0 | 0 | 0 | 155.801 | 0 | 0 | 0 | 0 | 0 | 4677.995 | 0 | 0
Maximum of Months | 668164000000 | 753759.867 |  | 220879.908 | 151653.867 | 101219.099 | 0 | 283849.316 | 0 | 4695.114 | 0 | 0 | 0 | 0 | 0 | 6894.65 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 144011.58 | 53777.71 | 0 | 197789.3
Cost per Total Building Area ($/m2) | 7.35 | 2.74 | 0 | 10.1
Cost per Net Conditioned Building Area ($/m2) | 7.35 | 2.74 | 0 | 10.1

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 16861.04 | 860.61 | 860.61
Net Site Energy | 16861.04 | 860.61 | 860.61
Total Source Energy | 38120.29 | 1945.71 | 1945.71
Net Source Energy | 38120.29 | 1945.71 | 1945.71
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 8080.3 | 0 | 0 | 0 | 0
Cooling | 990.52 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3382.14 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 141.97 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1081.98 | 0 | 0 | 0 | 0 | 0
Pumps | 19.81 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 396.36 | 0 | 0 | 0 | 2677.93
Refrigeration | 136.74 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8030.98 | 8830.06 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 9.68 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 266.35 | 15.06 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 15.06 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 15.06 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 80.28 | 15.06 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 12.91 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 13.99 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 13.99 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 13.99 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 16.14 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 16.14 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.5266 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.5266 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.385 | 0.305 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.385 | 0.305 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 72.8 | 72.8 | 3.241 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 72.8 | 72.8 | 3.241 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 36.4 | 36.4 | 3.241 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
GYM_ZN_1_FLR_2_SKYLIGHT_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_10 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_11 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_12 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_13 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_14 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_15 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_16 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_17 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_18 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_19 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_20 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_21 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_22 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_23 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_24 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_25 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_26 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_27 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_28 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_29 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_3 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_30 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_31 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_32 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_33 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_34 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_35 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_36 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_37 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_38 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_39 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_4 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_40 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_41 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_42 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_43 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_44 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_45 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_46 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_47 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_48 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_49 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_5 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_50 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_51 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_52 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_53 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_54 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_6 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_7 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_8 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_9 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 49.41 | 49.41 | 3.241 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.385 | 0.305 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.385 | 0.305 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 3.241 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 3.241 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 3.241 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 3.241 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 19.6 | 19.6 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 19.6 | 19.6 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2233.52 | 3.22 | 0.386 | 0.303
North Total or Average |  |  | 753.18 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 1480.33 | 3.22 | 0.386 | 0.303
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1281968.47 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 958243.48 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 490687.86 | 331745.83 | 158942.03 | 0.68 | 3.25
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 123268.8 | 83339.97 | 39928.83 | 0.68 | 3.49
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 196275.14 | 132698.33 | 63576.81 | 0.68 | 3.49
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13297.26 | 8990.06 | 4307.21 | 0.68 | 3.65
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 111477.74 | 75368.23 | 36109.51 | 0.68 | 3.51
VAV_OTHER_COOLC | Coil:Cooling:Water | 293300.82 | 193787.24 | 99513.58 | 0.66 | -
VAV_POD_1_COOLC | Coil:Cooling:Water | 258355.92 | 164626.99 | 93728.93 | 0.64 | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 253912.4 | 161649.71 | 92262.69 | 0.64 | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 270831.1 | 172860.32 | 97970.78 | 0.64 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6300.21 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8137.08 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5214.79 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7648.78 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5122.81 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7610.92 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5127.2 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7631.22 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4861.38 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7362.45 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4840.18 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7362.24 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4911.66 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7405.08 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4914.33 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9382.37 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3423.45 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9228.56 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3488.86 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9388.86 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 30308.06 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2860.81 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6451.66 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15026.9 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 33606.83 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12533.13 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9033.2 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11448.39 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19619.99 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11448.39 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19341.01 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11448.39 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 22851.39 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11448.39 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 17774.8 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11448.39 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 17776.59 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11448.39 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 21483.71 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10861.81 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19896.37 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 1416766.07 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 296052.59 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 566706.43 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 38393.27 | 0.8
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 321870.37 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 121237.78 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 79688 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 78030.58 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 84092.36 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 4.96 | 9312.48 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.54 | 621.11 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 12.64 | 21410.49 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.31 | 15582.02 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.13 | 15257.93 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.77 | 16443.24 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 11747.47 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 5276.5 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 317544.7083 | 485.9691 | 1186.6714 | 0 | 0.0038 | 273065.5567 | 128808.0479
February | 274062.5309 | 425.3037 | 1059.4238 | 0 | 0.0034 | 243795.7229 | 111732.1912
March | 293599.0427 | 469.862 | 1220.3134 | 0 | 0.0038 | 280845.9811 | 121058.5609
April | 229686.4264 | 394.9774 | 1118.9115 | 0 | 0.0034 | 257555.9335 | 97325.2667
May | 255447.4389 | 455.7439 | 1343.1204 | 0 | 0.0041 | 309189.3337 | 109815.4203
June | 318225.383 | 575.9462 | 1722.3589 | 0 | 0.0052 | 396501.9784 | 137587.3258
July | 232768.0836 | 422.2096 | 1265.4058 | 0 | 0.0038 | 291308.6143 | 100728.0825
August | 227133.3831 | 411.6711 | 1232.8676 | 0 | 0.0037 | 283817.5901 | 98259.3215
September | 253032.8804 | 455.9916 | 1357.7339 | 0 | 0.0041 | 312559.5611 | 109212.9708
October | 242546.1485 | 423.9093 | 1222.4289 | 0 | 0.0037 | 281393.9644 | 103426.1956
November | 267050.6903 | 435.0223 | 1155.8101 | 0 | 0.0036 | 266014.094 | 110843.1217
December | 293136.4399 | 457.9339 | 1151.3229 | 0 | 0.0036 | 264949.2167 | 119798.1473
Annual Sum or Average | 3204230 | 5414.5399 | 15036.3686 | 0 | 0.0463 | 3461000 | 1348590
Minimum of Months | 227133.3831 | 394.9774 | 1059.4238 | 0 | 0.0034 | 243795.7229 | 97325.2667
Maximum of Months | 318225.383 | 575.9462 | 1722.3589 | 0 | 0.0052 | 396501.9784 | 137587.3258
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 633628000000 | 453252.331 | 27-JAN-11:09 | 220879.908 | 151653.867 | 72766.714 | 0 | 0 | 0 | 2027.188 | 0 | 0 | 0 | 0 | 0 | 5924.655 | 0 | 0
February | 565710000000 | 453021.878 | 17-FEB-11:39 | 220879.908 | 151653.867 | 74097.376 | 0 | 0 | 0 | 252.931 | 0 | 0 | 0 | 0 | 0 | 6137.796 | 0 | 0
March | 651682000000 | 556017.512 | 31-MAR-15:09 | 220879.908 | 133019.064 | 75531.284 | 0 | 120806.834 | 0 | 967.102 | 0 | 0 | 0 | 0 | 0 | 4813.319 | 0 | 0
April | 597639000000 | 569087.582 | 07-APR-14:39 | 220879.908 | 137835.548 | 83471.313 | 0 | 119091.929 | 0 | 2767.687 | 0 | 0 | 0 | 0 | 0 | 5041.197 | 0 | 0
May | 717451000000 | 884653.622 | 30-MAY-15:00 | 220879.908 | 133019.064 | 85291.236 | 0 | 435788.919 | 0 | 4298.162 | 0 | 0 | 0 | 0 | 0 | 5376.333 | 0 | 0
June | 920053000000 | 1173825.458 | 08-JUN-12:00 | 220879.908 | 145652.643 | 101272.99 | 0 | 691217.348 | 0 | 9277.584 | 0 | 0 | 0 | 0 | 0 | 5524.985 | 0 | 0
July | 675960000000 | 895216.621 | 14-JUL-11:00 | 122711.06 | 88818.015 | 83612.084 | 0 | 589486.829 | 0 | 5294.199 | 0 | 0 | 0 | 0 | 0 | 5294.434 | 0 | 0
August | 658577000000 | 912957.35 | 04-AUG-15:50 | 122711.06 | 73183.824 | 84946.636 | 0 | 620276.443 | 0 | 6651.957 | 0 | 0 | 0 | 0 | 0 | 5187.43 | 0 | 0
September | 725271000000 | 890278.017 | 06-SEP-11:00 | 220879.908 | 151653.867 | 97585.523 | 0 | 409501.113 | 0 | 5270.182 | 0 | 0 | 0 | 0 | 0 | 5387.424 | 0 | 0
October | 652953000000 | 681976.499 | 31-OCT-11:00 | 220879.908 | 151653.867 | 84380.288 | 0 | 216701.201 | 0 | 3171.346 | 0 | 0 | 0 | 0 | 0 | 5189.889 | 0 | 0
November | 617266000000 | 676248.506 | 02-NOV-14:39 | 220879.908 | 137835.548 | 85010.919 | 0 | 224078.209 | 0 | 3257.528 | 0 | 0 | 0 | 0 | 0 | 5186.395 | 0 | 0
December | 614795000000 | 451854.542 | 12-DEC-11:39 | 220879.908 | 151653.867 | 72766.714 | 0 | 0 | 0 | 134.22 | 0 | 0 | 0 | 0 | 0 | 6419.833 | 0 | 0
Annual Sum or Average | 8030980000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 565710000000 | 451854.542 |  | 122711.06 | 73183.824 | 72766.714 | 0 | 0 | 0 | 134.22 | 0 | 0 | 0 | 0 | 0 | 4813.319 | 0 | 0
Maximum of Months | 920053000000 | 1173825.458 |  | 220879.908 | 151653.867 | 101272.99 | 0 | 691217.348 | 0 | 9277.584 | 0 | 0 | 0 | 0 | 0 | 6419.833 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 184157.85 | 73815.44 | 0 | 257973.29
Cost per Total Building Area ($/m2) | 9.4 | 3.77 | 0 | 13.17
Cost per Net Conditioned Building Area ($/m2) | 9.4 | 3.77 | 0 | 13.17

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 14257.04 | 727.7 | 727.7
Net Site Energy | 14257.04 | 727.7 | 727.7
Total Source Energy | 32722.14 | 1670.18 | 1670.18
Net Source Energy | 32722.14 | 1670.18 | 1670.18
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 5805.1 | 0 | 0 | 0 | 0
Cooling | 662.5 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3382.14 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 141.89 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1088.35 | 0 | 0 | 0 | 0 | 0
Pumps | 17.17 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 392.6 | 0 | 0 | 0 | 2677.93
Refrigeration | 136.09 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7705.95 | 6551.08 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 9.68 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 266.35 | 15.06 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 15.06 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 15.06 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 80.28 | 15.06 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 12.91 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 13.99 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 13.99 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 13.99 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 16.14 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 16.14 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.5266 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.5266 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.385 | 0.305 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.385 | 0.305 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 72.8 | 72.8 | 3.241 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 72.8 | 72.8 | 3.241 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 36.4 | 36.4 | 3.241 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
GYM_ZN_1_FLR_2_SKYLIGHT_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_10 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_11 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_12 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_13 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_14 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_15 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_16 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_17 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_18 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_19 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_20 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_21 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_22 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_23 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_24 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_25 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_26 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_27 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_28 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_29 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_3 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_30 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_31 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_32 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_33 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_34 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_35 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_36 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_37 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_38 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_39 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_4 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_40 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_41 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_42 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_43 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_44 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_45 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_46 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_47 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_48 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_49 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_5 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_50 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_51 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_52 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_53 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_54 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_6 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_7 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_8 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_9 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 49.41 | 49.41 | 3.241 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.385 | 0.305 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.385 | 0.305 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 3.241 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 3.241 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 3.241 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 3.241 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 19.6 | 19.6 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 19.6 | 19.6 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2233.52 | 3.22 | 0.386 | 0.303
North Total or Average |  |  | 753.18 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 1480.33 | 3.22 | 0.386 | 0.303
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 677681.61 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 767609.81 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 455189.53 | 316446.05 | 138743.48 | 0.7 | 3.32
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 103737.3 | 73970.04 | 29767.26 | 0.71 | 3.68
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 151440.39 | 113374.55 | 38065.84 | 0.75 | 3.84
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11856.71 | 8225.65 | 3631.07 | 0.69 | 3.7
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 103980.49 | 72136.91 | 31843.57 | 0.69 | 3.59
VAV_OTHER_COOLC | Coil:Cooling:Water | 196460.97 | 120945.84 | 75515.12 | 0.62 | -
VAV_POD_1_COOLC | Coil:Cooling:Water | 176615.76 | 107194.17 | 69421.58 | 0.61 | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 172343.06 | 104463.3 | 67879.76 | 0.61 | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 188095.7 | 114257.64 | 73838.07 | 0.61 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5458.59 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7557.2 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4120.96 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6498.2 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4019.49 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6453.47 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4025.5 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6476.39 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3810.06 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6249.88 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3781.41 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6245.12 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3855.93 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6292 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3656.31 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7817.77 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2589.28 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7630.52 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2646.57 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7796.78 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 25945.89 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2062.72 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 5925.1 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13658.16 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 27625.91 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11287.24 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7718.93 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9618.19 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 15974.62 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9618.19 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 15669.38 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9618.19 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19201.44 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9618.19 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14410.86 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9618.19 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14391.86 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9618.19 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 18111.63 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8028.54 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16310.86 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 1150276.54 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 238171.38 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 460110.62 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 29798.72 | 0.8
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 261327.5 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 93930.85 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 62836.73 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 61190.62 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 67053.81 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.81 | 9170.23 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.51 | 593.75 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 12.12 | 20542.77 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.11 | 15216.2 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.9 | 14817.59 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.66 | 16237.39 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 6210.01 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 4226.79 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 227991.6767 | 348.1452 | 765.1943 | 0 | 0.0031 | 795356.3966 | 92758.0423
February | 202798.0315 | 310.0355 | 682.5931 | 0 | 0.0028 | 709502.3469 | 82543.4721
March | 219417.0081 | 346.5186 | 798.4808 | 0 | 0.0032 | 830053.9492 | 90394.2414
April | 185919.742 | 306.8992 | 748.4687 | 0 | 0.003 | 778170.1245 | 77897.0229
May | 198973.6406 | 335.7726 | 840.6681 | 0 | 0.0033 | 874081.0105 | 84084.8926
June | 210875.0417 | 364.3379 | 936.8576 | 0 | 0.0037 | 974151.8135 | 89946.2819
July | 157038.8426 | 273.9761 | 712.0399 | 0 | 0.0028 | 740401.9439 | 67243.3448
August | 162293.7062 | 282.9033 | 734.5639 | 0 | 0.0029 | 763821.5614 | 69469.8507
September | 191921.309 | 329.2925 | 840.2127 | 0 | 0.0033 | 873644.6304 | 81636.3612
October | 191910.0201 | 322.1445 | 801.5795 | 0 | 0.0032 | 833427.0876 | 80932.3169
November | 204413.4446 | 323.0329 | 745.0123 | 0 | 0.003 | 774472.953 | 84233.6517
December | 225213.0723 | 341.5998 | 743.4063 | 0 | 0.003 | 772689.6849 | 91401.7199
Annual Sum or Average | 2378770 | 3884.6581 | 9349.0773 | 0 | 0.0371 | 9719770 | 992541.1983
Minimum of Months | 157038.8426 | 273.9761 | 682.5931 | 0 | 0.0028 | 709502.3469 | 67243.3448
Maximum of Months | 227991.6767 | 364.3379 | 936.8576 | 0 | 0.0037 | 974151.8135 | 92758.0423
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 630568000000 | 487713.153 | 27-JAN-12:00 | 220879.908 | 151653.867 | 79435.14 | 0 | 30069.16 | 0 | 854.095 | 0 | 0 | 0 | 0 | 0 | 4820.983 | 0 | 0
February | 562502000000 | 468585.621 | 07-FEB-14:00 | 220879.908 | 145652.643 | 80398.891 | 0 | 16379.643 | 0 | 643.183 | 0 | 0 | 0 | 0 | 0 | 4631.355 | 0 | 0
March | 658077000000 | 587028.344 | 30-MAR-15:00 | 220879.908 | 133019.064 | 86195.588 | 0 | 140403.522 | 0 | 1760.553 | 0 | 0 | 0 | 0 | 0 | 4769.709 | 0 | 0
April | 616943000000 | 656922.333 | 25-APR-14:00 | 220879.908 | 137835.548 | 100490.558 | 0 | 188937.15 | 0 | 3633.203 | 0 | 0 | 0 | 0 | 0 | 5145.968 | 0 | 0
May | 692982000000 | 754729.248 | 23-MAY-15:00 | 220879.908 | 133019.064 | 100713.367 | 0 | 290168.448 | 0 | 4889.591 | 0 | 0 | 0 | 0 | 0 | 5058.869 | 0 | 0
June | 772319000000 | 880110.706 | 28-JUN-11:00 | 220879.908 | 151653.867 | 102786.042 | 0 | 393035.002 | 0 | 6284.044 | 0 | 0 | 0 | 0 | 0 | 5471.842 | 0 | 0
July | 587000000000 | 700835.237 | 17-JUL-14:00 | 122711.06 | 78000.308 | 97855.371 | 0 | 391622.247 | 0 | 5501.721 | 0 | 0 | 0 | 0 | 0 | 5144.531 | 0 | 0
August | 605567000000 | 728871.407 | 30-AUG-13:00 | 122711.06 | 84617.158 | 95849.84 | 0 | 415112.363 | 0 | 5340.206 | 0 | 0 | 0 | 0 | 0 | 5240.781 | 0 | 0
September | 692636000000 | 811895.66 | 05-SEP-13:00 | 220879.908 | 145652.643 | 103957.091 | 0 | 329827.26 | 0 | 6154.125 | 0 | 0 | 0 | 0 | 0 | 5424.633 | 0 | 0
October | 660751000000 | 726725.59 | 05-OCT-14:00 | 220879.908 | 137835.548 | 103566.505 | 0 | 253959.32 | 0 | 5242.996 | 0 | 0 | 0 | 0 | 0 | 5241.314 | 0 | 0
November | 614011000000 | 538366.282 | 10-NOV-13:00 | 220879.908 | 145652.643 | 84149.873 | 0 | 81236.389 | 0 | 1467.916 | 0 | 0 | 0 | 0 | 0 | 4979.554 | 0 | 0
December | 612598000000 | 462289.185 | 21-DEC-14:30 | 220879.908 | 145652.643 | 79437.331 | 0 | 11181.571 | 0 | 515.149 | 0 | 0 | 0 | 0 | 0 | 4622.583 | 0 | 0
Annual Sum or Average | 7705950000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 562502000000 | 462289.185 |  | 122711.06 | 78000.308 | 79435.14 | 0 | 11181.571 | 0 | 515.149 | 0 | 0 | 0 | 0 | 0 | 4622.583 | 0 | 0
Maximum of Months | 772319000000 | 880110.706 |  | 220879.908 | 151653.867 | 103957.091 | 0 | 415112.363 | 0 | 6284.044 | 0 | 0 | 0 | 0 | 0 | 5471.842 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 79238.03 | 45479.81 | 0 | 124717.84
Cost per Total Building Area ($/m2) | 4.04 | 2.32 | 0 | 6.37
Cost per Net Conditioned Building Area ($/m2) | 4.04 | 2.32 | 0 | 6.37

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 19867.55 | 1014.06 | 1014.06
Net Site Energy | 19867.55 | 1014.06 | 1014.06
Total Source Energy | 40087.58 | 2046.12 | 2046.12
Net Source Energy | 40087.58 | 2046.12 | 2046.12
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 11238.99 | 0 | 0 | 0 | 0
Cooling | 778.66 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3382.14 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 141.88 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1106.87 | 0 | 0 | 0 | 0 | 0
Pumps | 20.54 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 432.02 | 0 | 0 | 0 | 2677.93
Refrigeration | 135.25 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7843.16 | 12024.39 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 9.68 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 266.35 | 15.06 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 15.06 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 15.06 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 80.28 | 15.06 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 12.91 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 13.99 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 13.99 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 13.99 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 16.14 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 16.14 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.5266 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.5266 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.385 | 0.305 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.385 | 0.305 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 72.8 | 72.8 | 3.241 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 72.8 | 72.8 | 3.241 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 36.4 | 36.4 | 3.241 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
GYM_ZN_1_FLR_2_SKYLIGHT_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_10 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_11 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_12 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_13 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_14 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_15 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_16 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_17 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_18 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_19 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_20 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_21 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_22 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_23 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_24 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_25 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_26 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_27 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_28 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_29 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_3 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_30 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_31 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_32 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_33 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_34 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_35 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_36 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_37 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_38 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_39 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_4 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_40 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_41 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_42 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_43 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_44 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_45 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_46 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_47 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_48 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_49 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_5 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_50 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_51 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_52 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_53 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_54 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_6 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_7 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_8 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_9 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 49.41 | 49.41 | 3.241 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.385 | 0.305 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.385 | 0.305 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 3.241 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 3.241 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 3.241 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 3.241 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 19.6 | 19.6 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 19.6 | 19.6 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2233.52 | 3.22 | 0.386 | 0.303
North Total or Average |  |  | 753.18 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 1480.33 | 3.22 | 0.386 | 0.303
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1202819.02 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 1009191.87 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 490687.86 | 331745.83 | 158942.03 | 0.68 | 3.25
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 121232.87 | 81963.51 | 39269.36 | 0.68 | 3.51
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 196275.14 | 132698.33 | 63576.81 | 0.68 | 3.49
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13442.32 | 9088.13 | 4354.19 | 0.68 | 3.65
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 111477.74 | 75368.23 | 36109.51 | 0.68 | 3.51
VAV_OTHER_COOLC | Coil:Cooling:Water | 284050.07 | 185327.02 | 98723.05 | 0.65 | -
VAV_POD_1_COOLC | Coil:Cooling:Water | 252214.07 | 158920.87 | 93293.2 | 0.63 | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 247737.49 | 155955.4 | 91782.09 | 0.63 | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 264643.78 | 167030.4 | 97613.39 | 0.63 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6381.81 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8830.58 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5120.41 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7462.77 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5026.42 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7423.89 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5030.9 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7444.42 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4665.21 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7073.16 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4643.91 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7072.91 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4716.11 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7116.14 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4756.36 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8962.44 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3267.95 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8804.66 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3335.05 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8965.83 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29330.66 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2889.26 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6904.85 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16889.67 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 31959.68 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12552.16 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8628.77 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11362.95 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19537.14 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11360.35 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19242.7 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11360.35 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 22756.78 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11360.35 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 17015.76 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11360.35 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 17017.57 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11360.35 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20730.06 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11096.15 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19647.15 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 1531107.56 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 315699.16 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 612443.02 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 41944.47 | 0.8
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 347847.23 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 130278.73 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 86105.83 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 84251.44 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 90971.77 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.88 | 9312.17 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.54 | 627.88 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 12.36 | 20949.45 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.17 | 15331.12 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8 | 15000.95 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.63 | 16197.5 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 11022.17 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 5557.04 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 289115.8522 | 392.08 | 423.4877 | 0 | 0.0034 | 277877.9673 | 112456.1111
February | 239384.4854 | 332.4045 | 375.933 | 0 | 0.003 | 246732.743 | 93854.7341
March | 223792.1016 | 334.4181 | 428.5033 | 0 | 0.0033 | 281401.9218 | 90003.5271
April | 161344.2071 | 266.4651 | 391.5226 | 0 | 0.0029 | 257262.4285 | 67313.0616
May | 169868.3561 | 298.294 | 470.0077 | 0 | 0.0035 | 308914.2939 | 72566.1116
June | 194863.7867 | 351.4441 | 569.3109 | 0 | 0.0042 | 374218.5854 | 84128.798
July | 137393.2209 | 248.9025 | 405.0159 | 0 | 0.003 | 266228.6051 | 59422.9304
August | 145472.8648 | 263.5327 | 428.8111 | 0 | 0.0031 | 281869.8475 | 62916.7385
September | 151787.8494 | 269.4457 | 429.429 | 0 | 0.0031 | 282255.3494 | 65119.6505
October | 169995.3433 | 280.2482 | 410.8731 | 0 | 0.0031 | 269974.9978 | 70874.1098
November | 208561.5915 | 312.892 | 403.3565 | 0 | 0.0031 | 264894.8929 | 83996.0823
December | 254111.7733 | 355.8906 | 408.9471 | 0 | 0.0032 | 268421.8556 | 99919.0276
Annual Sum or Average | 2345690 | 3706.0176 | 5145.1979 | 0 | 0.0388 | 3380050 | 962570.8825
Minimum of Months | 137393.2209 | 248.9025 | 375.933 | 0 | 0.0029 | 246732.743 | 59422.9304
Maximum of Months | 289115.8522 | 392.08 | 569.3109 | 0 | 0.0042 | 374218.5854 | 112456.1111
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 644795000000 | 455033.529 | 05-JAN-11:09 | 220879.908 | 151653.867 | 72729.926 | 0 | 0 | 0 | 3856.297 | 0 | 0 | 0 | 0 | 0 | 5913.531 | 0 | 0
February | 572525000000 | 453260.266 | 03-FEB-11:09 | 220879.908 | 151653.867 | 72729.926 | 0 | 0 | 0 | 2070.326 | 0 | 0 | 0 | 0 | 0 | 5926.239 | 0 | 0
March | 652972000000 | 469605.303 | 23-MAR-13:00 | 220879.908 | 145652.643 | 76901.653 | 0 | 20751.579 | 0 | 691.351 | 0 | 0 | 0 | 0 | 0 | 4728.168 | 0 | 0
April | 596958000000 | 564040.269 | 14-APR-15:00 | 220879.908 | 133019.064 | 77476.825 | 0 | 126820.134 | 0 | 1081.146 | 0 | 0 | 0 | 0 | 0 | 4763.191 | 0 | 0
May | 716812000000 | 865683.594 | 31-MAY-11:00 | 220879.908 | 151653.867 | 95872.283 | 0 | 386985.877 | 0 | 4904.346 | 0 | 0 | 0 | 0 | 0 | 5387.313 | 0 | 0
June | 868346000000 | 1098079.335 | 29-JUN-14:00 | 220879.908 | 137835.548 | 105712.926 | 0 | 619548.244 | 0 | 8603.407 | 0 | 0 | 0 | 0 | 0 | 5499.302 | 0 | 0
July | 617763000000 | 855784.023 | 13-JUL-15:00 | 122711.06 | 73183.824 | 81445.13 | 0 | 568008.682 | 0 | 5355.598 | 0 | 0 | 0 | 0 | 0 | 5079.73 | 0 | 0
August | 654058000000 | 836354.354 | 25-AUG-15:00 | 122711.06 | 73183.824 | 83725.025 | 0 | 546180.829 | 0 | 5542.093 | 0 | 0 | 0 | 0 | 0 | 5011.524 | 0 | 0
September | 654952000000 | 857646.107 | 14-SEP-14:00 | 220879.908 | 137835.548 | 102289.252 | 0 | 385901.655 | 0 | 5381.688 | 0 | 0 | 0 | 0 | 0 | 5358.056 | 0 | 0
October | 626457000000 | 590589.063 | 06-OCT-15:09 | 220879.908 | 133019.064 | 80445.009 | 0 | 148798.724 | 0 | 2587.737 | 0 | 0 | 0 | 0 | 0 | 4858.621 | 0 | 0
November | 614669000000 | 499271.085 | 02-NOV-14:00 | 220879.908 | 137835.548 | 81907.475 | 0 | 52723.912 | 0 | 1089.763 | 0 | 0 | 0 | 0 | 0 | 4834.479 | 0 | 0
December | 622853000000 | 452467.884 | 20-DEC-11:09 | 220879.908 | 151653.867 | 72729.926 | 0 | 0 | 0 | 1281.507 | 0 | 0 | 0 | 0 | 0 | 5922.676 | 0 | 0
Annual Sum or Average | 7843160000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 572525000000 | 452467.884 |  | 122711.06 | 73183.824 | 72729.926 | 0 | 0 | 0 | 691.351 | 0 | 0 | 0 | 0 | 0 | 4728.168 | 0 | 0
Maximum of Months | 868346000000 | 1098079.335 |  | 220879.908 | 151653.867 | 105712.926 | 0 | 619548.244 | 0 | 8603.407 | 0 | 0 | 0 | 0 | 0 | 5926.239 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 142696.9 | 94678.89 | 0 | 237375.8
Cost per Total Building Area ($/m2) | 7.28 | 4.83 | 0 | 12.12
Cost per Net Conditioned Building Area ($/m2) | 7.28 | 4.83 | 0 | 12.12

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 17121 | 873.88 | 873.88
Net Site Energy | 17121 | 873.88 | 873.88
Total Source Energy | 36389.19 | 1857.35 | 1857.35
Net Source Energy | 36389.19 | 1857.35 | 1857.35
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 8910.75 | 0 | 0 | 0 | 0
Cooling | 385.28 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3382.14 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 141.84 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1085.78 | 0 | 0 | 0 | 0 | 0
Pumps | 15.72 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 435.27 | 0 | 0 | 0 | 2677.93
Refrigeration | 132.99 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7421.58 | 9699.42 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 9.68 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 266.35 | 15.06 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 15.06 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 15.06 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 80.28 | 15.06 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 12.91 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 13.99 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 13.99 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 13.99 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 16.14 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 16.14 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.5266 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.5266 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.385 | 0.305 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.385 | 0.305 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 72.8 | 72.8 | 3.241 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 72.8 | 72.8 | 3.241 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 36.4 | 36.4 | 3.241 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
GYM_ZN_1_FLR_2_SKYLIGHT_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_10 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_11 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_12 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_13 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_14 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_15 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_16 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_17 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_18 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_19 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_20 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_21 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_22 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_23 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_24 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_25 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_26 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_27 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_28 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_29 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_3 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_30 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_31 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_32 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_33 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_34 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_35 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_36 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_37 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_38 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_39 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_4 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_40 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_41 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_42 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_43 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_44 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_45 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_46 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_47 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_48 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_49 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_5 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_50 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_51 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_52 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_53 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_54 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_6 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_7 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_8 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_9 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_2_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 49.41 | 49.41 | 3.241 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.385 | 0.305 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.385 | 0.305 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 3.241 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 3.241 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 3.241 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 3.241 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 19.6 | 19.6 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 19.6 | 19.6 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2233.52 | 3.22 | 0.386 | 0.303
North Total or Average |  |  | 753.18 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 1480.33 | 3.22 | 0.386 | 0.303
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 585124.92 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 904571.97 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 381405.58 | 284645.16 | 96760.41 | 0.75 | 3.51
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 88336.69 | 66307.58 | 22029.11 | 0.75 | 3.88
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 130839.27 | 104495.47 | 26343.8 | 0.8 | 4.14
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9839.63 | 7290.64 | 2548.99 | 0.74 | 3.84
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 88148.52 | 65313.34 | 22835.19 | 0.74 | 3.83
VAV_OTHER_COOLC | Coil:Cooling:Water | 213420.76 | 137883.55 | 75537.21 | 0.65 | -
VAV_POD_1_COOLC | Coil:Cooling:Water | 147550.27 | 94348.32 | 53201.95 | 0.64 | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 144014.3 | 92012.57 | 52001.73 | 0.64 | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 156574.63 | 100068.49 | 56506.15 | 0.64 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6244.17 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8786.7 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4296.84 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6729.28 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4196.35 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6685.1 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4202.12 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6707.53 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3753.2 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6242.37 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3725.27 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6238 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3800.23 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6285.45 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3622.38 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8200.29 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3190.45 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8225.56 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3247.1 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8261.76 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 26170.49 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2542.33 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6888.69 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16702.49 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 32171.76 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11417.29 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7610.17 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10156.02 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 17515.97 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10156.02 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 17190.6 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10156.02 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20725.44 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10156.02 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14508.47 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10156.02 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14490.36 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10156.02 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 18225.23 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8977.1 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 17499.43 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 1395210.11 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 282392.73 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 558084.04 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 35382.31 | 0.8
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 316973.14 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 113459.37 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 76742.45 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 74784.09 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 81702.54 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.64 | 8849.05 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.5 | 581.24 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 11.79 | 19968.55 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.97 | 14954.92 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.77 | 14573.29 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.49 | 15921.49 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 5361.86 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 4980.96 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 255030.548 | 362.3666 | 474.4663 | 0 | 0.0035 | 11243200 | 100917.2294
February | 211043.0384 | 308.5055 | 423.8758 | 0 | 0.0031 | 10046400 | 84346.2282
March | 211555.4297 | 326.6178 | 487.6994 | 0 | 0.0035 | 11563000 | 86229.4162
April | 177778.3878 | 282.4512 | 438.6977 | 0 | 0.0031 | 10402700 | 73233.4944
May | 175006.7036 | 294.0593 | 489.7644 | 0 | 0.0034 | 11616500 | 73639.4856
June | 183982.8982 | 318.4432 | 548.5233 | 0 | 0.0038 | 13011700 | 78315.6086
July | 128865.9988 | 226.7242 | 397.5037 | 0 | 0.0028 | 9429830 | 55209.7368
August | 129555.8134 | 225.777 | 391.8171 | 0 | 0.0027 | 9294620 | 55296.4045
September | 163404.0626 | 279.3428 | 474.5776 | 0 | 0.0033 | 11257100 | 69219.2841
October | 176192.1624 | 288.755 | 466.6951 | 0 | 0.0033 | 11068200 | 73433.0226
November | 203614.4287 | 310.279 | 454.6422 | 0 | 0.0033 | 10778400 | 82598.4173
December | 241546.0158 | 345.8463 | 458.9252 | 0 | 0.0034 | 10875600 | 95836.4633
Annual Sum or Average | 2257580 | 3569.1681 | 5507.188 | 0 | 0.0392 | 130587000 | 928274.7909
Minimum of Months | 128865.9988 | 225.777 | 391.8171 | 0 | 0.0027 | 9294620 | 55209.7368
Maximum of Months | 255030.548 | 362.3666 | 548.5233 | 0 | 0.0038 | 13011700 | 100917.2294
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 638979000000 | 456288.107 | 05-JAN-08:09 | 220879.908 | 145652.643 | 72305.488 | 0 | 0 | 9037 | 4510.775 | 0 | 0 | 0 | 0 | 0 | 3902.294 | 0 | 0
February | 570964000000 | 471240.08 | 02-FEB-14:00 | 220879.908 | 145652.643 | 75345.262 | 0 | 23806.578 | 0 | 742.822 | 0 | 0 | 0 | 0 | 0 | 4812.866 | 0 | 0
March | 657152000000 | 538573.578 | 30-MAR-15:00 | 220879.908 | 133019.064 | 81205.909 | 0 | 97355.662 | 0 | 1418.363 | 0 | 0 | 0 | 0 | 0 | 4694.672 | 0 | 0
April | 591211000000 | 510715.696 | 06-APR-15:00 | 220879.908 | 133019.064 | 76999.852 | 0 | 74203.182 | 0 | 990.503 | 0 | 0 | 0 | 0 | 0 | 4623.188 | 0 | 0
May | 660194000000 | 632011.417 | 16-MAY-15:00 | 220879.908 | 133019.064 | 86609.312 | 0 | 183863.288 | 0 | 2753.579 | 0 | 0 | 0 | 0 | 0 | 4886.266 | 0 | 0
June | 739484000000 | 870949.863 | 30-JUN-15:00 | 220879.908 | 133019.064 | 111978.345 | 0 | 394314.785 | 0 | 5476.528 | 0 | 0 | 0 | 0 | 0 | 5281.233 | 0 | 0
July | 535920000000 | 659833.771 | 21-JUL-15:00 | 122711.06 | 73183.824 | 105811.81 | 0 | 348305.942 | 0 | 4872.651 | 0 | 0 | 0 | 0 | 0 | 4948.485 | 0 | 0
August | 528235000000 | 591386.49 | 09-AUG-15:00 | 122711.06 | 73183.824 | 84847.492 | 0 | 301163.455 | 0 | 4583.886 | 0 | 0 | 0 | 0 | 0 | 4896.773 | 0 | 0
September | 639765000000 | 700584.745 | 12-SEP-13:00 | 220879.908 | 145652.643 | 105671.239 | 0 | 217985.296 | 0 | 5116.473 | 0 | 0 | 0 | 0 | 0 | 5279.186 | 0 | 0
October | 629032000000 | 593595.846 | 06-OCT-15:00 | 220879.908 | 133019.064 | 88607.703 | 0 | 143684.047 | 0 | 2596.312 | 0 | 0 | 0 | 0 | 0 | 4808.813 | 0 | 0
November | 612564000000 | 459274.863 | 21-NOV-11:39 | 220879.908 | 151653.867 | 72554.692 | 0 | 7093.316 | 0 | 365.548 | 0 | 0 | 0 | 0 | 0 | 6727.532 | 0 | 0
December | 618085000000 | 455477.301 | 18-DEC-08:09 | 220879.908 | 145652.643 | 72305.488 | 0 | 0 | 9037 | 3724.664 | 0 | 0 | 0 | 0 | 0 | 3877.598 | 0 | 0
Annual Sum or Average | 7421580000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 528235000000 | 455477.301 |  | 122711.06 | 73183.824 | 72305.488 | 0 | 0 | 0 | 365.548 | 0 | 0 | 0 | 0 | 0 | 3877.598 | 0 | 0
Maximum of Months | 739484000000 | 870949.863 |  | 220879.908 | 151653.867 | 111978.345 | 0 | 394314.785 | 9037 | 5476.528 | 0 | 0 | 0 | 0 | 0 | 6727.532 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 162255.98 | 78972.66 | 0 | 241228.64
Cost per Total Building Area ($/m2) | 8.28 | 4.03 | 0 | 12.31
Cost per Net Conditioned Building Area ($/m2) | 8.28 | 4.03 | 0 | 12.31

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 21686.06 | 1106.88 | 1106.88
Net Site Energy | 21686.06 | 1106.88 | 1106.88
Total Source Energy | 40971.44 | 2091.23 | 2091.23
Net Source Energy | 40971.44 | 2091.23 | 2091.23
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 13474.18 | 0 | 0 | 0 | 0
Cooling | 301.73 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3382.14 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 141.76 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1121.09 | 0 | 0 | 0 | 0 | 0
Pumps | 17.77 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 485.25 | 0 | 0 | 0 | 2677.93
Refrigeration | 130.92 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7373.25 | 14312.82 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 9.68 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 266.35 | 15.06 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 15.06 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 15.06 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 80.28 | 15.06 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 12.91 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 13.99 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 13.99 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 13.99 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 16.14 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 16.14 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.5266 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.5266 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.487 | 0.409 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.487 | 0.409 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.487 | 0.409 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 72.8 | 72.8 | 3.241 | 0.487 | 0.409 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.487 | 0.409 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 72.8 | 72.8 | 3.241 | 0.487 | 0.409 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.487 | 0.409 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.487 | 0.409 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.487 | 0.409 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.487 | 0.409 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 36.4 | 36.4 | 3.241 | 0.487 | 0.409 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.487 | 0.409 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.487 | 0.409 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.487 | 0.409 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.487 | 0.409 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.487 | 0.409 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.487 | 0.409 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.487 | 0.409 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.487 | 0.409 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.487 | 0.409 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.487 | 0.409 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.487 | 0.409 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.487 | 0.409 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.487 | 0.409 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.487 | 0.409 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.487 | 0.409 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.487 | 0.409 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.487 | 0.409 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.487 | 0.409 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.487 | 0.409 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.487 | 0.409 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.487 | 0.409 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.487 | 0.409 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.487 | 0.409 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.487 | 0.409 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.487 | 0.409 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.487 | 0.409 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.487 | 0.409 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.487 | 0.409 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.487 | 0.409 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.487 | 0.409 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 3.241 | 0.487 | 0.409 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
GYM_ZN_1_FLR_2_SKYLIGHT_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_10 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_11 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_12 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_13 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_14 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_15 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_16 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_17 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_18 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_19 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_20 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_21 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_22 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_23 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_24 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_25 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_26 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_27 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_28 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_29 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_3 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_30 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_31 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_32 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_33 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_34 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_35 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_36 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_37 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_38 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_39 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_4 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_40 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_41 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_42 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_43 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_44 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_45 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_46 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_47 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_48 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_49 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_5 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_50 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_51 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_52 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_53 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_54 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_6 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_7 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_8 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_9 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_2_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.487 | 0.409 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 49.41 | 49.41 | 3.241 | 0.487 | 0.409 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 3.241 | 0.487 | 0.409 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.487 | 0.409 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.487 | 0.409 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 3.241 | 0.487 | 0.409 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 3.241 | 0.487 | 0.409 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 3.241 | 0.487 | 0.409 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 3.241 | 0.487 | 0.409 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.487 | 0.409 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.487 | 0.409 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.487 | 0.409 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.487 | 0.409 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.487 | 0.409 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.487 | 0.409 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.487 | 0.409 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.487 | 0.409 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.487 | 0.409 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.487 | 0.409 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.487 | 0.409 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.487 | 0.409 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.487 | 0.409 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 19.6 | 19.6 | 3.241 | 0.487 | 0.409 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 3.241 | 0.487 | 0.409 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 19.6 | 19.6 | 3.241 | 0.487 | 0.409 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2233.52 | 3.22 | 0.496 | 0.422
North Total or Average |  |  | 753.18 | 3.24 | 0.487 | 0.409
Non-North Total or Average |  |  | 1480.33 | 3.22 | 0.5 | 0.428
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 976953.86 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 1025116.77 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 490687.86 | 331745.83 | 158942.03 | 0.68 | 3.25
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 134088 | 90654.64 | 43433.35 | 0.68 | 3.49
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 196275.14 | 132698.33 | 63576.81 | 0.68 | 3.49
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12849.76 | 8687.51 | 4162.25 | 0.68 | 3.65
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 111477.74 | 75368.23 | 36109.51 | 0.68 | 3.51
VAV_OTHER_COOLC | Coil:Cooling:Water | 249035.14 | 163918.65 | 85116.49 | 0.66 | -
VAV_POD_1_COOLC | Coil:Cooling:Water | 169994.37 | 110240.56 | 59753.81 | 0.65 | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 160817.94 | 104192.89 | 56625.04 | 0.65 | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 180923.5 | 117424.88 | 63498.62 | 0.65 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6397.66 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8949.08 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5074.37 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7790.67 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4950.87 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7738.23 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4957.02 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7761.79 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4407.35 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7202.33 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4381.44 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7202.02 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4480.68 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7256.89 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3963.17 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8795.47 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3286.9 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8602.15 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3341.32 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8774.86 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 28018.88 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2671.65 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7076.31 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17263.16 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 32855.09 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11456 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7936.83 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11671.95 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20495.24 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11123.39 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20073.51 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11123.39 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 23586.63 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11123.39 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 15634.15 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11123.39 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 15635.95 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11123.39 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19429.64 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10715.79 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19838.08 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 1567205.23 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 333322.83 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 626882.09 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 41040.79 | 0.8
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 356048.14 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 128968.12 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 89425.31 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 86775.91 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 93979.13 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.4 | 10129.83 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.52 | 600.21 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 11.89 | 20151.5 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.25 | 15471.33 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8 | 15012.96 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.67 | 16259.18 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8952.43 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 5644.73 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 291900.9936 | 394.9669 | 424.6687 | 0 | 0.0034 | 278646.2139 | 113454.3462
February | 246954.0569 | 340.5255 | 380.0385 | 0 | 0.003 | 249410.422 | 96594.0681
March | 248131.4238 | 357.4653 | 431.7228 | 0 | 0.0034 | 283439.4266 | 98518.6237
April | 180634.7852 | 282.8381 | 387.9086 | 0 | 0.0029 | 254817.3828 | 73880.8633
May | 170302.0486 | 283.9198 | 421.9231 | 0 | 0.0031 | 277250.1573 | 71304.6
June | 163690.22 | 291.2573 | 465.3268 | 0 | 0.0034 | 305852.9641 | 70291.2741
July | 123001.4512 | 221.5906 | 358.5544 | 0 | 0.0026 | 235683.4881 | 53079.9556
August | 120952.869 | 213.5993 | 338.5788 | 0 | 0.0025 | 222536.9448 | 51784.8191
September | 153522.0133 | 262.4249 | 401.4506 | 0 | 0.003 | 263826.2956 | 64898.2884
October | 180016.041 | 288.3305 | 407.6187 | 0 | 0.0031 | 267798.1451 | 74245.4011
November | 216505.4274 | 321.273 | 407.204 | 0 | 0.0031 | 267401.4544 | 86857.3271
December | 266301.92 | 368.1035 | 412.7408 | 0 | 0.0033 | 270878.6865 | 104247.7774
Annual Sum or Average | 2361910 | 3626.2946 | 4837.7358 | 0 | 0.0368 | 3177540 | 959157.344
Minimum of Months | 120952.869 | 213.5993 | 338.5788 | 0 | 0.0025 | 222536.9448 | 51784.8191
Maximum of Months | 291900.9936 | 394.9669 | 465.3268 | 0 | 0.0034 | 305852.9641 | 113454.3462
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 646578000000 | 456518.128 | 09-JAN-11:09 | 220879.908 | 151653.867 | 73593.029 | 0 | 0 | 0 | 4498.213 | 0 | 0 | 0 | 0 | 0 | 5893.111 | 0 | 0
February | 578738000000 | 455998.115 | 01-FEB-11:09 | 220879.908 | 151653.867 | 73593.029 | 0 | 0 | 0 | 3947.275 | 0 | 0 | 0 | 0 | 0 | 5924.036 | 0 | 0
March | 657700000000 | 453430.796 | 01-MAR-11:39 | 220879.908 | 151653.867 | 74331.101 | 0 | 0 | 0 | 576.62 | 0 | 0 | 0 | 0 | 0 | 5989.3 | 0 | 0
April | 591285000000 | 476787.335 | 04-APR-14:00 | 220879.908 | 137835.548 | 79820.581 | 0 | 32594.779 | 0 | 932.951 | 0 | 0 | 0 | 0 | 0 | 4723.569 | 0 | 0
May | 643338000000 | 633302.131 | 31-MAY-15:00 | 220879.908 | 133019.064 | 88346.667 | 0 | 183166.789 | 0 | 3045.018 | 0 | 0 | 0 | 0 | 0 | 4844.685 | 0 | 0
June | 709709000000 | 915534.518 | 14-JUN-15:09 | 220879.908 | 133019.064 | 110108.315 | 0 | 437601.561 | 0 | 8599.024 | 0 | 0 | 0 | 0 | 0 | 5326.646 | 0 | 0
July | 546886000000 | 742971.695 | 06-JUL-14:00 | 122711.06 | 78000.308 | 102359.364 | 0 | 426610.839 | 0 | 8131.331 | 0 | 0 | 0 | 0 | 0 | 5158.794 | 0 | 0
August | 516380000000 | 665237.934 | 11-AUG-14:00 | 122711.06 | 78000.308 | 80694.754 | 0 | 372243.187 | 0 | 6498.666 | 0 | 0 | 0 | 0 | 0 | 5089.96 | 0 | 0
September | 612189000000 | 788543.57 | 07-SEP-15:09 | 220879.908 | 133019.064 | 100702.631 | 0 | 320816.095 | 0 | 7915.256 | 0 | 0 | 0 | 0 | 0 | 5210.615 | 0 | 0
October | 621405000000 | 496539.398 | 06-OCT-14:00 | 220879.908 | 137835.548 | 86409.096 | 0 | 45233.078 | 0 | 1396.624 | 0 | 0 | 0 | 0 | 0 | 4785.145 | 0 | 0
November | 620485000000 | 453628.946 | 09-NOV-11:39 | 220879.908 | 151653.867 | 73650.54 | 0 | 681.295 | 0 | 154.048 | 0 | 0 | 0 | 0 | 0 | 6609.289 | 0 | 0
December | 628554000000 | 453996.83 | 20-DEC-11:09 | 220879.908 | 151653.867 | 73593.029 | 0 | 0 | 0 | 1940.398 | 0 | 0 | 0 | 0 | 0 | 5929.628 | 0 | 0
Annual Sum or Average | 7373250000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 516380000000 | 453430.796 |  | 122711.06 | 78000.308 | 73593.029 | 0 | 0 | 0 | 154.048 | 0 | 0 | 0 | 0 | 0 | 4723.569 | 0 | 0
Maximum of Months | 709709000000 | 915534.518 |  | 220879.908 | 151653.867 | 110108.315 | 0 | 437601.561 | 0 | 8599.024 | 0 | 0 | 0 | 0 | 0 | 6609.289 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 129615.07 | 112617.97 | 0 | 242233.04
Cost per Total Building Area ($/m2) | 6.62 | 5.75 | 0 | 12.36
Cost per Net Conditioned Building Area ($/m2) | 6.62 | 5.75 | 0 | 12.36

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 31403.2 | 1602.86 | 1602.86
Net Site Energy | 31403.2 | 1602.86 | 1602.86
Total Source Energy | 52501.77 | 2679.76 | 2679.76
Net Source Energy | 52501.77 | 2679.76 | 2679.76
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 23159.04 | 0 | 0 | 0 | 0
Cooling | 153.66 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3382.14 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 140.9 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1235.26 | 0 | 0 | 0 | 0 | 0
Pumps | 24.65 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 548.24 | 0 | 0 | 0 | 2677.93
Refrigeration | 128.09 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7342.53 | 24060.67 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 9.68 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 266.35 | 15.06 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 15.06 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 15.06 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 80.28 | 15.06 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 12.91 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 13.99 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 13.99 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 13.99 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 16.14 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 16.14 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.5266 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.5266 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 2.615 | 0.702 | 0.633 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 2.615 | 0.702 | 0.633 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 2.615 | 0.702 | 0.633 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 72.8 | 72.8 | 2.615 | 0.702 | 0.633 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 2.615 | 0.702 | 0.633 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 72.8 | 72.8 | 2.615 | 0.702 | 0.633 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 2.615 | 0.702 | 0.633 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 2.615 | 0.702 | 0.633 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 2.615 | 0.702 | 0.633 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 2.615 | 0.702 | 0.633 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 36.4 | 36.4 | 2.615 | 0.702 | 0.633 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 2.615 | 0.702 | 0.633 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 2.615 | 0.702 | 0.633 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 2.615 | 0.702 | 0.633 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 2.615 | 0.702 | 0.633 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 2.615 | 0.702 | 0.633 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 2.615 | 0.702 | 0.633 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 2.615 | 0.702 | 0.633 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 2.615 | 0.702 | 0.633 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 2.615 | 0.702 | 0.633 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 2.615 | 0.702 | 0.633 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 2.615 | 0.702 | 0.633 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 2.615 | 0.702 | 0.633 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 2.615 | 0.702 | 0.633 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 2.615 | 0.702 | 0.633 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 2.615 | 0.702 | 0.633 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 2.615 | 0.702 | 0.633 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 2.615 | 0.702 | 0.633 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 2.615 | 0.702 | 0.633 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 2.615 | 0.702 | 0.633 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 2.615 | 0.702 | 0.633 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 2.615 | 0.702 | 0.633 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 2.615 | 0.702 | 0.633 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 2.615 | 0.702 | 0.633 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 2.615 | 0.702 | 0.633 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 2.615 | 0.702 | 0.633 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 2.615 | 0.702 | 0.633 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 2.615 | 0.702 | 0.633 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 2.615 | 0.702 | 0.633 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 2.615 | 0.702 | 0.633 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 2.615 | 0.702 | 0.633 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 7 | 7 | 2.615 | 0.702 | 0.633 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
GYM_ZN_1_FLR_2_SKYLIGHT_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_10 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_11 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_12 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_13 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_14 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_15 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_16 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_17 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_18 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_19 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_20 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_21 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_22 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_23 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_24 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_25 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_26 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_27 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_28 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_29 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_3 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_30 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_31 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_32 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_33 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_34 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_35 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_36 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_37 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_38 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_39 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_4 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_40 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_41 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_42 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_43 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_44 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_45 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_46 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_47 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_48 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_49 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_5 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_50 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_51 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_52 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_53 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_54 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_6 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_7 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_8 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_9 | WINDOW-90.1-2004-NONRES-FIXED | 1.49 | 1.49 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_2_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 2.615 | 0.702 | 0.633 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 49.41 | 49.41 | 2.615 | 0.702 | 0.633 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 33.6 | 33.6 | 2.615 | 0.702 | 0.633 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 2.615 | 0.702 | 0.633 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 2.615 | 0.702 | 0.633 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 2.615 | 0.702 | 0.633 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 2.615 | 0.702 | 0.633 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 2.615 | 0.702 | 0.633 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 2.615 | 0.702 | 0.633 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 2.615 | 0.702 | 0.633 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 2.615 | 0.702 | 0.633 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 2.615 | 0.702 | 0.633 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 2.615 | 0.702 | 0.633 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 2.615 | 0.702 | 0.633 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 2.615 | 0.702 | 0.633 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 2.615 | 0.702 | 0.633 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 2.615 | 0.702 | 0.633 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 2.615 | 0.702 | 0.633 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 2.615 | 0.702 | 0.633 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 2.615 | 0.702 | 0.633 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 2.615 | 0.702 | 0.633 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 2.615 | 0.702 | 0.633 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 19.6 | 19.6 | 2.615 | 0.702 | 0.633 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 53.2 | 53.2 | 2.615 | 0.702 | 0.633 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 19.6 | 19.6 | 2.615 | 0.702 | 0.633 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2233.52 | 2.61 | 0.704 | 0.639
North Total or Average |  |  | 753.18 | 2.61 | 0.702 | 0.633
Non-North Total or Average |  |  | 1480.33 | 2.61 | 0.705 | 0.642
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 692550.14 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 1580366.57 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 327098.16 | 261238.67 | 65859.49 | 0.8 | 3.73
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 96980.4 | 77453.91 | 19526.49 | 0.8 | 4.14
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 130839.27 | 104495.47 | 26343.8 | 0.8 | 4.14
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8884.32 | 7095.51 | 1788.81 | 0.8 | 4.04
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 74312.34 | 59349.94 | 14962.4 | 0.8 | 4.18
VAV_OTHER_COOLC | Coil:Cooling:Water | 285880.55 | 201931.65 | 83948.91 | 0.71 | -
VAV_POD_1_COOLC | Coil:Cooling:Water | 237222.65 | 167352.8 | 69869.85 | 0.71 | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 228306.09 | 161072.39 | 67233.7 | 0.71 | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 244679.88 | 172185.72 | 72494.16 | 0.7 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7296.09 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9793.33 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7953.43 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10837.14 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7753.42 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10750.6 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7766.01 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10782.78 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5193.36 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8098.83 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5168.5 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8102.9 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5347.86 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8194.93 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4341.69 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8659.13 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4007.48 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8677.82 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4055.61 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8708.34 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29046.82 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6302.45 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10796.26 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 21401.27 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 34789.5 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9946.82 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6333.91 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 25824.35 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 37422.16 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 24091.59 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 36438.08 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 24209.73 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 40067.95 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11519.22 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14668.07 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11519.22 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14677.68 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11519.22 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 18802.79 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 20402.06 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 31487.23 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 1940738.03 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 415837.03 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 776295.21 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 52712.42 | 0.8
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 440909.81 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 181207.65 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 149865.26 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 144401.44 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 154045.07 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.86 | 10990.65 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.54 | 622.52 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 13.45 | 22787.63 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 11.12 | 18846.19 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1017.59 | 10.72 | 18438.46 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 11.43 | 19371.82 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 6346.26 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8702.17 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 373451.039 | 384.3999 | 950.7986 | 0 | 0.0037 | 190582.3305 | 136237.4234
February | 313158.5223 | 324.7951 | 848.664 | 0 | 0.0033 | 170130.8616 | 114620.1594
March | 283157.2942 | 302.4218 | 950.2687 | 0 | 0.0035 | 190569.1868 | 104984.7075
April | 194521.8261 | 216.8536 | 843.1401 | 0 | 0.003 | 169143.9605 | 73521.7943
May | 154464.8427 | 183.8118 | 912.4906 | 0 | 0.0031 | 183114.41 | 60169.0034
June | 147437.906 | 180.8171 | 983.2688 | 0 | 0.0033 | 197337.4902 | 58257.7377
July | 99798.147 | 122.6975 | 671.9515 | 0 | 0.0023 | 134858.5302 | 39480.6775
August | 108645.1448 | 130.5322 | 667.8707 | 0 | 0.0023 | 134029.7577 | 42512.4259
September | 154850.5676 | 180.231 | 830.252 | 0 | 0.0029 | 166596.3604 | 59697.5836
October | 222619.2764 | 244.6411 | 890.9581 | 0 | 0.0032 | 178719.1714 | 83597.4747
November | 303810.6481 | 319.427 | 913.8594 | 0 | 0.0035 | 183235.0324 | 111864.6001
December | 335313.0073 | 348.5643 | 925.2627 | 0 | 0.0036 | 185492.8468 | 122850.8001
Annual Sum or Average | 2691230 | 2939.1922 | 10388.7853 | 0 | 0.0378 | 2083810 | 1007790
Minimum of Months | 99798.147 | 122.6975 | 667.8707 | 0 | 0.0023 | 134029.7577 | 39480.6775
Maximum of Months | 373451.039 | 384.3999 | 983.2688 | 0 | 0.0037 | 197337.4902 | 136237.4234
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 671537000000 | 471852.929 | 02-JAN-11:09 | 220879.908 | 151653.867 | 75729.399 | 0 | 0 | 9037 | 8708.312 | 0 | 0 | 0 | 0 | 0 | 5844.443 | 0 | 0
February | 599474000000 | 463475.554 | 03-FEB-08:09 | 220879.908 | 145652.643 | 75729.399 | 0 | 0 | 9037 | 8297.543 | 0 | 0 | 0 | 0 | 0 | 3879.061 | 0 | 0
March | 671491000000 | 462191.574 | 14-MAR-07:10 | 220879.908 | 145652.643 | 75729.399 | 0 | 0 | 9037 | 7004.298 | 0 | 0 | 0 | 0 | 0 | 3888.325 | 0 | 0
April | 595997000000 | 460372.603 | 24-APR-11:00 | 220879.908 | 151653.867 | 83321.989 | 0 | 0 | 0 | 170.11 | 0 | 0 | 0 | 0 | 0 | 4346.729 | 0 | 0
May | 645223000000 | 563129.907 | 24-MAY-14:00 | 220879.908 | 137835.548 | 101787.907 | 0 | 95545.684 | 0 | 2198.738 | 0 | 0 | 0 | 0 | 0 | 4882.123 | 0 | 0
June | 695340000000 | 711582.062 | 20-JUN-14:00 | 220879.908 | 137835.548 | 103934.396 | 0 | 240308.276 | 0 | 3446.51 | 0 | 0 | 0 | 0 | 0 | 5177.425 | 0 | 0
July | 475189000000 | 477438.221 | 21-JUL-15:00 | 122711.06 | 73183.824 | 82274.008 | 0 | 192746.522 | 0 | 1823.253 | 0 | 0 | 0 | 0 | 0 | 4699.554 | 0 | 0
August | 472268000000 | 473406.932 | 15-AUG-13:00 | 122711.06 | 84617.158 | 83674.74 | 0 | 173985.246 | 0 | 3483.727 | 0 | 0 | 0 | 0 | 0 | 4935.001 | 0 | 0
September | 587020000000 | 472095.773 | 07-SEP-14:00 | 220879.908 | 137835.548 | 84228.897 | 0 | 23679.789 | 0 | 859.807 | 0 | 0 | 0 | 0 | 0 | 4611.825 | 0 | 0
October | 629736000000 | 457482.23 | 30-OCT-07:10 | 220879.908 | 145652.643 | 75729.399 | 0 | 0 | 9037 | 2299.774 | 0 | 0 | 0 | 0 | 0 | 3883.506 | 0 | 0
November | 645648000000 | 463240.136 | 27-NOV-10:09 | 220879.908 | 151653.867 | 75729.399 | 0 | 0 | 9037 | 1982.823 | 0 | 0 | 0 | 0 | 0 | 3957.138 | 0 | 0
December | 653604000000 | 470320.269 | 29-DEC-11:09 | 220879.908 | 151653.867 | 75729.399 | 0 | 0 | 9037 | 7130.204 | 0 | 0 | 0 | 0 | 0 | 5889.89 | 0 | 0
Annual Sum or Average | 7342530000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 472268000000 | 457482.23 |  | 122711.06 | 73183.824 | 75729.399 | 0 | 0 | 0 | 170.11 | 0 | 0 | 0 | 0 | 0 | 3879.061 | 0 | 0
Maximum of Months | 695340000000 | 711582.062 |  | 220879.908 | 151653.867 | 103934.396 | 0 | 240308.276 | 9037 | 8708.312 | 0 | 0 | 0 | 0 | 0 | 5889.89 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 197543.04 | 99396.5 | 0 | 296939.54
Cost per Total Building Area ($/m2) | 10.08 | 5.07 | 0 | 15.16
Cost per Net Conditioned Building Area ($/m2) | 10.08 | 5.07 | 0 | 15.16

## Picture
DOE Commercial Building Benchmark - Secondary School

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | 14.37 | 80.38 | 3909.96
|  |  | WE, WinterDesign, Hol, Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
|  | Through 9/1 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 8.13 | 49.15
|  |  | WE, WinterDesign, Hol, Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
|  | Through 12/31 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | 14.37 | 80.38
|  |  | WE, WinterDesign, Hol, Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
BLDG_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 13.8 | 85.8 | 4180.91
|  |  | WE, WinterDesign, Hol, Other | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
|  | Through 9/1 | WD, SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 8.25 | 53.25
|  |  | WE, WinterDesign, Hol, Other | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  | Through 12/31 | WD, SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 13.8 | 85.8
|  |  | WE, WinterDesign, Hol, Other | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
KITCHEN_ELEC_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 20.05 | 1045.46
|  |  | WE, WinterDesign, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
|  | Through 9/1 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 20.05
|  |  | WE, WinterDesign, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
|  | Through 12/31 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 20.05
|  |  | WE, WinterDesign, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
KITCHEN_GAS_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 8.16 | 425.49
|  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
|  | Through 9/1 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 8.16
|  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
|  | Through 12/31 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 8.16
|  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.25 | 11.25 | 586.61
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH | Fraction | Through 6/15 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 6.35 | 31.75 | 1366.39
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/15 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 1.95 | 9.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 6.35 | 31.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Extend | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 9.1 | 45.5 | 2255.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 6.5 | 32.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 9.1 | 45.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Offices | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 9.15 | 45.75 | 2203.29
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 5.1 | 25.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 9.15 | 45.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Gym | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75 | 1833.39
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 4.55 | 22.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Auditorium | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 6.5 | 32.5 | 1494.39
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | 2.05 | 10.25
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 6.5 | 32.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Cafeteria | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 7.45 | 37.25 | 1692.57
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | 1.9 | 9.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 7.45 | 37.25
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INFIL_SCH | Fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 17 | 119 | 6205
BLDG_SWH_SCH | Fraction | Through 6/15 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 6.91 | 36.19 | 1599.88
|  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
|  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
|  | Through 9/15 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 2.54 | 14.34
|  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
|  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
|  | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 6.91 | 36.19
|  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
|  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
Showers_SWH_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 7.6 | 41.8 | 1848.37
|  |  | WE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 1.9
|  |  | WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 7.6 | 41.8
|  |  | WE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 1.9
|  |  | WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 26.4 | 184.8 | 7800
|  | Through 09/30 | All | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 14.4 | 100.8
|  | Through 12/31 | All | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 26.4 | 184.8
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PlantOnSched | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Humidity Setpoint Schedule | Humidity | Through 12/31 | All | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1560 | 10920 | 569400
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 03/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 09/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 1608 | 11256 | 586920
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
Kitchen_Exhaust_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 45 | 2137.86
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 7.15 | 35.75
|  |  | WE, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75
|  |  | WE, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 70 | 3650
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 70 | 3650
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HTGSETP_SCH | Temperature | Through 12/31 | SummerDesign | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 3038 | 158410
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | WD | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 454
|  |  | WE, Hol, Other | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
HTGSETP_SCH_Setback | Temperature | Through 12/31 | SummerDesign | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | WD | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
|  |  | WE, Hol, Other | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
CLGSETP_SCH | Temperature | Through 12/31 | SummerDesign | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456 | 4788 | 249660
|  |  | WinterDesign | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WE | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WD, Hol, Other | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 31 | 31 | 31 | 660
CLGSETP_SCH_Setup | Temperature | Through 12/31 | SummerDesign | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456 | 5208 | 271560
|  |  | WinterDesign | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WE | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WD, Hol, Other | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
MinOA_Sched | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 118 | 6152.86
|  |  | WE, WinterDesign, Hol, Other | [24 empty] | 24 | bar: 1 to 24
MinOA_MotorizedDamper_Sched | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 70 | 3650
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MinOA_Kitchen_Sched | On/Off | Through 12/31 | WD, SummerDesign, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 70 | 3650
|  |  | WE, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
Bathrooms_ZN_1_FLR_1 SHW_default Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Bathrooms_ZN_1_FLR_1 SHW_default Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Bathrooms_ZN_1_FLR_1 SHW_default Temp Sched | Temperature | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
Bathrooms_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Bathrooms_ZN_1_FLR_2 SHW_default Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Bathrooms_ZN_1_FLR_2 SHW_default Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Bathrooms_ZN_1_FLR_2 SHW_default Temp Sched | Temperature | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
Bathrooms_ZN_1_FLR_2 SHW_default Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Gym_ZN_1_FLR_1 SHW_default Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Gym_ZN_1_FLR_1 SHW_default Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Gym_ZN_1_FLR_1 SHW_default Temp Sched | Temperature | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
Gym_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_ZN_1_FLR_1 SHW_default Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Kitchen_ZN_1_FLR_1 SHW_default Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Kitchen_ZN_1_FLR_1 SHW_default Temp Sched | Temperature | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
Kitchen_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720