## BuildingSummary
Building Summary Super Market new construction version 1.1_3.1
|  | Value | Data Source
Program
| Building Name | Benchmark Super Market
| Available Fuel Types | gas, electricity
| Principal Building Activity | Food Sales
Form
| Total Floor Area (m2) | 4181 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 1.5
| Number of Floors | 1
| Window Fraction (Window to Wall Ratio) | South: 0.362 East: 0.00 North: 0.00 West: 0.00 Total: 0.109
| Skylight/TDD Percentage | 0.00%
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | Office, DryStorage, Deli, Sales, Produce, Bakery
| Floor to Ceiling Height (m) | 6.1
| Roof type | Insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Mass wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1609.58
| Net Dimensions - Total Area (m2) | 1434.88
| Wall to Skin Ratio | 0.28
Roof
| Construction Type | Insulation entirely above deck | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 4181
| Net Dimensions - Total Area (m2) | 4181
| Roof to Skin Ratio | 0.72
Window
| Dimensions - Total Area (m2) | South: 174.7 East: 0.00 North: 0.00 West: 0.00 Total: 174.7
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab-on-grade
| Dimensions - Total Area (m2) | 4181
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 46.47
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.25 | See Benchmark Technical Report
HVAC
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | Unitary DX | 2003 CBECS
| Fan Control | Constant volume | 2003 CBECS
Service Water Heating
| SWH Type | N/A
| Fuel | N/A
| Thermal Efficiency (%) | N/A
| Temperature Setpoint (ºC ) | N/A
| Water Consumption (m3 ) | N/A

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Office | Yes | 1 | 88.84 | 541.72 | 6.0977 | 115.08 | 0 | 18.5806 | 4.7813 | 11.836 | 8.07 | 0 | 0 | 2.5 | 0.3 | 38.6053 | 0 | 0.40969
DryStorage | Yes | 1 | 621.89 | 3792.03 | 6.0976 | 477.24 | 0 | 27.8709 | 22.3132 | 8.608 | 8.07 | 0 | 0 | 3.8 | 0.6 | 457.9242 | 0 | 0.31547
Deli | Yes | 1 | 224.72 | 1370.24 | 6.0975 | 138.43 | 0 | 11.6129 | 19.3509 | 18.292 | 53.8 | 26.9 | 18.927 | 3.8 | 0.6 | 208.3655 | 1415.841 | 0.28845
Sales | Yes | 1 | 2324.94 | 14176.6 | 6.0976 | 323.52 | 174.7 | 11.6129 | 200.2034 | 18.292 | 5.38 | 0 | 0 | 3.8 | 0.6 | 2155.7368 | 0 | 0.20333
Produce | Yes | 1 | 711.36 | 4337.61 | 6.0976 | 366.18 | 0 | 11.6129 | 61.2561 | 18.292 | 5.38 | 0 | 0 | 3.8 | 0.6 | 659.589 | 0 | 0.27037
Bakery | Yes | 1 | 209.04 | 1274.65 | 6.0976 | 189.13 | 0 | 11.6129 | 18.0007 | 18.292 | 53.8 | 26.9 | 18.927 | 3.8 | 0.6 | 193.8266 | 353.9603 | 0.33998
Total Conditioned Zones |  |  | 4180.79 | 25492.85 |  | 1609.58 | 174.7 |  | 325.9056 | [6 empty] | 3714.0474 | 1769.8013
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 3.2427 | 48.5293 | 13.8511 | 58.2142 |  | 36.0031 | 4.9396 | 93.7809 | 1.6382 | 10.8413 | 113.3876 | 15.6058 | 24.6924 | 2.8076 | 2.9867 | 0.54444
Fabric | [6 empty] | weighting factor is for all of 3B
Exterior walls
| Construction Type | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall
| R-value (m2·K / W) | 0.4207 | 0.4207 | 0.4207 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.4327 | 1.4327 | 1.692 | 1.692 | 1.9569 | 2.2026
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.849 | 2.849 | 2.849 | 2.849 | 2.7933 | 3.7175
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
| SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.702
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.162 | 0.162 | 0.162 | 0.223 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.633
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade
| R-value (m2·K / W) | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC:1_COOLC DXCOIL | 9.3486 | 9.4383 | 8.8832 | 8.6481 | 4.5896 | 7.0816 | 5.1427 | 10.0355 | 8.5183 | 6.3993 | 12.2684 | 10.0048 | 13.0252 | 10.938 | 12.9516 | 11.894
| PSZ-AC:2_COOLC DXCOIL | 47.3552 | 54.8862 | 52.5221 | 54.6727 | 26.7131 | 45.9691 | 29.3048 | 58.876 | 44.7924 | 38.334 | 69.9943 | 55.5519 | 76.9671 | 57.5277 | 81.0669 | 63.2132
| PSZ-AC:3_COOLC DXCOIL | 51.0147 | 50.0243 | 54.937 | 51.275 | 43.6868 | 38.6934 | 24.2761 | 48.5511 | 32.8091 | 27.4555 | 48.5028 | 31.8407 | 48.5163 | 29.7955 | 29.6548 | 24.1066
| PSZ-AC:4_COOLC DXCOIL | 114.0609 | 179.8554 | 199.6548 | 194.1031 | 129.4553 | 195.799 | 127.8135 | 203.0213 | 224.9394 | 168.2325 | 235.1872 | 257.1278 | 255.3809 | 235.3782 | 270.9108 | 198.7833
| PSZ-AC:5_COOLC DXCOIL | 54.5119 | 63.2512 | 64.0594 | 57.8103 | 39.1783 | 58.5434 | 29.2386 | 61.9278 | 49.8746 | 36.0447 | 77.2594 | 57.056 | 83.5479 | 59.1782 | 83.3591 | 64.7239
| PSZ-AC:6_COOLC DXCOIL | 45.5475 | 45.7606 | 43.0065 | 36.6488 | 30.8296 | 31.5651 | 26.7491 | 34.5416 | 33.6131 | 28.6597 | 33.8889 | 33.1713 | 33.6866 | 31.4352 | 29.1238 | 27.3297
Heating (kW)
| PSZ-AC:1_HEATC | 11.7182 | 12.4693 | 12.2065 | 11.0429 | 6.664 | 9.7118 | 8.2034 | 12.6476 | 11.4281 | 10.3537 | 14.9414 | 13.4949 | 16.11 | 15.8383 | 16.4858 | 20.1743
| PSZ-AC:2_HEATC | 52.7649 | 66.6522 | 66.8122 | 65.2563 | 37.3599 | 57.7878 | 47.7077 | 73.4359 | 65.2868 | 62.0412 | 87.881 | 78.6234 | 96.6389 | 94.7469 | 99.9551 | 123.1144
| PSZ-AC:3_HEATC | 79.5365 | 102.9606 | 95.3984 | 113.845 | 75.9657 | 85.9686 | 65.271 | 119.9975 | 96.6536 | 88.0341 | 140.0426 | 111.9714 | 151.3869 | 127.0904 | 134.3577 | 143.0293
| PSZ-AC:4_HEATC | 160.4459 | 264.2778 | 254.71 | 288.1865 | 183.0921 | 255.9927 | 222.4813 | 321.2739 | 285.1002 | 274.3137 | 384.602 | 341.1938 | 421.892 | 407.3462 | 438.7523 | 535.3349
| PSZ-AC:5_HEATC | 67.2509 | 88.4456 | 82.6459 | 87.8954 | 55.6835 | 79.1825 | 64.1329 | 99.054 | 88.8418 | 82.8175 | 122.4763 | 107.0467 | 133.9478 | 126.8349 | 136.1256 | 171.0727
| PSZ-AC:6_HEATC | 57.2614 | 61.9099 | 59.7694 | 56.5201 | 49.2797 | 49.4307 | 45.0791 | 57.4159 | 48.7068 | 49.6993 | 60.0614 | 51.1276 | 61.6788 | 54.358 | 57.0548 | 61.644
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC:1_COOLC DXCOIL | 3.82 | 3.83 | 3.94 | 3.79 | 3.9 | 3.92 | 4.01 | 3.75 | 4.04 | 4.02 | 3.73 | 4.04 | 3.74 | 4.04 | 3.78 | 4.04
| PSZ-AC:2_COOLC DXCOIL | 3.19 | 3.2 | 3.28 | 3.19 | 3.54 | 3.25 | 3.67 | 3.19 | 3.44 | 3.61 | 3.19 | 3.39 | 3.11 | 3.45 | 3.11 | 4.32
| PSZ-AC:3_COOLC DXCOIL | 3.19 | 3.19 | 3.19 | 3.19 | 3.22 | 3.52 | 3.77 | 3.19 | 3.73 | 3.77 | 3.19 | 3.73 | 3.19 | 3.73 | 3.71 | 3.77
| PSZ-AC:4_COOLC DXCOIL | 3.51 | 3.49 | 3.49 | 3.49 | 3.5 | 3.49 | 3.78 | 3.49 | 3.32 | 3.59 | 3.27 | 3.29 | 3.27 | 3.45 | 3.26 | 3.92
| PSZ-AC:5_COOLC DXCOIL | 3.19 | 3.19 | 3.2 | 3.19 | 3.46 | 3.21 | 3.73 | 3.19 | 3.45 | 3.73 | 3.11 | 3.45 | 3.11 | 4.32 | 3.11 | 4.32
| PSZ-AC:6_COOLC DXCOIL | 3.29 | 3.3 | 3.36 | 3.65 | 3.73 | 3.73 | 3.77 | 3.65 | 3.73 | 3.77 | 3.67 | 3.73 | 3.68 | 3.73 | 3.77 | 3.77
Heating Efficiency (%)
| PSZ-AC:1_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC:2_HEATC | 0.8 | 0.78 | 0.78 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78 | 0.8 | 0.8 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:3_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.8 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:4_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:5_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.8 | 0.78 | 0.8 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:6_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
HVAC Control - Economizer
| DELI EXHAUST FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| SALES EXHAUST FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC:1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ-AC:2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC:3_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC:4_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
Fan Max Flow Rate (m3/s )
| BAKERY EXHAUST FAN | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
| DELI EXHAUST FAN | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34
| SALES EXHAUST FAN | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08
| PSZ-AC:1_FAN | 0.46 | 0.47 | 0.49 | 0.42 | 0.25 | 0.39 | 0.3 | 0.46 | 0.51 | 0.38 | 0.55 | 0.6 | 0.59 | 0.66 | 0.62 | 0.72
| PSZ-AC:2_FAN | 1.94 | 2.28 | 2.5 | 2.2 | 1.25 | 2.1 | 1.6 | 2.37 | 2.65 | 2.05 | 2.82 | 3.11 | 3.1 | 3.48 | 3.26 | 3.82
| PSZ-AC:3_FAN | 2.05 | 2.01 | 2.21 | 2.06 | 1.89 | 1.84 | 1.47 | 1.96 | 1.98 | 1.66 | 1.95 | 1.92 | 1.95 | 1.8 | 1.69 | 1.46
| PSZ-AC:4_FAN | 4.59 | 7.24 | 8.04 | 7.82 | 5.29 | 7.88 | 6.43 | 8.18 | 9.57 | 7.42 | 9.47 | 10.81 | 10.28 | 11.57 | 10.91 | 12.01
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Cost ($/m2) | Electric | Electric | Electric | Electric | Electric | Electric | Electric | Electric | Electric | Electric | Electric | Electric | Electric | Electric | Electric | Electric
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Cost ($/m2) | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas
Total Utility Costs
| Cost Intensity ($/m2) | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 143919.4444 | 114466.6667 | 121166.6667 | 54816.6667 | 12297.2222 | 60727.7778 | 2894.4444 | 42475 | 25344.4444 | 4258.3333 | 28072.2222 | 15122.2222 | 24327.7778 | 9102.7778 | 9580.5556 | 4477.7778
| Interior Lighting | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778
| Exterior Lighting | 17511.1111 | 17480.5556 | 17475 | 17505.5556 | 17502.7778 | 17486.1111 | 17466.6667 | 17483.3333 | 17480.5556 | 17455.5556 | 17461.1111 | 17463.8889 | 17475 | 17452.7778 | 17447.2222 | 17344.4444
| Interior Equipment | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 108797.2222 | 141786.1111 | 154463.8889 | 145305.5556 | 103433.3333 | 144161.1111 | 115658.3333 | 152675 | 165855.5556 | 134813.8889 | 169075 | 186055.5556 | 185552.7778 | 216758.3333 | 193280.5556 | 261572.2222
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 1243933.3333 | 1140769.4444 | 1006775 | 1023402.7778 | 1027077.7778 | 915344.4444 | 934366.6667 | 956580.5556 | 876008.3333 | 889969.4444 | 915011.1111 | 841788.8889 | 896536.1111 | 815019.4444 | 831900 | 785958.3333
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1991786.1111 | 1892127.7778 | 1777502.7778 | 1718652.7778 | 1637933.3333 | 1615341.6667 | 1548008.3333 | 1646836.1111 | 1562313.8889 | 1524119.4444 | 1607244.4444 | 1538055.5556 | 1601513.8889 | 1535958.3333 | 1529833.3333 | 1546977.7778
Gas (MJ)
| Heating | 99670 | 919910 | 926330 | 1676330 | 1133970 | 1481250 | 2104430 | 2568750 | 2144490 | 2863830 | 3233970 | 2762660 | 3886200 | 3605590 | 4838460 | 6852920
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 15860 | 17830 | 16700 | 19720 | 19360 | 18060 | 20980 | 21210 | 20930 | 21990 | 22520 | 22450 | 23650 | 23850 | 25510 | 27770
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 314660 | 1136870 | 1142150 | 1895180 | 1352450 | 1698440 | 2324530 | 2789090 | 2364550 | 3084940 | 3455620 | 2984240 | 4108970 | 3828570 | 5063100 | 7079820
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 7485090 | 7948530 | 7541170 | 8082330 | 7249010 | 7513670 | 7897360 | 8717700 | 7988870 | 8571780 | 9241700 | 8521230 | 9874420 | 9358020 | 10570500 | 12648940
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 123.9263 | 98.5651 | 104.3343 | 47.2016 | 10.5889 | 52.2916 | 2.4924 | 36.5744 | 21.8236 | 3.6668 | 24.1725 | 13.0215 | 20.9482 | 7.8382 | 8.2496 | 3.8557
| Interior Lighting (elec) | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453
| Exterior Lighting (elec) | 15.0785 | 15.0522 | 15.0474 | 15.0737 | 15.0713 | 15.057 | 15.0402 | 15.0546 | 15.0522 | 15.0307 | 15.0354 | 15.0378 | 15.0474 | 15.0283 | 15.0235 | 14.935
| Interior Equipment (elec) | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 93.6833 | 122.0894 | 133.006 | 125.1199 | 89.0645 | 124.1344 | 99.5912 | 131.4656 | 142.8151 | 116.0857 | 145.5873 | 160.209 | 159.776 | 186.6465 | 166.4303 | 225.2349
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 1071.1277 | 982.2952 | 866.9151 | 881.233 | 884.3974 | 788.186 | 804.5656 | 823.6936 | 754.3144 | 766.336 | 787.8989 | 724.8487 | 771.9905 | 701.798 | 716.3335 | 676.774
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1715.0897 | 1629.2758 | 1530.5744 | 1479.8997 | 1410.3937 | 1390.9405 | 1332.961 | 1418.0597 | 1345.2792 | 1312.3907 | 1383.9681 | 1324.3908 | 1379.0336 | 1322.585 | 1317.3108 | 1332.0736
Gas (MJ/m2)
| Heating (gas) | 23.84 | 220.0326 | 221.5682 | 400.9601 | 271.2334 | 354.2991 | 503.357 | 614.4174 | 512.9389 | 684.9973 | 773.5308 | 660.7986 | 929.5372 | 862.4183 | 1157.3076 | 1639.1448
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 3.7935 | 4.2647 | 3.9945 | 4.7168 | 4.6307 | 4.3198 | 5.0182 | 5.0732 | 5.0062 | 5.2598 | 5.3865 | 5.3698 | 5.6568 | 5.7047 | 6.1017 | 6.6423
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 75.2633 | 271.9271 | 273.19 | 453.3067 | 323.4915 | 406.2486 | 556.0026 | 667.1203 | 565.5749 | 737.8845 | 826.5471 | 713.7981 | 982.8214 | 915.7528 | 1211.0391 | 1693.4168
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 1790.353 | 1901.2029 | 1803.7668 | 1933.2064 | 1733.8852 | 1797.189 | 1888.9636 | 2085.1801 | 1910.8518 | 2050.2776 | 2210.5152 | 2038.1866 | 2361.8551 | 2238.3377 | 2528.3499 | 3025.4904
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 357.5484 | 351.9592 | 305.4612 | 330.2393 | 305.1668 | 296.1587 | 307.9885 | 309.4609 | 292.412 | 302.4166 | 294.4566 | 298.0388 | 292.561 | 298.5484 | 290.1098 | 301.0203
| Feb | 363.5316 | 340.7716 | 312.4141 | 318.0644 | 312.6833 | 308.2163 | 314.0244 | 299.194 | 294.0532 | 293.7328 | 296.0863 | 294.2413 | 292.2359 | 306.0451 | 294.9597 | 299.0493
| Mar | 372.7766 | 351.6901 | 341.0751 | 331.0654 | 310.3579 | 302.704 | 301.2145 | 337.5855 | 298.5595 | 302.9578 | 320.6172 | 306.0492 | 304.4265 | 306.5628 | 296.263 | 302.2092
| Apr | 383.9357 | 374.0028 | 346.0951 | 349.9695 | 313.4456 | 339.3962 | 310.8561 | 335.0386 | 315.3546 | 308.0953 | 322.9858 | 315.7516 | 326.6953 | 306.3782 | 303.1585 | 301.6039
| May | 394.6824 | 416.0821 | 383.6845 | 382.4875 | 332.9317 | 351.7747 | 320.2313 | 360.8343 | 334.574 | 329.7211 | 361.5966 | 334.3582 | 378.1103 | 324.5215 | 316.6433 | 321.1891
| Jun | 416.5436 | 419.7054 | 437.2005 | 396.4604 | 332.0059 | 387.6338 | 325.7276 | 417.9553 | 352.9025 | 328.6465 | 388.845 | 348.1024 | 405.9526 | 356.2201 | 362.7705 | 346.2612
| Jul | 407.0064 | 429.4339 | 445.3446 | 421.0274 | 342.8159 | 394.7682 | 339.4557 | 425.977 | 366.0643 | 345.8758 | 416.8087 | 362.6062 | 405.7457 | 361.9498 | 388.3635 | 345.8734
| Aug | 408.9778 | 427.7826 | 438.3691 | 400.4808 | 350.1069 | 407.7575 | 335.0269 | 420.2483 | 376.4821 | 342.8347 | 410.7643 | 363.0412 | 405.2696 | 358.0662 | 366.4189 | 343.5952
| Sep | 395.7652 | 414.2123 | 419.5248 | 378.8035 | 346.3524 | 373.9219 | 342.2948 | 369.6674 | 340.933 | 345.1317 | 364.9238 | 340.8669 | 357.0214 | 343.6029 | 343.7131 | 316.68
| Oct | 395.1908 | 380.5598 | 368.6068 | 349.587 | 332.5798 | 344.195 | 320.9021 | 349.1883 | 327.0497 | 313.7417 | 344.2253 | 316.5258 | 321.0327 | 318.5103 | 312.8733 | 308.2539
| Nov | 371.465 | 364.8429 | 327.6928 | 328.1143 | 321.0587 | 304.8444 | 315.7655 | 339.1588 | 299.8888 | 316.1681 | 344.4859 | 297.0882 | 308.6943 | 299.7278 | 313.1797 | 299.3488
| Dec | 360.7485 | 350.7844 | 322.1488 | 327.2946 | 312.4559 | 295.0391 | 307.7866 | 309.4863 | 291.3417 | 296.6912 | 302.2755 | 292.3917 | 296.0608 | 296.7792 | 293.849 | 303.4348
Time of Peak Electrical Demand
| Jan | 23-JAN-18:15 | 20-JAN-18:15 | 05-JAN-18:15 | 24-JAN-18:15 | 10-JAN-18:15 | 23-JAN-18:15 | 05-JAN-18:15 | 09-JAN-11:15 | 02-JAN-11:15 | 14-JAN-11:15 | 17-JAN-18:15 | 23-JAN-11:15 | 30-JAN-11:15 | 23-JAN-11:15 | 13-JAN-11:15 | 21-JAN-11:15
| Feb | 23-FEB-11:00 | 15-FEB-18:15 | 14-FEB-18:15 | 21-FEB-18:15 | 13-FEB-11:45 | 10-FEB-18:15 | 15-FEB-18:15 | 13-FEB-11:15 | 14-FEB-18:15 | 21-FEB-11:15 | 28-FEB-11:15 | 11-FEB-11:15 | 21-FEB-11:15 | 02-FEB-18:15 | 21-FEB-11:15 | 27-FEB-11:15
| Mar | 13-MAR-17:15 | 28-MAR-17:15 | 17-MAR-17:15 | 29-MAR-17:15 | 04-MAR-11:45 | 31-MAR-17:15 | 27-MAR-17:15 | 09-MAR-18:15 | 08-MAR-18:15 | 30-MAR-10:15 | 14-MAR-17:15 | 30-MAR-17:15 | 23-MAR-17:15 | 30-MAR-17:15 | 30-MAR-10:15 | 09-MAR-11:15
| Apr | 03-APR-17:15 | 29-APR-10:00 | 17-APR-17:15 | 14-APR-17:15 | 10-APR-10:45 | 21-APR-17:15 | 29-APR-10:45 | 04-APR-17:15 | 21-APR-17:15 | 29-APR-10:15 | 10-APR-10:15 | 26-APR-10:45 | 01-APR-17:15 | 24-APR-10:15 | 14-APR-10:15 | 14-APR-10:15
| May | 15-MAY-17:15 | 26-MAY-17:15 | 30-MAY-17:15 | 31-MAY-17:15 | 30-MAY-10:45 | 31-MAY-17:15 | 25-MAY-17:15 | 15-MAY-17:15 | 30-MAY-10:45 | 05-MAY-17:15 | 30-MAY-17:15 | 24-MAY-10:45 | 27-MAY-17:15 | 25-MAY-17:15 | 27-MAY-10:45 | 31-MAY-10:15
| Jun | 27-JUN-17:15 | 13-JUN-17:15 | 28-JUN-17:15 | 19-JUN-17:15 | 28-JUN-17:15 | 27-JUN-17:15 | 16-JUN-10:45 | 30-JUN-17:15 | 29-JUN-17:15 | 28-JUN-10:45 | 20-JUN-17:15 | 28-JUN-10:45 | 29-JUN-17:15 | 30-JUN-10:45 | 14-JUN-17:15 | 21-JUN-17:15
| Jul | 13-JUL-17:15 | 05-JUL-17:15 | 11-JUL-17:15 | 03-JUL-17:15 | 29-JUL-10:45 | 11-JUL-10:45 | 03-JUL-10:45 | 25-JUL-10:00 | 18-JUL-17:15 | 31-JUL-17:15 | 14-JUL-10:00 | 19-JUL-10:45 | 13-JUL-17:15 | 21-JUL-17:15 | 06-JUL-17:15 | 11-JUL-17:15
| Aug | 21-AUG-17:15 | 31-AUG-17:15 | 01-AUG-17:15 | 14-AUG-17:15 | 08-AUG-17:15 | 05-AUG-10:45 | 15-AUG-10:45 | 17-AUG-17:15 | 01-AUG-17:15 | 18-AUG-17:15 | 04-AUG-17:15 | 30-AUG-10:45 | 25-AUG-17:15 | 11-AUG-17:15 | 11-AUG-17:15 | 15-AUG-17:15
| Sep | 13-SEP-17:15 | 16-SEP-10:00 | 08-SEP-17:15 | 06-SEP-17:15 | 09-SEP-10:45 | 01-SEP-17:15 | 29-SEP-10:45 | 08-SEP-17:15 | 01-SEP-17:15 | 02-SEP-10:45 | 06-SEP-10:45 | 09-SEP-10:45 | 14-SEP-17:15 | 12-SEP-17:15 | 08-SEP-17:15 | 01-SEP-17:15
| Oct | 06-OCT-17:15 | 06-OCT-17:15 | 13-OCT-17:15 | 20-OCT-17:15 | 05-OCT-10:45 | 06-OCT-10:45 | 16-OCT-17:15 | 20-OCT-17:15 | 11-OCT-17:15 | 18-OCT-17:15 | 31-OCT-17:15 | 05-OCT-10:45 | 14-OCT-10:15 | 06-OCT-17:15 | 07-OCT-10:15 | 02-OCT-10:15
| Nov | 01-NOV-17:15 | 27-NOV-18:15 | 13-NOV-18:15 | 28-NOV-18:15 | 20-NOV-11:45 | 21-NOV-18:15 | 16-NOV-18:15 | 03-NOV-17:15 | 10-NOV-11:15 | 03-NOV-17:15 | 02-NOV-17:15 | 16-NOV-11:15 | 02-NOV-17:15 | 01-NOV-10:15 | 09-NOV-11:15 | 14-NOV-11:15
| Dec | 15-DEC-18:15 | 02-DEC-11:00 | 13-DEC-18:15 | 04-DEC-18:15 | 04-DEC-18:15 | 05-DEC-11:45 | 14-DEC-18:15 | 23-DEC-11:15 | 22-DEC-11:15 | 05-DEC-11:15 | 12-DEC-18:15 | 30-DEC-11:15 | 02-DEC-11:15 | 29-DEC-11:15 | 02-DEC-11:15 | 18-DEC-11:15
Source Energy
| Total Source Energy (GJ) | 24127.92 | 25981.41 | 21487.31 | 22883.12 | 19726.72 | 22655.78 | 19786.3 | 24246.41 | 21243.6 | 12926.82 | 24290.98 | 21630.54 | 24302.85 | 23401.15 | 24457.85 | 27624.07
| Total Source Energy (MJ/m2) | 5771.13 | 6214.47 | 5139.53 | 5473.39 | 4718.41 | 5419.01 | 4732.67 | 5799.47 | 5081.24 | 3091.95 | 5810.14 | 5173.79 | 5812.98 | 5597.3 | 5850.05 | 6607.37
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12
| Total Building | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12
Emissions
| Carbon Equivalent (kg) | 551920.8615 | 651640.6943 | 557180.9088 | 563583.6061 | 215806.6489 | 575441.9371 | 222826.8402 | 494702.8204 | 680840.8489 | 166637.8346 | 919215.4957 | 682105.9754 | 622282.9602 | 630335.8542 | 614952.8638 | 562968.4686
| CO2 (kg) | 1281260 | 1642940 | 1321390 | 1300280 | 581517.2478 | 1378890 | 604105.2088 | 1141910 | 1610260 | 424422.7366 | 2157140 | 1619460 | 1477860 | 1504970 | 1471010 | 1459290
| NOX (kg) | 2245.6037 | 2135.417 | 2186.8152 | 2409.8247 | 501.3185 | 2196.4986 | 523.2871 | 2124.531 | 2720.968 | 569.6111 | 3763.5503 | 2709.7666 | 2500.5347 | 2498.4823 | 2442.4456 | 1700.9812
| SO2 (kg) | 8525.7234 | 9025.7538 | 7148.0051 | 6032.9835 | 4766.5487 | 8886.1276 | 4505.1424 | 6012.3622 | 6822.9415 | 1178.85 | 10832.4695 | 6717.1754 | 3780.9307 | 4102.2164 | 3612.0099 | 7876.6371
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0389 | 0.0255 | 0.0195 | 0.0222 | 0.0023 | 0.0168 | 0.0023 | 0.0245 | 0.0268 | 0.0049 | 0.033 | 0.0265 | 0.028 | 0.0288 | 0.0269 | 0.0274
| Water for Electricity (m3) | 1055.16 | 3078.71 | 52799.7 | 10730.6 | 28758.4 | 44315.3 | 27179.6 | 373.894 | 7094.15 | 15571.6 | 2493.54 | 6984 | 2484.65 | 97293.9 | 2373.45 | 1580.52

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 7485.09 | 1790.35 | 1790.35
Net Site Energy | 7485.09 | 1790.35 | 1790.35
Total Source Energy | 24127.92 | 5771.13 | 5771.13
Net Source Energy | 24127.92 | 5771.13 | 5771.13
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 99.67 | 0 | 0 | 0 | 0
Cooling | 518.11 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 63.04 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 391.67 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 15.86 | 0 | 0 | 0 | 87.12
Refrigeration | 4478.16 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7170.43 | 314.66 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 18.29 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 18.29 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 8.61 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 11.84 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 18.29 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 18.29 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 174.7 | 174.7 | 5.835 | 0.251 | 0.11 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9348.58 | 6847.55 | 2501.03 | 0.73 | 3.82
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 47355.23 | 32216.84 | 15138.39 | 0.68 | 3.19
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 51014.67 | 34490.17 | 16524.51 | 0.68 | 3.19
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 114060.94 | 77114.69 | 36946.25 | 0.68 | 3.51
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 54511.93 | 36854.6 | 17657.33 | 0.68 | 3.19
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 45547.48 | 33161.24 | 12386.24 | 0.73 | 3.29
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 11718.23 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 52764.89 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 79536.51 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 160445.85 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 67250.89 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 57261.37 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.46 | 537.13 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.94 | 2121.62 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.05 | 2246.7 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.59 | 8761.28 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.2 | 2400.72 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.22 | 2431.33 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.72 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 100249.9203 | 174.3664 | 656.5568 | 0 | 0.003 | 81256.0675 | 43050.1714
February | 90856.6803 | 158.5575 | 599.2011 | 0 | 0.0027 | 74158.075 | 39069.4383
March | 102257.7247 | 178.681 | 676.1787 | 0 | 0.0031 | 83685.1171 | 43994.778
April | 103208.583 | 181.069 | 688.1846 | 0 | 0.0031 | 85171.5433 | 44476.6694
May | 112573.6269 | 197.6934 | 752.1594 | 0 | 0.0034 | 93089.3766 | 48531.911
June | 112820.2848 | 198.176 | 754.1963 | 0 | 0.0034 | 93341.5114 | 48643.1993
July | 117943.1476 | 207.2032 | 788.6673 | 0 | 0.0036 | 97607.7638 | 50854.8193
August | 118690.2731 | 208.5012 | 793.5488 | 0 | 0.0036 | 98211.892 | 51175.5079
September | 111798.615 | 196.3836 | 747.3841 | 0 | 0.0034 | 92498.4124 | 48202.9234
October | 110643.3214 | 194.2818 | 739.0913 | 0 | 0.0034 | 91472.0189 | 47697.5581
November | 101351.3877 | 177.7708 | 675.4864 | 0 | 0.0031 | 83599.956 | 43672.3257
December | 98863.8134 | 172.9199 | 655.0686 | 0 | 0.003 | 81072.6181 | 42551.5598
Annual Sum or Average | 1281260 | 2245.6037 | 8525.7234 | 0 | 0.0389 | 1055160 | 551920.8615
Minimum of Months | 90856.6803 | 158.5575 | 599.2011 | 0 | 0.0027 | 74158.075 | 39069.4383
Maximum of Months | 118690.2731 | 208.5012 | 793.5488 | 0 | 0.0036 | 98211.892 | 51175.5079
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 552180000000 | 357548.393 | 23-JAN-18:15 | 41924.28 | 36859.929 | 18629.698 | 0 | 22645.311 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 233484.175 | 0 | 0
February | 503945000000 | 363531.636 | 23-FEB-11:00 | 62886.42 | 41401.92 | 18629.698 | 0 | 31026.266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209587.332 | 0 | 0
March | 568687000000 | 372776.625 | 13-MAR-17:15 | 41924.28 | 36859.929 | 18629.698 | 0 | 36115.217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239247.501 | 0 | 0
April | 578788000000 | 383935.655 | 03-APR-17:15 | 41924.28 | 36859.929 | 18629.698 | 0 | 47084.986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239436.762 | 0 | 0
May | 632594000000 | 394682.397 | 15-MAY-17:15 | 41924.28 | 36859.929 | 18629.698 | 0 | 55318.691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241949.799 | 0 | 0
June | 634307000000 | 416543.617 | 27-JUN-17:15 | 41924.28 | 36859.929 | 18629.698 | 0 | 72697.779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246431.932 | 0 | 0
July | 663299000000 | 407006.351 | 13-JUL-17:15 | 41924.28 | 36859.929 | 18629.698 | 0 | 65333.323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244259.121 | 0 | 0
August | 667404000000 | 408977.809 | 21-AUG-17:15 | 41924.28 | 36859.929 | 18629.698 | 0 | 65998.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245565.781 | 0 | 0
September | 628578000000 | 395765.232 | 13-SEP-17:15 | 41924.28 | 36859.929 | 18629.698 | 0 | 56263.981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242087.343 | 0 | 0
October | 621603000000 | 395190.82 | 06-OCT-17:15 | 41924.28 | 36859.929 | 18629.698 | 0 | 55802.959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241973.953 | 0 | 0
November | 568108000000 | 371464.983 | 01-NOV-17:15 | 41924.28 | 36859.929 | 18629.698 | 0 | 34178.615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239872.461 | 0 | 0
December | 550933000000 | 360748.542 | 15-DEC-18:15 | 41924.28 | 36859.929 | 18629.698 | 0 | 23522.557 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 235807.079 | 0 | 0
Annual Sum or Average | 7170430000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 503945000000 | 357548.393 |  | 41924.28 | 36859.929 | 18629.698 | 0 | 22645.311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209587.332 | 0 | 0
Maximum of Months | 667404000000 | 416543.617 |  | 62886.42 | 41401.92 | 18629.698 | 0 | 72697.779 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 246431.932 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 159897.27 | 3600.5 | 0 | 163497.76
Cost per Total Building Area ($/m2) | 38.25 | 0.86 | 0 | 39.11
Cost per Net Conditioned Building Area ($/m2) | 38.25 | 0.86 | 0 | 39.11

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 7948.53 | 1901.2 | 1901.2
Net Site Energy | 7948.53 | 1901.2 | 1901.2
Total Source Energy | 25981.41 | 6214.47 | 6214.47
Net Source Energy | 25981.41 | 6214.47 | 6214.47
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 919.91 | 0 | 0 | 0 | 0
Cooling | 412.08 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.93 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 510.43 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 17.83 | 0 | 0 | 0 | 87.12
Refrigeration | 4106.77 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6811.66 | 1136.87 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 18.29 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 18.29 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 8.61 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 11.84 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 18.29 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 18.29 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 174.7 | 174.7 | 5.835 | 0.251 | 0.11 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9438.25 | 6944.75 | 2493.5 | 0.74 | 3.83
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 54886.16 | 37553.14 | 17333.02 | 0.68 | 3.2
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 50024.27 | 33820.57 | 16203.7 | 0.68 | 3.19
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 179855.43 | 121597.24 | 58258.19 | 0.68 | 3.49
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 63251.21 | 42763.08 | 20488.13 | 0.68 | 3.19
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 45760.6 | 33480.16 | 12280.44 | 0.73 | 3.3
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 12469.32 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 66652.2 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 102960.63 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 264277.83 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 88445.62 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 61909.89 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.47 | 548.29 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.28 | 2497.26 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.01 | 2203.09 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.24 | 13587.38 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.55 | 2785.6 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.26 | 2472.13 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.72 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 126525.9244 | 161.1022 | 648.1686 | 0 | 0.0018 | 221077.3838 | 49752.2001
February | 113194.7571 | 143.762 | 574.7508 | 0 | 0.0016 | 196034.2663 | 44462.9873
March | 126889.2892 | 164.0094 | 684.2682 | 0 | 0.0019 | 233401.9749 | 50210.1896
April | 130021.7498 | 169.958 | 727.7665 | 0 | 0.002 | 248247.7927 | 51694.5736
May | 144946.9422 | 190.012 | 818.934 | 0 | 0.0023 | 279348.2451 | 57698.7882
June | 151048.7836 | 198.1569 | 855.4532 | 0 | 0.0024 | 291806.0125 | 60146.5541
July | 159798.5075 | 209.6562 | 905.2975 | 0 | 0.0025 | 308808.6461 | 63633.3099
August | 158868.4654 | 208.4151 | 899.735 | 0 | 0.0025 | 306911.1012 | 63260.2558
September | 144262.4424 | 189.2261 | 816.6264 | 0 | 0.0023 | 278561.5733 | 57440.6654
October | 137840.4648 | 180.4044 | 774.6981 | 0 | 0.0022 | 264257.5737 | 54832.3276
November | 123957.9298 | 160.9453 | 678.6108 | 0 | 0.0019 | 231475.5561 | 49143.6664
December | 125586.3963 | 159.7695 | 641.4449 | 0 | 0.0018 | 218783.3955 | 49365.1762
Annual Sum or Average | 1642940 | 2135.417 | 9025.7538 | 0 | 0.0255 | 3078710 | 651640.6943
Minimum of Months | 113194.7571 | 143.762 | 574.7508 | 0 | 0.0016 | 196034.2663 | 44462.9873
Maximum of Months | 159798.5075 | 209.6562 | 905.2975 | 0 | 0.0025 | 308808.6461 | 63633.3099
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 489134000000 | 351959.187 | 20-JAN-18:15 | 41924.28 | 36859.929 | 24224.671 | 0 | 13106.041 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 231839.265 | 0 | 0
February | 433726000000 | 340771.621 | 15-FEB-18:15 | 41924.28 | 36859.929 | 24224.671 | 0 | 7489.05 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 226268.691 | 0 | 0
March | 516402000000 | 351690.097 | 28-MAR-17:15 | 41924.28 | 36859.929 | 24224.671 | 0 | 16096.747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232584.47 | 0 | 0
April | 549249000000 | 374002.825 | 29-APR-10:00 | 62886.42 | 41401.92 | 24224.671 | 0 | 33412.542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212077.271 | 0 | 0
May | 618059000000 | 416082.113 | 26-MAY-17:15 | 41924.28 | 36859.929 | 24224.671 | 0 | 68701.064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244372.168 | 0 | 0
June | 645621000000 | 419705.436 | 13-JUN-17:15 | 41924.28 | 36859.929 | 24224.671 | 0 | 72286.802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244409.753 | 0 | 0
July | 683240000000 | 429433.906 | 05-JUL-17:15 | 41924.28 | 36859.929 | 24224.671 | 0 | 80032.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246392.365 | 0 | 0
August | 679041000000 | 427782.574 | 31-AUG-17:15 | 41924.28 | 36859.929 | 24224.671 | 0 | 78708.404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246065.289 | 0 | 0
September | 616318000000 | 414212.319 | 16-SEP-10:00 | 62886.42 | 41401.92 | 24224.671 | 0 | 67250.785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218448.522 | 0 | 0
October | 584670000000 | 380559.791 | 06-OCT-17:15 | 41924.28 | 36859.929 | 24224.671 | 0 | 40502.264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 237048.647 | 0 | 0
November | 512140000000 | 364842.879 | 27-NOV-18:15 | 41924.28 | 36859.929 | 24224.671 | 0 | 19429.363 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 238399.635 | 0 | 0
December | 484059000000 | 350784.38 | 02-DEC-11:00 | 62886.42 | 41401.92 | 24224.671 | 0 | 13718.802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208552.565 | 0 | 0
Annual Sum or Average | 6811660000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 433726000000 | 340771.621 |  | 41924.28 | 36859.929 | 24224.671 | 0 | 7489.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208552.565 | 0 | 0
Maximum of Months | 683240000000 | 429433.906 |  | 62886.42 | 41401.92 | 24224.671 | 0 | 80032.66 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 246392.365 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 205124.72 | 9181.19 | 0 | 214305.91
Cost per Total Building Area ($/m2) | 49.06 | 2.2 | 0 | 51.26
Cost per Net Conditioned Building Area ($/m2) | 49.06 | 2.2 | 0 | 51.26

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 7541.17 | 1803.76 | 1803.76
Net Site Energy | 7541.17 | 1803.76 | 1803.76
Total Source Energy | 21487.31 | 5139.53 | 5139.53
Net Source Energy | 21487.31 | 5139.53 | 5139.53
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 926.33 | 0 | 0 | 0 | 0
Cooling | 436.2 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.91 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 556.07 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 16.7 | 0 | 0 | 0 | 87.12
Refrigeration | 3624.39 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6399.01 | 1142.15 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 18.29 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 18.29 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 8.61 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 11.84 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 18.29 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 18.29 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 174.7 | 174.7 | 5.835 | 0.251 | 0.11 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8883.22 | 6836.82 | 2046.4 | 0.77 | 3.94
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 52522.07 | 37863.72 | 14658.35 | 0.72 | 3.28
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 54937.02 | 37142 | 17795.02 | 0.68 | 3.19
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 199654.78 | 134983.25 | 64671.53 | 0.68 | 3.49
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 64059.36 | 43826.01 | 20233.35 | 0.68 | 3.2
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 43006.49 | 32712.02 | 10294.47 | 0.76 | 3.36
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 12206.45 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 66812.17 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 95398.41 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 254709.96 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 82645.95 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 59769.36 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.49 | 573.31 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.5 | 2736.17 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.21 | 2419.44 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 8.04 | 15083.14 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.66 | 2914.02 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.33 | 2547.4 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.72 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 101468.7325 | 161.4379 | 501.9698 | 0 | 0.0014 | 3707540 | 42129.6435
February | 90656.3169 | 144.8296 | 452.7798 | 0 | 0.0013 | 3344250 | 37700.4477
March | 102077.4455 | 168.261 | 547.3335 | 0 | 0.0015 | 4042920 | 42974.4082
April | 99399.5408 | 165.7349 | 546.6333 | 0 | 0.0015 | 4037840 | 42037.9438
May | 109116.9788 | 183.0343 | 608.0079 | 0 | 0.0017 | 4491260 | 46258.5517
June | 119376.8344 | 200.8963 | 669.8932 | 0 | 0.0018 | 4948420 | 50673.9992
July | 135583.1861 | 228.4016 | 762.5149 | 0 | 0.0021 | 5632620 | 57576.8582
August | 133987.9616 | 225.7077 | 753.496 | 0 | 0.002 | 5566000 | 56898.766
September | 121919.6384 | 205.246 | 684.672 | 0 | 0.0019 | 5057600 | 51760.5123
October | 107476.7184 | 179.7878 | 595.287 | 0 | 0.0016 | 4397260 | 45513.1261
November | 98237.2808 | 161.8045 | 525.8275 | 0 | 0.0014 | 3884060 | 41344.9128
December | 102091.067 | 161.6736 | 499.5904 | 0 | 0.0014 | 3689920 | 42311.7394
Annual Sum or Average | 1321390 | 2186.8152 | 7148.0051 | 0 | 0.0195 | 52799700 | 557180.9088
Minimum of Months | 90656.3169 | 144.8296 | 452.7798 | 0 | 0.0013 | 3344250 | 37700.4477
Maximum of Months | 135583.1861 | 228.4016 | 762.5149 | 0 | 0.0021 | 5632620 | 57576.8582
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 449332000000 | 305461.207 | 05-JAN-18:15 | 41924.28 | 36859.929 | 26404.407 | 0 | 0 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 196267.591 | 0 | 0
February | 405304000000 | 312414.147 | 14-FEB-18:15 | 41924.28 | 36859.929 | 26404.407 | 0 | 0 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 203220.531 | 0 | 0
March | 489978000000 | 341075.147 | 17-MAR-17:15 | 41924.28 | 36859.929 | 26404.407 | 0 | 26159.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209727.431 | 0 | 0
April | 489363000000 | 346095.073 | 17-APR-17:15 | 41924.28 | 36859.929 | 26404.407 | 0 | 28488.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212417.536 | 0 | 0
May | 544314000000 | 383684.517 | 30-MAY-17:15 | 41924.28 | 36859.929 | 26404.407 | 0 | 62966.042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215529.859 | 0 | 0
June | 599720000000 | 437200.526 | 28-JUN-17:15 | 41924.28 | 36859.929 | 26404.407 | 0 | 109448.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222563.401 | 0 | 0
July | 682641000000 | 445344.646 | 11-JUL-17:15 | 41924.28 | 36859.929 | 26404.407 | 0 | 104273.502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 235882.527 | 0 | 0
August | 674567000000 | 438369.082 | 01-AUG-17:15 | 41924.28 | 36859.929 | 26404.407 | 0 | 106736.324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226444.142 | 0 | 0
September | 612951000000 | 419524.844 | 08-SEP-17:15 | 41924.28 | 36859.929 | 26404.407 | 0 | 81518.665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232817.563 | 0 | 0
October | 532923000000 | 368606.777 | 13-OCT-17:15 | 41924.28 | 36859.929 | 26404.407 | 0 | 40655.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222762.998 | 0 | 0
November | 470725000000 | 327692.776 | 13-NOV-18:15 | 41924.28 | 36859.929 | 26404.407 | 0 | 13096.261 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 205402.899 | 0 | 0
December | 447197000000 | 322148.835 | 13-DEC-18:15 | 41924.28 | 36859.929 | 26404.407 | 0 | 1667.791 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 211287.428 | 0 | 0
Annual Sum or Average | 6399010000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 405304000000 | 305461.207 |  | 41924.28 | 36859.929 | 26404.407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196267.591 | 0 | 0
Maximum of Months | 682641000000 | 445344.646 |  | 41924.28 | 36859.929 | 26404.407 | 0 | 109448.51 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 235882.527 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 139417.11 | 9449.63 | 0 | 148866.73
Cost per Total Building Area ($/m2) | 33.35 | 2.26 | 0 | 35.61
Cost per Net Conditioned Building Area ($/m2) | 33.35 | 2.26 | 0 | 35.61

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 8082.33 | 1933.2 | 1933.2
Net Site Energy | 8082.33 | 1933.2 | 1933.2
Total Source Energy | 22883.12 | 5473.39 | 5473.39
Net Source Energy | 22883.12 | 5473.39 | 5473.39
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1676.33 | 0 | 0 | 0 | 0
Cooling | 197.34 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 63.02 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 523.1 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 19.72 | 0 | 0 | 0 | 87.12
Refrigeration | 3684.25 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6187.15 | 1895.18 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 18.29 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 18.29 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 8.61 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 11.84 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 18.29 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 18.29 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 174.7 | 174.7 | 3.241 | 0.252 | 0.162 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 3.24 | 0.252 | 0.162
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 3.24 | 0.252 | 0.162
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8648.06 | 6262.17 | 2385.9 | 0.72 | 3.79
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 54672.69 | 36963.29 | 17709.4 | 0.68 | 3.19
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 51275.03 | 34666.19 | 16608.84 | 0.68 | 3.19
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 194103.12 | 131229.86 | 62873.26 | 0.68 | 3.49
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 57810.33 | 39084.6 | 18725.74 | 0.68 | 3.19
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 36648.84 | 28180.75 | 8468.09 | 0.77 | 3.65
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 11042.93 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 65256.28 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 113845.03 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 288186.46 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 87895.36 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 56520.14 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.42 | 483.11 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.2 | 2407.8 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.06 | 2258.17 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.82 | 14663.74 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.33 | 2545.99 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.04 | 2225.55 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.72 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 105639.6495 | 182.6216 | 425.6244 | 0 | 0.0016 | 756910.8404 | 44572.0539
February | 94852.0074 | 166.3065 | 393.6011 | 0 | 0.0015 | 699988.1121 | 40236.0046
March | 102919.7833 | 186.3585 | 456.0338 | 0 | 0.0017 | 811083.6892 | 44203.8253
April | 101392.6996 | 189.0482 | 476.0071 | 0 | 0.0017 | 846662.6214 | 44051.7105
May | 111003.7798 | 212.0651 | 546.1134 | 0 | 0.002 | 971407.8661 | 48698.1131
June | 114839.7033 | 220.5671 | 570.739 | 0 | 0.0021 | 1015220 | 50489.3557
July | 122744.2724 | 235.9784 | 611.1484 | 0 | 0.0022 | 1087100 | 53985.7931
August | 122723.3144 | 235.8993 | 610.8536 | 0 | 0.0022 | 1086580 | 53972.9874
September | 113952.962 | 218.8355 | 566.1926 | 0 | 0.0021 | 1007130 | 50096.8723
October | 105546.2841 | 198.2229 | 502.5181 | 0 | 0.0018 | 893830.7943 | 45988.3911
November | 99906.2974 | 180.327 | 439.8624 | 0 | 0.0016 | 782315.9636 | 42856.4346
December | 104763.2927 | 183.5945 | 434.2895 | 0 | 0.0016 | 772348.3089 | 44432.0645
Annual Sum or Average | 1300280 | 2409.8247 | 6032.9835 | 0 | 0.0222 | 10730600 | 563583.6061
Minimum of Months | 94852.0074 | 166.3065 | 393.6011 | 0 | 0.0015 | 699988.1121 | 40236.0046
Maximum of Months | 122744.2724 | 235.9784 | 611.1484 | 0 | 0.0022 | 1087100 | 53985.7931
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 436428000000 | 330239.305 | 24-JAN-18:15 | 41924.28 | 36859.929 | 24715.266 | 0 | 3858.494 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 218876.335 | 0 | 0
February | 403607000000 | 318064.407 | 21-FEB-18:15 | 41924.28 | 36859.929 | 24715.266 | 0 | 3053.797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211511.135 | 0 | 0
March | 467663000000 | 331065.356 | 29-MAR-17:15 | 41924.28 | 36859.929 | 24715.266 | 0 | 5943.405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221622.475 | 0 | 0
April | 488178000000 | 349969.519 | 14-APR-17:15 | 41924.28 | 36859.929 | 24715.266 | 0 | 15756.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230713.803 | 0 | 0
May | 560105000000 | 382487.513 | 31-MAY-17:15 | 41924.28 | 36859.929 | 24715.266 | 0 | 37878.877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241109.161 | 0 | 0
June | 585367000000 | 396460.426 | 19-JUN-17:15 | 41924.28 | 36859.929 | 24715.266 | 0 | 53922.971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239037.979 | 0 | 0
July | 626814000000 | 421027.384 | 03-JUL-17:15 | 41924.28 | 36859.929 | 24715.266 | 0 | 72389.491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245138.418 | 0 | 0
August | 626511000000 | 400480.841 | 14-AUG-17:15 | 41924.28 | 36859.929 | 24715.266 | 0 | 53855.272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243126.093 | 0 | 0
September | 580704000000 | 378803.53 | 06-SEP-17:15 | 41924.28 | 36859.929 | 24715.266 | 0 | 37108.869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 238195.185 | 0 | 0
October | 515374000000 | 349587.014 | 20-OCT-17:15 | 41924.28 | 36859.929 | 24715.266 | 0 | 13696.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232391.38 | 0 | 0
November | 451076000000 | 328114.296 | 28-NOV-18:15 | 41924.28 | 36859.929 | 24715.266 | 0 | 3816.881 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 216792.94 | 0 | 0
December | 445329000000 | 327294.599 | 04-DEC-18:15 | 41924.28 | 36859.929 | 24715.266 | 0 | 4009.847 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 215780.277 | 0 | 0
Annual Sum or Average | 6187150000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 403607000000 | 318064.407 |  | 41924.28 | 36859.929 | 24715.266 | 0 | 3053.797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211511.135 | 0 | 0
Maximum of Months | 626814000000 | 421027.384 |  | 41924.28 | 36859.929 | 24715.266 | 0 | 72389.491 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 245138.418 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 170121.05 | 18573.9 | 0 | 188694.95
Cost per Total Building Area ($/m2) | 40.69 | 4.44 | 0 | 45.13
Cost per Net Conditioned Building Area ($/m2) | 40.69 | 4.44 | 0 | 45.13

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 7249.01 | 1733.88 | 1733.88
Net Site Energy | 7249.01 | 1733.88 | 1733.88
Total Source Energy | 19726.72 | 4718.41 | 4718.41
Net Source Energy | 19726.72 | 4718.41 | 4718.41
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1133.97 | 0 | 0 | 0 | 0
Cooling | 44.27 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 63.01 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 372.36 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 19.36 | 0 | 0 | 0 | 87.12
Refrigeration | 3697.48 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5896.56 | 1352.45 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 18.29 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 18.29 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 8.61 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 11.84 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 18.29 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 18.29 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 174.7 | 174.7 | 3.241 | 0.252 | 0.162 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 3.24 | 0.252 | 0.162
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 3.24 | 0.252 | 0.162
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4589.61 | 3483.07 | 1106.54 | 0.76 | 3.9
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26713.1 | 19141.35 | 7571.75 | 0.72 | 3.54
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 43686.83 | 30310.79 | 13376.04 | 0.69 | 3.22
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 129455.3 | 87969.17 | 41486.13 | 0.68 | 3.5
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 39178.3 | 26758.03 | 12420.28 | 0.68 | 3.46
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 30829.61 | 24622.23 | 6207.38 | 0.8 | 3.73
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 6663.98 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 37359.9 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 75965.72 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 183092.05 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 55683.53 | 0.8
PSZ-AC:6_HEATC | Coil:Heating:Gas | 49279.67 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.25 | 286.82 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.25 | 1427.83 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.89 | 2063.22 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.29 | 9917.51 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.62 | 1847.9 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.86 | 2036.79 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.72 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 50273.6287 | 43.5988 | 365.818 | 0 | 0.0002 | 2206940 | 18515.8836
February | 45684.8905 | 39.5921 | 337.2893 | 0 | 0.0002 | 2034850 | 16840.6736
March | 50241.1013 | 43.4663 | 384.2446 | 0 | 0.0002 | 2318190 | 18560.8448
April | 48065.3461 | 41.5219 | 378.7029 | 0 | 0.0002 | 2284800 | 17790.9046
May | 49201.5611 | 42.3729 | 411.0022 | 0 | 0.0002 | 2479760 | 18282.6946
June | 47645.8781 | 40.9691 | 409.4662 | 0 | 0.0002 | 2470540 | 17739.5838
July | 48745.0652 | 41.8099 | 437.5842 | 0 | 0.0002 | 2640260 | 18205.801
August | 49773.2839 | 42.6769 | 449.4857 | 0 | 0.0002 | 2712080 | 18597.9804
September | 46967.3195 | 40.2813 | 422.3029 | 0 | 0.0002 | 2548060 | 17543.8976
October | 47797.3926 | 41.0689 | 416.2194 | 0 | 0.0002 | 2511300 | 17812.6269
November | 47561.7121 | 41.0502 | 381.2845 | 0 | 0.0002 | 2300400 | 17624.4725
December | 49560.0687 | 42.91 | 373.1488 | 0 | 0.0002 | 2251220 | 18291.2854
Annual Sum or Average | 581517.2478 | 501.3185 | 4766.5487 | 0 | 0.0023 | 28758400 | 215806.6489
Minimum of Months | 45684.8905 | 39.5921 | 337.2893 | 0 | 0.0002 | 2034850 | 16840.6736
Maximum of Months | 50273.6287 | 43.5988 | 449.4857 | 0 | 0.0002 | 2712080 | 18597.9804
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 452507000000 | 305166.78 | 10-JAN-18:15 | 41924.28 | 36859.929 | 17710.991 | 0 | 0 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 204666.58 | 0 | 0
February | 417222000000 | 312683.309 | 13-FEB-11:45 | 62886.42 | 41401.92 | 17710.991 | 0 | 6283.839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184400.139 | 0 | 0
March | 475316000000 | 310357.913 | 04-MAR-11:45 | 62886.42 | 41401.92 | 17710.991 | 0 | 6117.232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182241.349 | 0 | 0
April | 468470000000 | 313445.627 | 10-APR-10:45 | 62886.42 | 41401.92 | 17710.991 | 0 | 2199.116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189247.179 | 0 | 0
May | 508445000000 | 332931.742 | 30-MAY-10:45 | 62886.42 | 41401.92 | 17710.991 | 0 | 10272.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200660.328 | 0 | 0
June | 506553000000 | 332005.942 | 28-JUN-17:15 | 41924.28 | 36859.929 | 17710.991 | 0 | 9158.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226351.892 | 0 | 0
July | 541352000000 | 342815.906 | 29-JUL-10:45 | 62886.42 | 41401.92 | 17710.991 | 0 | 14431.928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206384.647 | 0 | 0
August | 556078000000 | 350106.891 | 08-AUG-17:15 | 41924.28 | 36859.929 | 17710.991 | 0 | 19548.232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234063.459 | 0 | 0
September | 522447000000 | 346352.432 | 09-SEP-10:45 | 62886.42 | 41401.92 | 17710.991 | 0 | 15986.543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208366.557 | 0 | 0
October | 514912000000 | 332579.843 | 05-OCT-10:45 | 62886.42 | 41401.92 | 17710.991 | 0 | 9805.953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200774.559 | 0 | 0
November | 471669000000 | 321058.71 | 20-NOV-11:45 | 62886.42 | 41401.92 | 17710.991 | 0 | 7092.572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191966.807 | 0 | 0
December | 461586000000 | 312455.921 | 04-DEC-18:15 | 41924.28 | 36859.929 | 17710.991 | 0 | 0 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 211955.721 | 0 | 0
Annual Sum or Average | 5896560000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 417222000000 | 305166.78 |  | 41924.28 | 36859.929 | 17710.991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182241.349 | 0 | 0
Maximum of Months | 556078000000 | 350106.891 |  | 62886.42 | 41401.92 | 17710.991 | 0 | 19548.232 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 234063.459 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 200988.22 | 11520.57 | 0 | 212508.78
Cost per Total Building Area ($/m2) | 48.07 | 2.76 | 0 | 50.83
Cost per Net Conditioned Building Area ($/m2) | 48.07 | 2.76 | 0 | 50.83

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 7513.67 | 1797.19 | 1797.19
Net Site Energy | 7513.67 | 1797.19 | 1797.19
Total Source Energy | 22655.78 | 5419.01 | 5419.01
Net Source Energy | 22655.78 | 5419.01 | 5419.01
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1481.25 | 0 | 0 | 0 | 0
Cooling | 218.62 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.95 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 518.98 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 18.06 | 0 | 0 | 0 | 87.12
Refrigeration | 3295.24 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5815.23 | 1698.44 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 18.29 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 18.29 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 8.61 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 11.84 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 18.29 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 18.29 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 174.7 | 174.7 | 3.241 | 0.252 | 0.162 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 3.24 | 0.252 | 0.162
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 3.24 | 0.252 | 0.162
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7081.56 | 5426.47 | 1655.09 | 0.77 | 3.92
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 45969.11 | 32576.48 | 13392.63 | 0.71 | 3.25
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 38693.38 | 27900.68 | 10792.7 | 0.72 | 3.52
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 195799 | 132376.42 | 63422.58 | 0.68 | 3.49
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 58543.45 | 40160.21 | 18383.24 | 0.69 | 3.21
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 31565.14 | 25209.67 | 6355.48 | 0.8 | 3.73
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 9711.79 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 57787.79 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 85968.57 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 255992.73 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 79182.54 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 49430.68 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.39 | 452.51 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.1 | 2293.59 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.84 | 2016.87 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.88 | 14791.85 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.45 | 2682.49 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.91 | 2085.38 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.72 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 112959.5018 | 171.7084 | 650.5988 | 0 | 0.0013 | 3244240 | 46285.1668
February | 100015.0114 | 155.2599 | 606.3876 | 0 | 0.0012 | 3023910 | 41316.7012
March | 110764.2729 | 172.4407 | 676.2032 | 0 | 0.0013 | 3372090 | 45808.6192
April | 105842.4638 | 170.1277 | 696.4365 | 0 | 0.0013 | 3473200 | 44329.1162
May | 113220.2474 | 183.3179 | 757.4963 | 0 | 0.0014 | 3777760 | 47557.4776
June | 120579.5282 | 196.7975 | 821.4335 | 0 | 0.0015 | 4096680 | 50811.2541
July | 133486.0801 | 218.1439 | 912.0052 | 0 | 0.0017 | 4548390 | 56279.2466
August | 134894.9632 | 220.382 | 921.0263 | 0 | 0.0017 | 4593380 | 56866.5609
September | 118167.4596 | 192.6657 | 803.1683 | 0 | 0.0015 | 4005580 | 49774.5547
October | 111178.1739 | 179.2125 | 736.3232 | 0 | 0.0014 | 3672140 | 46616.6633
November | 106155.2518 | 165.8709 | 653.7585 | 0 | 0.0012 | 3260180 | 43965.4248
December | 111625.4526 | 170.5716 | 651.2903 | 0 | 0.0013 | 3247730 | 45831.1519
Annual Sum or Average | 1378890 | 2196.4986 | 8886.1276 | 0 | 0.0168 | 44315300 | 575441.9371
Minimum of Months | 100015.0114 | 155.2599 | 606.3876 | 0 | 0.0012 | 3023910 | 41316.7012
Maximum of Months | 134894.9632 | 220.382 | 921.0263 | 0 | 0.0017 | 4593380 | 56866.5609
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 425722000000 | 296158.733 | 23-JAN-18:15 | 41924.28 | 36859.929 | 24453.62 | 0 | 0 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 188915.904 | 0 | 0
February | 396810000000 | 308216.252 | 10-FEB-18:15 | 41924.28 | 36859.929 | 24453.62 | 0 | 0 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 200973.423 | 0 | 0
March | 442499000000 | 302704.008 | 31-MAR-17:15 | 41924.28 | 36859.929 | 24453.62 | 0 | 4524.069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194942.109 | 0 | 0
April | 455767000000 | 339396.219 | 21-APR-17:15 | 41924.28 | 36859.929 | 24453.62 | 0 | 22020.457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214137.934 | 0 | 0
May | 495733000000 | 351774.728 | 31-MAY-17:15 | 41924.28 | 36859.929 | 24453.62 | 0 | 37254.468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211282.431 | 0 | 0
June | 537583000000 | 387633.841 | 27-JUN-17:15 | 41924.28 | 36859.929 | 24453.62 | 0 | 71700.475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212695.537 | 0 | 0
July | 596859000000 | 394768.163 | 11-JUL-10:45 | 62886.42 | 41401.92 | 24453.62 | 0 | 47471.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218554.353 | 0 | 0
August | 602762000000 | 407757.495 | 05-AUG-10:45 | 62886.42 | 41401.92 | 24453.62 | 0 | 54362.057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224653.478 | 0 | 0
September | 525629000000 | 373921.909 | 01-SEP-17:15 | 41924.28 | 36859.929 | 24453.62 | 0 | 51297.952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219386.128 | 0 | 0
October | 481873000000 | 344195.043 | 06-OCT-10:45 | 62886.42 | 41401.92 | 24453.62 | 0 | 15527.627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199925.456 | 0 | 0
November | 427815000000 | 304844.38 | 21-NOV-18:15 | 41924.28 | 36859.929 | 24453.62 | 0 | 0 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 197601.551 | 0 | 0
December | 426180000000 | 295039.139 | 05-DEC-11:45 | 62886.42 | 41401.92 | 24453.62 | 0 | 1400.152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164897.028 | 0 | 0
Annual Sum or Average | 5815230000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 396810000000 | 295039.139 |  | 41924.28 | 36859.929 | 24453.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164897.028 | 0 | 0
Maximum of Months | 602762000000 | 407757.495 |  | 62886.42 | 41401.92 | 24453.62 | 0 | 71700.475 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 224653.478 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 153776.91 | 13208.75 | 0 | 166985.66
Cost per Total Building Area ($/m2) | 36.78 | 3.16 | 0 | 39.94
Cost per Net Conditioned Building Area ($/m2) | 36.78 | 3.16 | 0 | 39.94

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 7897.36 | 1888.96 | 1888.96
Net Site Energy | 7897.36 | 1888.96 | 1888.96
Total Source Energy | 19786.3 | 4732.67 | 4732.67
Net Source Energy | 19786.3 | 4732.67 | 4732.67
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2104.43 | 0 | 0 | 0 | 0
Cooling | 10.42 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.88 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 416.37 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 20.98 | 0 | 0 | 0 | 87.12
Refrigeration | 3363.72 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5572.83 | 2324.53 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 18.29 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 18.29 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 8.61 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 11.84 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 18.29 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 18.29 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 174.7 | 174.7 | 5.835 | 0.39 | 0.223 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 5.83 | 0.39 | 0.223
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 5.83 | 0.39 | 0.223
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5142.74 | 4071.64 | 1071.1 | 0.79 | 4.01
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 29304.75 | 22345.87 | 6958.88 | 0.76 | 3.67
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 24276.06 | 19388.2 | 4887.86 | 0.8 | 3.77
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 127813.47 | 94193.89 | 33619.58 | 0.74 | 3.78
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 29238.63 | 23351.59 | 5887.04 | 0.8 | 3.73
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26749.05 | 21363.27 | 5385.78 | 0.8 | 3.77
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 8203.38 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 47707.67 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 65270.98 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 222481.34 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 64132.94 | 0.8
PSZ-AC:6_HEATC | Coil:Heating:Gas | 45079.11 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.3 | 353.56 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.6 | 1818.58 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.47 | 1670.65 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.43 | 12054.39 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.77 | 1931.68 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.62 | 1840.84 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.72 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 54753.5998 | 47.7155 | 356.9872 | 0 | 0.0002 | 2153490 | 20039.4669
February | 47314.2674 | 41.0883 | 334.2765 | 0 | 0.0002 | 2016620 | 17395.4119
March | 52639.331 | 45.7446 | 366.1729 | 0 | 0.0002 | 2209010 | 19335.7399
April | 49501.9128 | 42.9315 | 359.8603 | 0 | 0.0002 | 2171000 | 18230.6147
May | 50396.1345 | 43.5982 | 385.8343 | 0 | 0.0002 | 2327780 | 18619.352
June | 48442.7454 | 41.8477 | 381.7108 | 0 | 0.0002 | 2302950 | 17930.7001
July | 48916.0172 | 42.1804 | 399.0738 | 0 | 0.0002 | 2407760 | 18147.4742
August | 49852.3609 | 42.9786 | 408.3596 | 0 | 0.0002 | 2463790 | 18499.875
September | 47620.5362 | 41.0302 | 394.4243 | 0 | 0.0002 | 2379730 | 17684.9205
October | 49893.2808 | 43.0986 | 393.5387 | 0 | 0.0002 | 2374310 | 18468.8195
November | 50150.6903 | 43.4966 | 364.1269 | 0 | 0.0002 | 2196740 | 18468.1752
December | 54624.3324 | 47.577 | 360.7772 | 0 | 0.0002 | 2176380 | 20006.2902
Annual Sum or Average | 604105.2088 | 523.2871 | 4505.1424 | 0 | 0.0023 | 27179600 | 222826.8402
Minimum of Months | 47314.2674 | 41.0302 | 334.2765 | 0 | 0.0002 | 2016620 | 17395.4119
Maximum of Months | 54753.5998 | 47.7155 | 408.3596 | 0 | 0.0002 | 2463790 | 20039.4669
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 441547000000 | 307988.55 | 05-JAN-18:15 | 41924.28 | 36859.929 | 19800.603 | 0 | 0 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 205398.737 | 0 | 0
February | 413482000000 | 314024.406 | 15-FEB-18:15 | 41924.28 | 36859.929 | 19800.603 | 0 | 710.463 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 210724.13 | 0 | 0
March | 452931000000 | 301214.464 | 27-MAR-17:15 | 41924.28 | 36859.929 | 19800.603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202629.651 | 0 | 0
April | 445137000000 | 310856.069 | 29-APR-10:45 | 62886.42 | 41401.92 | 19800.603 | 0 | 2811.574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183955.551 | 0 | 0
May | 477283000000 | 320231.346 | 25-MAY-17:15 | 41924.28 | 36859.929 | 19800.603 | 0 | 2967.809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218678.724 | 0 | 0
June | 472191000000 | 325727.573 | 16-JUN-10:45 | 62886.42 | 41401.92 | 19800.603 | 0 | 6376.155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195262.474 | 0 | 0
July | 493681000000 | 339455.744 | 03-JUL-10:45 | 62886.42 | 41401.92 | 19800.603 | 0 | 10551.712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204815.088 | 0 | 0
August | 505169000000 | 335026.879 | 15-AUG-10:45 | 62886.42 | 41401.92 | 19800.603 | 0 | 7445.955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203491.98 | 0 | 0
September | 487934000000 | 342294.83 | 29-SEP-10:45 | 62886.42 | 41401.92 | 19800.603 | 0 | 9867.487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208338.399 | 0 | 0
October | 486823000000 | 320902.109 | 16-OCT-17:15 | 41924.28 | 36859.929 | 19800.603 | 0 | 5007.286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 217310.011 | 0 | 0
November | 450414000000 | 315765.488 | 16-NOV-18:15 | 41924.28 | 36859.929 | 19800.603 | 0 | 0 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 213175.675 | 0 | 0
December | 446239000000 | 307786.637 | 14-DEC-18:15 | 41924.28 | 36859.929 | 19800.603 | 0 | 0 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 205196.824 | 0 | 0
Annual Sum or Average | 5572830000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 413482000000 | 301214.464 |  | 41924.28 | 36859.929 | 19800.603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183955.551 | 0 | 0
Maximum of Months | 505169000000 | 342294.83 |  | 62886.42 | 41401.92 | 19800.603 | 0 | 10551.712 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 218678.724 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 223578.62 | 19696.78 | 0 | 243275.4
Cost per Total Building Area ($/m2) | 53.48 | 4.71 | 0 | 58.19
Cost per Net Conditioned Building Area ($/m2) | 53.48 | 4.71 | 0 | 58.19

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 8717.7 | 2085.18 | 2085.18
Net Site Energy | 8717.7 | 2085.18 | 2085.18
Total Source Energy | 24246.41 | 5799.47 | 5799.47
Net Source Energy | 24246.41 | 5799.47 | 5799.47
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2568.75 | 0 | 0 | 0 | 0
Cooling | 152.91 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.94 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 549.63 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 21.21 | 0 | 0 | 0 | 87.12
Refrigeration | 3443.69 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5928.61 | 2789.09 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 18.29 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 18.29 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 8.61 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 11.84 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 18.29 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 18.29 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 174.7 | 174.7 | 3.241 | 0.385 | 0.305 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10035.48 | 7125.87 | 2909.61 | 0.71 | 3.75
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 58875.96 | 39805.05 | 19070.91 | 0.68 | 3.19
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 48551.09 | 32824.58 | 15726.51 | 0.68 | 3.19
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 203021.27 | 137259.28 | 65762 | 0.68 | 3.49
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 61927.81 | 41868.35 | 20059.46 | 0.68 | 3.19
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 34541.56 | 26669.27 | 7872.29 | 0.77 | 3.65
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 12647.62 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 73435.88 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 119997.5 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 321273.9 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 99053.99 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 57415.88 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.46 | 533.75 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.37 | 2592.92 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.96 | 2138.21 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 8.18 | 15337.47 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.49 | 2727.32 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.94 | 2117.15 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.72 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 100686.3004 | 169.7531 | 433.0937 | 0 | 0.0018 | 26927.1288 | 42012.731
February | 88526.251 | 150.9903 | 390.3882 | 0 | 0.0016 | 24272.6773 | 37097.76
March | 93302.7713 | 166.6755 | 453.0756 | 0 | 0.0019 | 28173.3298 | 39788.6914
April | 87141.6633 | 160.5262 | 449.9745 | 0 | 0.0018 | 27982.2655 | 37605.3958
May | 92435.4085 | 178.7499 | 524.0885 | 0 | 0.0021 | 32594.0434 | 40664.5291
June | 98169.843 | 194.5803 | 582.7805 | 0 | 0.0023 | 36245.6894 | 43620.7678
July | 104702.5656 | 208.1161 | 624.8053 | 0 | 0.0025 | 38859.5704 | 46577.2301
August | 105508.8994 | 209.6422 | 629.1941 | 0 | 0.0025 | 39132.5108 | 46928.9269
September | 92957.8852 | 183.1936 | 546.008 | 0 | 0.0022 | 33958.3338 | 41208.311
October | 91143.3485 | 172.7226 | 497.2786 | 0 | 0.002 | 30925.5866 | 39773.4634
November | 90102.0462 | 163.319 | 450.5709 | 0 | 0.0018 | 28018.4416 | 38639.6597
December | 97234.5014 | 166.2622 | 431.1044 | 0 | 0.0018 | 26804.4012 | 40785.354
Annual Sum or Average | 1141910 | 2124.531 | 6012.3622 | 0 | 0.0245 | 373893.9785 | 494702.8204
Minimum of Months | 87141.6633 | 150.9903 | 390.3882 | 0 | 0.0016 | 24272.6773 | 37097.76
Maximum of Months | 105508.8994 | 209.6422 | 629.1941 | 0 | 0.0025 | 39132.5108 | 46928.9269
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 426967000000 | 309460.898 | 09-JAN-11:15 | 62886.42 | 41401.92 | 25577.726 | 0 | 2393.608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177201.223 | 0 | 0
February | 384877000000 | 299193.952 | 13-FEB-11:15 | 62886.42 | 41401.92 | 25577.726 | 0 | 203.598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169124.287 | 0 | 0
March | 446728000000 | 337585.542 | 09-MAR-18:15 | 41924.28 | 36859.929 | 25577.726 | 0 | 5985.125 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 223233.481 | 0 | 0
April | 443698000000 | 335038.611 | 04-APR-17:15 | 41924.28 | 36859.929 | 25577.726 | 0 | 7735.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222941.669 | 0 | 0
May | 516824000000 | 360834.289 | 15-MAY-17:15 | 41924.28 | 36859.929 | 25577.726 | 0 | 17965.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 238506.871 | 0 | 0
June | 574726000000 | 417955.311 | 30-JUN-17:15 | 41924.28 | 36859.929 | 25577.726 | 0 | 66469.758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 247123.617 | 0 | 0
July | 616173000000 | 425977.019 | 25-JUL-10:00 | 62886.42 | 41401.92 | 25577.726 | 0 | 71404.889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224706.063 | 0 | 0
August | 620501000000 | 420248.332 | 17-AUG-17:15 | 41924.28 | 36859.929 | 25577.726 | 0 | 69036.492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246849.904 | 0 | 0
September | 538457000000 | 369667.428 | 08-SEP-17:15 | 41924.28 | 36859.929 | 25577.726 | 0 | 35026.899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230278.593 | 0 | 0
October | 490369000000 | 349188.304 | 20-OCT-17:15 | 41924.28 | 36859.929 | 25577.726 | 0 | 13811.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231014.919 | 0 | 0
November | 444272000000 | 339158.831 | 03-NOV-17:15 | 41924.28 | 36859.929 | 25577.726 | 0 | 6652.628 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 224139.268 | 0 | 0
December | 425021000000 | 309486.297 | 23-DEC-11:15 | 62886.42 | 41401.92 | 25577.726 | 0 | 1439.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178181.081 | 0 | 0
Annual Sum or Average | 5928610000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 384877000000 | 299193.952 |  | 41924.28 | 36859.929 | 25577.726 | 0 | 203.598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169124.287 | 0 | 0
Maximum of Months | 620501000000 | 425977.019 |  | 62886.42 | 41401.92 | 25577.726 | 0 | 71404.889 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 247123.617 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 115181.62 | 27161.44 | 0 | 142343.06
Cost per Total Building Area ($/m2) | 27.55 | 6.5 | 0 | 34.05
Cost per Net Conditioned Building Area ($/m2) | 27.55 | 6.5 | 0 | 34.05

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 7988.87 | 1910.85 | 1910.85
Net Site Energy | 7988.87 | 1910.85 | 1910.85
Total Source Energy | 21243.6 | 5081.24 | 5081.24
Net Source Energy | 21243.6 | 5081.24 | 5081.24
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2144.49 | 0 | 0 | 0 | 0
Cooling | 91.24 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.93 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 597.08 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 20.93 | 0 | 0 | 0 | 87.12
Refrigeration | 3153.63 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5624.33 | 2364.55 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 18.29 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 18.29 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 8.61 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 11.84 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 18.29 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 18.29 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 174.7 | 174.7 | 3.241 | 0.385 | 0.305 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8518.29 | 6803.18 | 1715.11 | 0.8 | 4.04
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 44792.42 | 35447.42 | 9344.99 | 0.79 | 3.44
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 32809.06 | 26203.13 | 6605.93 | 0.8 | 3.73
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 224939.38 | 155185.77 | 69753.6 | 0.69 | 3.32
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 49874.58 | 39832.59 | 10041.98 | 0.8 | 3.45
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 33613.11 | 26845.29 | 6767.82 | 0.8 | 3.73
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 11428.14 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 65286.82 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 96653.64 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 285100.23 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 88841.8 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 48706.84 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.51 | 596.88 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.65 | 2900.62 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.98 | 2167.56 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.59 | 1017.59 | 9.57 | 16462.1 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.01 | 3295.01 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.03 | 2220.68 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.72 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 134312.2665 | 217.4333 | 517.5596 | 0 | 0.0021 | 538067.0733 | 55854.8848
February | 119126.5216 | 194.8273 | 469.7469 | 0 | 0.0019 | 488374.6942 | 49733.7523
March | 131203.9647 | 216.855 | 529.6876 | 0 | 0.0021 | 550709.1442 | 54999.1301
April | 124257.7324 | 209.4974 | 523.9612 | 0 | 0.0021 | 544785.0213 | 52491.7868
May | 131636.6886 | 226.9661 | 582.2899 | 0 | 0.0023 | 605466.4884 | 56102.1602
June | 137608.0469 | 239.717 | 621.9922 | 0 | 0.0024 | 646765.0806 | 58887.908
July | 151891.2622 | 265.3544 | 690.6429 | 0 | 0.0027 | 718154.8826 | 65074.3842
August | 151858.1417 | 265.1386 | 689.6376 | 0 | 0.0027 | 717108.5794 | 65044.7058
September | 136637.9374 | 237.7627 | 616.1768 | 0 | 0.0024 | 640716.4169 | 58446.8366
October | 130824.5393 | 221.8608 | 558.6439 | 0 | 0.0022 | 580855.0027 | 55392.6061
November | 126441.8556 | 208.1913 | 506.171 | 0 | 0.002 | 526253.587 | 52925.1407
December | 134465.7332 | 217.3641 | 516.432 | 0 | 0.0021 | 536892.4315 | 55887.5532
Annual Sum or Average | 1610260 | 2720.968 | 6822.9415 | 0 | 0.0268 | 7094150 | 680840.8489
Minimum of Months | 119126.5216 | 194.8273 | 469.7469 | 0 | 0.0019 | 488374.6942 | 49733.7523
Maximum of Months | 151891.2622 | 265.3544 | 690.6429 | 0 | 0.0027 | 718154.8826 | 65074.3842
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 426586000000 | 292411.955 | 02-JAN-11:15 | 62886.42 | 41401.92 | 27773.776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160349.839 | 0 | 0
February | 387189000000 | 294053.239 | 14-FEB-18:15 | 41924.28 | 36859.929 | 27773.776 | 0 | 0 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 183490.254 | 0 | 0
March | 436609000000 | 298559.491 | 08-MAR-18:15 | 41924.28 | 36859.929 | 27773.776 | 0 | 0 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 187996.505 | 0 | 0
April | 431912000000 | 315354.608 | 21-APR-17:15 | 41924.28 | 36859.929 | 27773.776 | 0 | 9891.815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198904.807 | 0 | 0
May | 480021000000 | 334573.961 | 30-MAY-10:45 | 62886.42 | 41401.92 | 27773.776 | 0 | 10112.076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192399.768 | 0 | 0
June | 512763000000 | 352902.47 | 29-JUN-17:15 | 41924.28 | 36859.929 | 27773.776 | 0 | 29938.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216406.075 | 0 | 0
July | 569362000000 | 366064.326 | 18-JUL-17:15 | 41924.28 | 36859.929 | 27773.776 | 0 | 36349.706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223156.635 | 0 | 0
August | 568532000000 | 376482.099 | 01-AUG-17:15 | 41924.28 | 36859.929 | 27773.776 | 0 | 40324.395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229599.718 | 0 | 0
September | 507968000000 | 340933.042 | 01-SEP-17:15 | 41924.28 | 36859.929 | 27773.776 | 0 | 14872.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219502.837 | 0 | 0
October | 460509000000 | 327049.702 | 11-OCT-17:15 | 41924.28 | 36859.929 | 27773.776 | 0 | 8822.519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211669.198 | 0 | 0
November | 417220000000 | 299888.83 | 10-NOV-11:15 | 62886.42 | 41401.92 | 27773.776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167826.714 | 0 | 0
December | 425655000000 | 291341.729 | 22-DEC-11:15 | 62886.42 | 41401.92 | 27773.776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159279.613 | 0 | 0
Annual Sum or Average | 5624330000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 387189000000 | 291341.729 |  | 41924.28 | 36859.929 | 27773.776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159279.613 | 0 | 0
Maximum of Months | 569362000000 | 376482.099 |  | 62886.42 | 41401.92 | 27773.776 | 0 | 40324.395 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 229599.718 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 57885.3 | 16460.58 | 0 | 74345.88
Cost per Total Building Area ($/m2) | 13.85 | 3.94 | 0 | 17.78
Cost per Net Conditioned Building Area ($/m2) | 13.85 | 3.94 | 0 | 17.78

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 8571.78 | 2050.27 | 2050.27
Net Site Energy | 8571.78 | 2050.27 | 2050.27
Total Source Energy | 12926.82 | 3091.95 | 3091.95
Net Source Energy | 12926.82 | 3091.95 | 3091.95
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2863.83 | 0 | 0 | 0 | 0
Cooling | 15.33 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.84 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 485.33 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 21.99 | 0 | 0 | 0 | 87.12
Refrigeration | 3203.89 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5486.83 | 3084.94 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 18.29 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 18.29 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 8.61 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 11.84 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 18.29 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 18.29 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 174.7 | 174.7 | 3.241 | 0.385 | 0.305 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6399.33 | 5088.51 | 1310.82 | 0.8 | 4.02
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 38334.02 | 28981.84 | 9352.18 | 0.76 | 3.61
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 27455.53 | 21927.5 | 5528.03 | 0.8 | 3.77
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 168232.53 | 117682.76 | 50549.77 | 0.7 | 3.59
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 36044.73 | 28787.31 | 7257.42 | 0.8 | 3.73
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 28659.69 | 22889.21 | 5770.48 | 0.8 | 3.77
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 10353.65 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 62041.17 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 88034.11 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 274313.68 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 82817.51 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 49699.27 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.38 | 444.14 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.05 | 2238.98 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.66 | 1889.45 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.42 | 13924.91 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.18 | 2381.33 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.73 | 1972.32 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.72 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 43389.7184 | 53.8065 | 92.256 | 0 | 0.0004 | 1217930 | 16561.7213
February | 36642.6175 | 46.3776 | 83.8996 | 0 | 0.0004 | 1107810 | 14086.8416
March | 39681.65 | 50.8374 | 94.7739 | 0 | 0.0004 | 1251510 | 15320.8494
April | 35516.15 | 46.802 | 93.1332 | 0 | 0.0004 | 1230080 | 13851.9349
May | 32930.3883 | 45.8106 | 101.7787 | 0 | 0.0004 | 1344670 | 13102.2044
June | 29973.276 | 43.1393 | 101.8485 | 0 | 0.0004 | 1345790 | 12080.1213
July | 29087.8299 | 43.4624 | 109.0397 | 0 | 0.0004 | 1441020 | 11894.3565
August | 28946.681 | 43.9144 | 112.7432 | 0 | 0.0004 | 1490040 | 11907.6393
September | 30401.2015 | 43.7573 | 103.3164 | 0 | 0.0004 | 1365190 | 12252.8207
October | 35353.5049 | 47.8365 | 100.6799 | 0 | 0.0004 | 1329960 | 13922.2458
November | 39089.9882 | 49.861 | 91.9662 | 0 | 0.0004 | 1214390 | 15069.0196
December | 43409.7308 | 54.0061 | 93.4146 | 0 | 0.0004 | 1233260 | 16588.0799
Annual Sum or Average | 424422.7366 | 569.6111 | 1178.85 | 0 | 0.0049 | 15571600 | 166637.8346
Minimum of Months | 28946.681 | 43.1393 | 83.8996 | 0 | 0.0004 | 1107810 | 11894.3565
Maximum of Months | 43409.7308 | 54.0061 | 112.7432 | 0 | 0.0004 | 1490040 | 16588.0799
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 429152000000 | 302416.592 | 14-JAN-11:15 | 62886.42 | 41401.92 | 22982.056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175146.196 | 0 | 0
February | 390348000000 | 293732.771 | 21-FEB-11:15 | 62886.42 | 41401.92 | 22982.056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166462.374 | 0 | 0
March | 440982000000 | 302957.811 | 30-MAR-10:15 | 62886.42 | 41401.92 | 22982.056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175687.415 | 0 | 0
April | 433431000000 | 308095.339 | 29-APR-10:15 | 62886.42 | 41401.92 | 22982.056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180824.943 | 0 | 0
May | 473808000000 | 329721.111 | 05-MAY-17:15 | 41924.28 | 36859.929 | 22982.056 | 0 | 6047.095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221907.751 | 0 | 0
June | 474204000000 | 328646.474 | 28-JUN-10:45 | 62886.42 | 41401.92 | 22982.056 | 0 | 6771.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194604.447 | 0 | 0
July | 507758000000 | 345875.751 | 31-JUL-17:15 | 41924.28 | 36859.929 | 22982.056 | 0 | 14382.063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229727.423 | 0 | 0
August | 525031000000 | 342834.724 | 18-AUG-17:15 | 41924.28 | 36859.929 | 22982.056 | 0 | 12673.198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228395.26 | 0 | 0
September | 481038000000 | 345131.699 | 02-SEP-10:45 | 62886.42 | 41401.92 | 22982.056 | 0 | 10151.299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207710.004 | 0 | 0
October | 468626000000 | 313741.704 | 18-OCT-17:15 | 41924.28 | 36859.929 | 22982.056 | 0 | 0 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 207970.439 | 0 | 0
November | 427904000000 | 316168.059 | 03-NOV-17:15 | 41924.28 | 36859.929 | 22982.056 | 0 | 0 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 210396.794 | 0 | 0
December | 434554000000 | 296691.209 | 05-DEC-11:15 | 62886.42 | 41401.92 | 22982.056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169420.813 | 0 | 0
Annual Sum or Average | 5486830000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 390348000000 | 293732.771 |  | 41924.28 | 36859.929 | 22982.056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166462.374 | 0 | 0
Maximum of Months | 525031000000 | 345875.751 |  | 62886.42 | 41401.92 | 22982.056 | 0 | 14382.063 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 229727.423 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 108478.39 | 25790.92 | 0 | 134269.31
Cost per Total Building Area ($/m2) | 25.95 | 6.17 | 0 | 32.12
Cost per Net Conditioned Building Area ($/m2) | 25.95 | 6.17 | 0 | 32.12

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 9241.7 | 2210.51 | 2210.51
Net Site Energy | 9241.7 | 2210.51 | 2210.51
Total Source Energy | 24290.98 | 5810.14 | 5810.14
Net Source Energy | 24290.98 | 5810.14 | 5810.14
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 3233.97 | 0 | 0 | 0 | 0
Cooling | 101.06 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.86 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 608.67 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 22.52 | 0 | 0 | 0 | 87.12
Refrigeration | 3294.04 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5786.08 | 3455.62 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 18.29 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 18.29 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 8.61 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 11.84 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 18.29 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 18.29 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 174.7 | 174.7 | 3.241 | 0.385 | 0.305 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12268.36 | 8636.02 | 3632.34 | 0.7 | 3.73
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 69994.27 | 47321.95 | 22672.32 | 0.68 | 3.19
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 48502.84 | 32791.96 | 15710.88 | 0.68 | 3.19
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 235187.23 | 159006.14 | 76181.09 | 0.68 | 3.27
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 77259.35 | 52233.75 | 25025.6 | 0.68 | 3.11
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 33888.91 | 26391.6 | 7497.3 | 0.78 | 3.67
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 14941.44 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 87881.03 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 140042.56 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 384601.98 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 122476.32 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 60061.39 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.55 | 638.15 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.82 | 3082.57 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.95 | 2136.08 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.59 | 1017.59 | 9.47 | 16293.5 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.11 | 3402.53 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.94 | 2117.8 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.72 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 180517.6499 | 297.7064 | 803.1431 | 0 | 0.0025 | 184852.4248 | 75274.9059
February | 159475.2866 | 265.6029 | 725.1049 | 0 | 0.0022 | 166895.2143 | 66748.8651
March | 173256.4102 | 293.1159 | 815.1058 | 0 | 0.0025 | 187617.5718 | 72953.055
April | 164201.0224 | 285.0619 | 816.0611 | 0 | 0.0025 | 187848.4312 | 69834.8069
May | 177690.1257 | 316.9969 | 934.1584 | 0 | 0.0028 | 215045.3467 | 76386.0617
June | 189821.299 | 343.6357 | 1027.8905 | 0 | 0.0031 | 236629.4184 | 82078.8188
July | 206905.4054 | 375.5682 | 1126.4256 | 0 | 0.0034 | 259314.3872 | 89562.0711
August | 204258.1918 | 370.5857 | 1110.9506 | 0 | 0.0033 | 255751.6523 | 88399.2288
September | 182911.5225 | 329.9054 | 983.1511 | 0 | 0.003 | 226328.4172 | 78974.2386
October | 173357.2539 | 305.0148 | 885.8881 | 0 | 0.0027 | 203927.6696 | 74116.8665
November | 166838.974 | 284.8794 | 800.6237 | 0 | 0.0025 | 184288.1156 | 70501.4196
December | 177908.4255 | 295.4772 | 803.9667 | 0 | 0.0025 | 185045.2975 | 74385.1577
Annual Sum or Average | 2157140 | 3763.5503 | 10832.4695 | 0 | 0.033 | 2493540 | 919215.4957
Minimum of Months | 159475.2866 | 265.6029 | 725.1049 | 0 | 0.0022 | 166895.2143 | 66748.8651
Maximum of Months | 206905.4054 | 375.5682 | 1126.4256 | 0 | 0.0034 | 259314.3872 | 89562.0711
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 428936000000 | 294456.553 | 17-JAN-18:15 | 41924.28 | 36859.929 | 27801.542 | 0 | 358.891 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 183506.91 | 0 | 0
February | 387268000000 | 296086.3 | 28-FEB-11:15 | 62886.42 | 41401.92 | 27801.542 | 0 | 900.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163096.132 | 0 | 0
March | 435352000000 | 320617.212 | 14-MAR-17:15 | 41924.28 | 36859.929 | 27801.542 | 0 | 2227.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211804.334 | 0 | 0
April | 435888000000 | 322985.766 | 10-APR-10:15 | 62886.42 | 41401.92 | 27801.542 | 0 | 2550.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188345.843 | 0 | 0
May | 498997000000 | 361596.638 | 30-MAY-17:15 | 41924.28 | 36859.929 | 27801.542 | 0 | 16491.198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 238519.689 | 0 | 0
June | 549081000000 | 388844.993 | 20-JUN-17:15 | 41924.28 | 36859.929 | 27801.542 | 0 | 41055.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241203.89 | 0 | 0
July | 601719000000 | 416808.715 | 14-JUL-10:00 | 62886.42 | 41401.92 | 27801.542 | 0 | 61888.213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222830.62 | 0 | 0
August | 593452000000 | 410764.299 | 04-AUG-17:15 | 41924.28 | 36859.929 | 27801.542 | 0 | 58426.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245751.916 | 0 | 0
September | 525178000000 | 364923.79 | 06-SEP-10:45 | 62886.42 | 41401.92 | 27801.542 | 0 | 19996.891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212837.017 | 0 | 0
October | 473199000000 | 344225.342 | 31-OCT-17:15 | 41924.28 | 36859.929 | 27801.542 | 0 | 7653.165 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 225981.425 | 0 | 0
November | 427627000000 | 344485.892 | 02-NOV-17:15 | 41924.28 | 36859.929 | 27801.542 | 0 | 6495.065 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 227400.075 | 0 | 0
December | 429384000000 | 302275.528 | 12-DEC-18:15 | 41924.28 | 36859.929 | 27801.542 | 0 | 902.301 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 190782.475 | 0 | 0
Annual Sum or Average | 5786080000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 387268000000 | 294456.553 |  | 41924.28 | 36859.929 | 27801.542 | 0 | 358.891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163096.132 | 0 | 0
Maximum of Months | 601719000000 | 416808.715 |  | 62886.42 | 41401.92 | 27801.542 | 0 | 61888.213 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 245751.916 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 154655.88 | 29170.56 | 0 | 183826.44
Cost per Total Building Area ($/m2) | 36.99 | 6.98 | 0 | 43.97
Cost per Net Conditioned Building Area ($/m2) | 36.99 | 6.98 | 0 | 43.97

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 8521.23 | 2038.18 | 2038.18
Net Site Energy | 8521.23 | 2038.18 | 2038.18
Total Source Energy | 21630.54 | 5173.79 | 5173.79
Net Source Energy | 21630.54 | 5173.79 | 5173.79
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2762.66 | 0 | 0 | 0 | 0
Cooling | 54.44 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.87 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 669.8 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 22.45 | 0 | 0 | 0 | 87.12
Refrigeration | 3030.44 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5537 | 2984.24 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 18.29 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 18.29 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 8.61 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 11.84 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 18.29 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 18.29 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 174.7 | 174.7 | 3.241 | 0.385 | 0.305 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10004.77 | 7990.36 | 2014.41 | 0.8 | 4.04
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 55551.93 | 42896.88 | 12655.05 | 0.77 | 3.39
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 31840.71 | 25429.75 | 6410.96 | 0.8 | 3.73
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 257127.8 | 176587.92 | 80539.88 | 0.69 | 3.29
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 57055.99 | 45568.07 | 11487.92 | 0.8 | 3.45
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 33171.33 | 26492.46 | 6678.87 | 0.8 | 3.73
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 13494.86 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 78623.36 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 111971.36 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 341193.76 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 107046.74 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 51127.55 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.6 | 701.03 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.11 | 3405.95 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.92 | 2103.59 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 10.81 | 18308.67 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.45 | 3769.46 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2 | 2191.5 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.72 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 139689.477 | 223.99 | 526.6526 | 0 | 0.0021 | 547504.1718 | 57880.3189
February | 124012.8102 | 200.12 | 474.4086 | 0 | 0.0019 | 493201.4629 | 51509.0098
March | 135055.1459 | 221.0818 | 533.6608 | 0 | 0.0021 | 554824.6979 | 56403.7375
April | 126963.3368 | 211.8787 | 523.5693 | 0 | 0.0021 | 544362.5727 | 53420.8892
May | 133735.0694 | 227.0906 | 572.663 | 0 | 0.0022 | 595433.5157 | 56653.7848
June | 134742.7817 | 232.8499 | 598.8888 | 0 | 0.0023 | 622729.5672 | 57477.7617
July | 148383.441 | 258.8779 | 672.8077 | 0 | 0.0026 | 699606.9948 | 63537.3708
August | 146151.5324 | 254.6304 | 660.774 | 0 | 0.0026 | 687091.6996 | 62546.9928
September | 129982.5509 | 223.4068 | 571.1449 | 0 | 0.0022 | 593873.2496 | 55327.8106
October | 131053.9543 | 220.2964 | 549.0505 | 0 | 0.0022 | 570866.957 | 55298.1312
November | 129974.6335 | 212.1791 | 510.4138 | 0 | 0.002 | 530651.3928 | 54224.4569
December | 139715.5536 | 223.3649 | 523.1415 | 0 | 0.0021 | 543848.9304 | 57825.7113
Annual Sum or Average | 1619460 | 2709.7666 | 6717.1754 | 0 | 0.0265 | 6984000 | 682105.9754
Minimum of Months | 124012.8102 | 200.12 | 474.4086 | 0 | 0.0019 | 493201.4629 | 51509.0098
Maximum of Months | 148383.441 | 258.8779 | 672.8077 | 0 | 0.0026 | 699606.9948 | 63537.3708
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 434068000000 | 298038.773 | 23-JAN-11:15 | 62886.42 | 41401.92 | 30611.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163139.324 | 0 | 0
February | 391016000000 | 294241.32 | 11-FEB-11:15 | 62886.42 | 41401.92 | 30611.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159341.871 | 0 | 0
March | 439872000000 | 306049.227 | 30-MAR-17:15 | 41924.28 | 36859.929 | 30611.109 | 0 | 4752.664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191901.244 | 0 | 0
April | 431577000000 | 315751.567 | 26-APR-10:45 | 62886.42 | 41401.92 | 30611.109 | 0 | 4822.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176029.617 | 0 | 0
May | 472067000000 | 334358.153 | 24-MAY-10:45 | 62886.42 | 41401.92 | 30611.109 | 0 | 7341.984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192116.72 | 0 | 0
June | 493708000000 | 348102.403 | 28-JUN-10:45 | 62886.42 | 41401.92 | 30611.109 | 0 | 15342.342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197860.611 | 0 | 0
July | 554657000000 | 362606.19 | 19-JUL-10:45 | 62886.42 | 41401.92 | 30611.109 | 0 | 20366.039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207340.702 | 0 | 0
August | 544735000000 | 363041.201 | 30-AUG-10:45 | 62886.42 | 41401.92 | 30611.109 | 0 | 21457.366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206684.386 | 0 | 0
September | 470830000000 | 340866.935 | 09-SEP-10:45 | 62886.42 | 41401.92 | 30611.109 | 0 | 9865.374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196102.112 | 0 | 0
October | 452590000000 | 316525.848 | 05-OCT-10:45 | 62886.42 | 41401.92 | 30611.109 | 0 | 5797.421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175828.977 | 0 | 0
November | 420707000000 | 297088.229 | 16-NOV-11:15 | 62886.42 | 41401.92 | 30611.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162188.78 | 0 | 0
December | 431170000000 | 292391.654 | 30-DEC-11:15 | 62886.42 | 41401.92 | 30611.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157492.204 | 0 | 0
Annual Sum or Average | 5537000000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 391016000000 | 292391.654 |  | 41924.28 | 36859.929 | 30611.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157492.204 | 0 | 0
Maximum of Months | 554657000000 | 363041.201 |  | 62886.42 | 41401.92 | 30611.109 | 0 | 21457.366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207340.702 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 56989.49 | 20873.59 | 0 | 77863.08
Cost per Total Building Area ($/m2) | 13.63 | 4.99 | 0 | 18.62
Cost per Net Conditioned Building Area ($/m2) | 13.63 | 4.99 | 0 | 18.62

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 9874.42 | 2361.85 | 2361.85
Net Site Energy | 9874.42 | 2361.85 | 2361.85
Total Source Energy | 24302.85 | 5812.98 | 5812.98
Net Source Energy | 24302.85 | 5812.98 | 5812.98
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 3886.2 | 0 | 0 | 0 | 0
Cooling | 87.58 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.91 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 667.99 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 23.65 | 0 | 0 | 0 | 87.12
Refrigeration | 3227.53 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5765.45 | 4108.97 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 18.29 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 18.29 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 8.61 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 11.84 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 18.29 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 18.29 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 174.7 | 174.7 | 3.241 | 0.385 | 0.305 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13025.17 | 9224.05 | 3801.12 | 0.71 | 3.74
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 76967.07 | 52036.14 | 24930.93 | 0.68 | 3.11
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 48516.34 | 32801.08 | 15715.26 | 0.68 | 3.19
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 255380.92 | 172658.75 | 82722.16 | 0.68 | 3.27
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 83547.94 | 56485.36 | 27062.58 | 0.68 | 3.11
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 33686.58 | 26324.53 | 7362.05 | 0.78 | 3.68
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 16110.03 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 96638.94 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 151386.93 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 421891.97 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 133947.81 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 61678.82 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.59 | 688.05 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.1 | 3389.66 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.95 | 2136.68 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.59 | 1017.59 | 10.28 | 17692.49 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.36 | 3679.48 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.94 | 2121.42 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.72 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 138763.5053 | 213.317 | 285.1002 | 0 | 0.0022 | 187262.1292 | 56376.8019
February | 119520.1193 | 187.0609 | 256.3936 | 0 | 0.0019 | 168424.6672 | 48876.5379
March | 122771.5171 | 200.3309 | 290.0081 | 0 | 0.0022 | 190548.063 | 50988.1872
April | 111701.9504 | 190.193 | 289.6638 | 0 | 0.0021 | 190358.8084 | 47148.3806
May | 118740.2186 | 210.4438 | 334.8338 | 0 | 0.0025 | 220078.4109 | 50909.3784
June | 122786.4675 | 222.0028 | 360.5311 | 0 | 0.0026 | 236985.8429 | 53063.6064
July | 130393.5582 | 236.4511 | 385.1284 | 0 | 0.0028 | 253156.8239 | 56417.4719
August | 130990.5316 | 237.5218 | 386.8531 | 0 | 0.0028 | 254290.5069 | 56674.6355
September | 116222.4779 | 207.1718 | 331.6093 | 0 | 0.0024 | 217963.7049 | 49943.6687
October | 115263.8866 | 196.5163 | 299.7424 | 0 | 0.0022 | 196983.2754 | 48676.5543
November | 117578.6114 | 191.726 | 277.3135 | 0 | 0.0021 | 182206.5049 | 48818.9569
December | 133131.4799 | 207.7992 | 283.7536 | 0 | 0.0021 | 186394.5074 | 54388.7806
Annual Sum or Average | 1477860 | 2500.5347 | 3780.9307 | 0 | 0.028 | 2484650 | 622282.9602
Minimum of Months | 111701.9504 | 187.0609 | 256.3936 | 0 | 0.0019 | 168424.6672 | 47148.3806
Maximum of Months | 138763.5053 | 237.5218 | 386.8531 | 0 | 0.0028 | 254290.5069 | 56674.6355
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 434528000000 | 292561.002 | 30-JAN-11:15 | 62886.42 | 41401.92 | 29838.689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158433.973 | 0 | 0
February | 390817000000 | 292235.898 | 21-FEB-11:15 | 62886.42 | 41401.92 | 29838.689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158108.869 | 0 | 0
March | 442152000000 | 304426.467 | 23-MAR-17:15 | 41924.28 | 36859.929 | 29838.689 | 0 | 1972.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193830.769 | 0 | 0
April | 441713000000 | 326695.307 | 01-APR-17:15 | 34936.9 | 32317.938 | 29838.689 | 0 | 4788.936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224812.844 | 0 | 0
May | 510675000000 | 378110.326 | 27-MAY-17:15 | 34936.9 | 32317.938 | 29838.689 | 0 | 38761.719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242255.081 | 0 | 0
June | 549908000000 | 405952.601 | 29-JUN-17:15 | 41924.28 | 36859.929 | 29838.689 | 0 | 53824.421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243505.282 | 0 | 0
July | 587431000000 | 405745.738 | 13-JUL-17:15 | 41924.28 | 36859.929 | 29838.689 | 0 | 51332.808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245790.031 | 0 | 0
August | 590062000000 | 405269.565 | 25-AUG-17:15 | 41924.28 | 36859.929 | 29838.689 | 0 | 52794.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243852.662 | 0 | 0
September | 505768000000 | 357021.353 | 14-SEP-17:15 | 41924.28 | 36859.929 | 29838.689 | 0 | 15630.336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232768.119 | 0 | 0
October | 457085000000 | 321032.655 | 14-OCT-10:15 | 62886.42 | 41401.92 | 29838.689 | 0 | 2259.392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184646.234 | 0 | 0
November | 422796000000 | 308694.278 | 02-NOV-17:15 | 41924.28 | 36859.929 | 29838.689 | 0 | 1924.033 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 194142.347 | 0 | 0
December | 432514000000 | 296060.843 | 02-DEC-11:15 | 62886.42 | 41401.92 | 29838.689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161933.814 | 0 | 0
Annual Sum or Average | 5765450000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 390817000000 | 292235.898 |  | 34936.9 | 32317.938 | 29838.689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158108.869 | 0 | 0
Maximum of Months | 590062000000 | 405952.601 |  | 62886.42 | 41401.92 | 29838.689 | 0 | 53824.421 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 245790.031 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 89512.47 | 32280.79 | 0 | 121793.26
Cost per Total Building Area ($/m2) | 21.41 | 7.72 | 0 | 29.13
Cost per Net Conditioned Building Area ($/m2) | 21.41 | 7.72 | 0 | 29.13

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 9358.02 | 2238.33 | 2238.33
Net Site Energy | 9358.02 | 2238.33 | 2238.33
Total Source Energy | 23401.15 | 5597.3 | 5597.3
Net Source Energy | 23401.15 | 5597.3 | 5597.3
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 3605.59 | 0 | 0 | 0 | 0
Cooling | 32.77 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.83 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 780.33 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 23.85 | 0 | 0 | 0 | 87.12
Refrigeration | 2934.07 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5529.45 | 3828.57 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 18.29 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 18.29 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 8.61 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 11.84 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 18.29 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 18.29 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 174.7 | 174.7 | 3.241 | 0.385 | 0.305 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10938.02 | 8735.7 | 2202.31 | 0.8 | 4.04
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 57527.67 | 45944.78 | 11582.89 | 0.8 | 3.45
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 29795.53 | 23796.36 | 5999.17 | 0.8 | 3.73
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 235378.15 | 171841.83 | 63536.32 | 0.73 | 3.45
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 59178.17 | 47262.95 | 11915.21 | 0.8 | 4.32
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 31435.21 | 25105.9 | 6329.31 | 0.8 | 3.73
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 15838.31 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 94746.93 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 127090.38 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 407346.15 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 126834.92 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 54357.97 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.66 | 766.43 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.48 | 3800.62 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.8 | 1968.47 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 11.57 | 19597.07 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.57 | 6818.98 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.9 | 2076.8 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.72 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 139130.5285 | 217.2434 | 329.5679 | 0 | 0.0024 | 7814270 | 56945.2315
February | 122227.7148 | 193.3325 | 298.504 | 0 | 0.0021 | 7078190 | 50266.9072
March | 126867.9297 | 206.8425 | 332.1515 | 0 | 0.0023 | 7877160 | 52771.6767
April | 118318.2742 | 195.5909 | 319.4874 | 0 | 0.0022 | 7577280 | 49475.1742
May | 121298.9634 | 205.5135 | 345.6014 | 0 | 0.0024 | 8197440 | 51204.4225
June | 121661.3436 | 210.72 | 363.2426 | 0 | 0.0025 | 8616590 | 51801.322
July | 127260.9874 | 223.5361 | 391.2354 | 0 | 0.0027 | 9281080 | 54486.8922
August | 128507.2166 | 225.0168 | 392.5053 | 0 | 0.0027 | 9311100 | 54952.0055
September | 119205.2052 | 205.0443 | 350.7682 | 0 | 0.0024 | 8320470 | 50618.1249
October | 121395.2298 | 202.5327 | 334.5056 | 0 | 0.0023 | 7933770 | 50941.153
November | 122799.2413 | 198.8433 | 316.5605 | 0 | 0.0022 | 7507180 | 50947.2676
December | 136298.1232 | 214.2664 | 328.0863 | 0 | 0.0023 | 7779410 | 55925.6768
Annual Sum or Average | 1504970 | 2498.4823 | 4102.2164 | 0 | 0.0288 | 97293900 | 630335.8542
Minimum of Months | 118318.2742 | 193.3325 | 298.504 | 0 | 0.0021 | 7078190 | 49475.1742
Maximum of Months | 139130.5285 | 225.0168 | 392.5053 | 0 | 0.0027 | 9311100 | 56945.2315
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 444103000000 | 298548.404 | 23-JAN-11:15 | 62886.42 | 41401.92 | 35159.279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159100.784 | 0 | 0
February | 402270000000 | 306045.112 | 02-FEB-18:15 | 41924.28 | 36859.929 | 35159.279 | 0 | 0 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 188096.624 | 0 | 0
March | 447678000000 | 306562.827 | 30-MAR-17:15 | 41924.28 | 36859.929 | 35159.279 | 0 | 2091.567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190527.771 | 0 | 0
April | 430635000000 | 306378.162 | 24-APR-10:15 | 62886.42 | 41401.92 | 35159.279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166930.542 | 0 | 0
May | 465880000000 | 324521.498 | 25-MAY-17:15 | 41924.28 | 36859.929 | 35159.279 | 0 | 7087.233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203490.777 | 0 | 0
June | 489701000000 | 356220.138 | 30-JUN-10:45 | 62886.42 | 41401.92 | 35159.279 | 0 | 13103.677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203668.841 | 0 | 0
July | 527466000000 | 361949.841 | 21-JUL-17:15 | 41924.28 | 36859.929 | 35159.279 | 0 | 31390.525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216615.827 | 0 | 0
August | 529172000000 | 358066.192 | 11-AUG-17:15 | 41924.28 | 36859.929 | 35159.279 | 0 | 21082.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223039.973 | 0 | 0
September | 472872000000 | 343602.856 | 12-SEP-17:15 | 41924.28 | 36859.929 | 35159.279 | 0 | 10036.214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219623.154 | 0 | 0
October | 450895000000 | 318510.311 | 06-OCT-17:15 | 41924.28 | 36859.929 | 35159.279 | 0 | 5135.226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199431.597 | 0 | 0
November | 426651000000 | 299727.83 | 01-NOV-10:15 | 62886.42 | 41401.92 | 35159.279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160280.211 | 0 | 0
December | 442122000000 | 296779.152 | 29-DEC-11:15 | 62886.42 | 41401.92 | 35159.279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157331.532 | 0 | 0
Annual Sum or Average | 5529450000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 402270000000 | 296779.152 |  | 41924.28 | 36859.929 | 35159.279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157331.532 | 0 | 0
Maximum of Months | 529172000000 | 361949.841 |  | 62886.42 | 41401.92 | 35159.279 | 0 | 31390.525 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 223039.973 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 108146.24 | 31822.84 | 0 | 139969.08
Cost per Total Building Area ($/m2) | 25.87 | 7.61 | 0 | 33.48
Cost per Net Conditioned Building Area ($/m2) | 25.87 | 7.61 | 0 | 33.48

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 10570.5 | 2528.35 | 2528.35
Net Site Energy | 10570.5 | 2528.35 | 2528.35
Total Source Energy | 24457.85 | 5850.05 | 5850.05
Net Source Energy | 24457.85 | 5850.05 | 5850.05
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 4838.46 | 0 | 0 | 0 | 0
Cooling | 34.49 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.81 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 695.81 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 25.51 | 0 | 0 | 0 | 87.12
Refrigeration | 2994.84 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5507.4 | 5063.1 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 18.29 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 18.29 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 8.61 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 11.84 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 18.29 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 18.29 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 174.7 | 174.7 | 3.241 | 0.487 | 0.409 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 3.24 | 0.487 | 0.409
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 3.24 | 0.487 | 0.409
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12951.58 | 9341.76 | 3609.82 | 0.72 | 3.78
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 81066.91 | 54807.98 | 26258.93 | 0.68 | 3.11
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 29654.84 | 23091.16 | 6563.68 | 0.78 | 3.71
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 270910.79 | 183158.24 | 87752.55 | 0.68 | 3.26
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 83359.14 | 56357.72 | 27001.43 | 0.68 | 3.11
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 29123.75 | 23259.84 | 5863.91 | 0.8 | 3.77
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 16485.78 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 99955.13 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 134357.65 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 438752.35 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 136125.61 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 57054.82 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.62 | 716.53 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.26 | 3570.21 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.69 | 1929.84 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 10.91 | 18484.01 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.36 | 3671.16 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.76 | 2004.26 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.72 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 140147.7996 | 214.8568 | 286.0287 | 0 | 0.0022 | 187868.8495 | 56882.9785
February | 123649.9514 | 191.4295 | 258.4311 | 0 | 0.002 | 169752.3491 | 50365.134
March | 128126.3974 | 204.0887 | 286.4415 | 0 | 0.0022 | 188181.3813 | 52736.0952
April | 113923.1576 | 188.2671 | 276.8381 | 0 | 0.0021 | 181905.8873 | 47540.339
May | 114182.8935 | 195.5768 | 299.873 | 0 | 0.0022 | 197072.9731 | 48306.4026
June | 114122.5089 | 202.4247 | 322.3493 | 0 | 0.0024 | 211873.2899 | 48945.3159
July | 124487.7933 | 224.1707 | 362.5696 | 0 | 0.0026 | 238322.3766 | 53712.0489
August | 123174.3665 | 220.1313 | 353.2926 | 0 | 0.0026 | 232218.143 | 52985.3159
September | 114356.5393 | 198.8445 | 310.0008 | 0 | 0.0023 | 203741.3136 | 48663.786
October | 116287.2304 | 195.0711 | 292.0165 | 0 | 0.0022 | 191892.5226 | 48803.8003
November | 121758.0764 | 195.9194 | 278.634 | 0 | 0.0021 | 183061.8848 | 50303.6761
December | 136793.4129 | 211.665 | 285.5347 | 0 | 0.0022 | 187554.9168 | 55707.9715
Annual Sum or Average | 1471010 | 2442.4456 | 3612.0099 | 0 | 0.0269 | 2373450 | 614952.8638
Minimum of Months | 113923.1576 | 188.2671 | 258.4311 | 0 | 0.002 | 169752.3491 | 47540.339
Maximum of Months | 140147.7996 | 224.1707 | 362.5696 | 0 | 0.0026 | 238322.3766 | 56882.9785
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 435936000000 | 290109.782 | 13-JAN-11:15 | 62886.42 | 41401.92 | 30506.941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155314.501 | 0 | 0
February | 393898000000 | 294959.727 | 21-FEB-11:15 | 62886.42 | 41401.92 | 30506.941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160164.446 | 0 | 0
March | 436661000000 | 296262.959 | 30-MAR-10:15 | 62886.42 | 41401.92 | 30506.941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161467.678 | 0 | 0
April | 422099000000 | 303158.489 | 14-APR-10:15 | 62886.42 | 41401.92 | 30506.941 | 0 | 468.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167894.762 | 0 | 0
May | 457293000000 | 316643.33 | 27-MAY-10:45 | 62886.42 | 41401.92 | 30506.941 | 0 | 3599.043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178249.006 | 0 | 0
June | 491636000000 | 362770.542 | 14-JUN-17:15 | 41924.28 | 36859.929 | 30506.941 | 0 | 15427.195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 238052.197 | 0 | 0
July | 553009000000 | 388363.5 | 06-JUL-17:15 | 41924.28 | 36859.929 | 30506.941 | 0 | 38374.603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240697.747 | 0 | 0
August | 538845000000 | 366418.935 | 11-AUG-17:15 | 41924.28 | 36859.929 | 30506.941 | 0 | 18260.935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 238866.85 | 0 | 0
September | 472766000000 | 343713.133 | 08-SEP-17:15 | 41924.28 | 36859.929 | 30506.941 | 0 | 7185.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227236.893 | 0 | 0
October | 445272000000 | 312873.301 | 07-OCT-10:15 | 62886.42 | 41401.92 | 30506.941 | 0 | 2700.261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175377.759 | 0 | 0
November | 424781000000 | 313179.667 | 09-NOV-11:15 | 62886.42 | 41401.92 | 30506.941 | 0 | 1412.501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176971.885 | 0 | 0
December | 435207000000 | 293848.987 | 02-DEC-11:15 | 62886.42 | 41401.92 | 30506.941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159053.706 | 0 | 0
Annual Sum or Average | 5507400000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 393898000000 | 290109.782 |  | 41924.28 | 36859.929 | 30506.941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155314.501 | 0 | 0
Maximum of Months | 553009000000 | 388363.5 |  | 62886.42 | 41401.92 | 30506.941 | 0 | 38374.603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240697.747 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 85157.6 | 39889.68 | 0 | 125047.29
Cost per Total Building Area ($/m2) | 20.37 | 9.54 | 0 | 29.91
Cost per Net Conditioned Building Area ($/m2) | 20.37 | 9.54 | 0 | 29.91

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 12648.94 | 3025.49 | 3025.49
Net Site Energy | 12648.94 | 3025.49 | 3025.49
Total Source Energy | 27624.07 | 6607.37 | 6607.37
Net Source Energy | 27624.07 | 6607.37 | 6607.37
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 6852.92 | 0 | 0 | 0 | 0
Cooling | 16.12 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.44 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 941.66 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 27.77 | 0 | 0 | 0 | 87.12
Refrigeration | 2829.45 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5569.12 | 7079.82 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 18.29 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 18.29 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 8.61 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 11.84 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 18.29 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 18.29 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 174.7 | 174.7 | 2.615 | 0.702 | 0.633 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 2.61 | 0.702 | 0.633
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 2.61 | 0.702 | 0.633
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11893.99 | 9499.2 | 2394.79 | 0.8 | 4.04
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 63213.16 | 50485.53 | 12727.64 | 0.8 | 4.32
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 24106.61 | 19252.87 | 4853.74 | 0.8 | 3.77
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 198783.33 | 158759.36 | 40023.98 | 0.8 | 3.92
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 64723.93 | 51692.11 | 13031.82 | 0.8 | 4.32
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 27329.72 | 21827.02 | 5502.69 | 0.8 | 3.77
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 20174.29 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 123114.35 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 143029.3 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 535334.89 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 171072.74 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 61643.99 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.72 | 833.41 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.82 | 7283.92 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.46 | 1658.99 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 12.01 | 20345.91 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.91 | 7458 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.65 | 1880.8 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.72 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 152272.5338 | 169.3502 | 651.5671 | 0 | 0.0023 | 130710.1075 | 57491.051
February | 133713.2428 | 149.4677 | 588.0167 | 0 | 0.0021 | 117965.1738 | 50600.6113
March | 132506.8914 | 151.3696 | 650.7135 | 0 | 0.0023 | 130559.0877 | 50644.2879
April | 111529.0438 | 130.4538 | 611.4686 | 0 | 0.0021 | 122698.416 | 43095.6158
May | 103454.7747 | 124.844 | 647.4236 | 0 | 0.0022 | 129928.3173 | 40565.7451
June | 103248.8777 | 126.8848 | 694.0303 | 0 | 0.0024 | 139289.5063 | 40837.3071
July | 109100.4655 | 134.8378 | 749.3031 | 0 | 0.0025 | 150385.0131 | 43268.9843
August | 108969.5604 | 133.5417 | 724.6724 | 0 | 0.0025 | 145438.0673 | 43042.5081
September | 104743.7184 | 125.6398 | 639.5984 | 0 | 0.0022 | 128355.2906 | 40954.2634
October | 118752.144 | 138.3728 | 639.9881 | 0 | 0.0022 | 128419.1048 | 45805.16
November | 134337.9245 | 151.9568 | 628.2295 | 0 | 0.0022 | 126041.2765 | 51112.5885
December | 146663.6012 | 164.2622 | 651.6258 | 0 | 0.0023 | 130727.6961 | 55550.346
Annual Sum or Average | 1459290 | 1700.9812 | 7876.6371 | 0 | 0.0274 | 1580520 | 562968.4686
Minimum of Months | 103248.8777 | 124.844 | 588.0167 | 0 | 0.0021 | 117965.1738 | 40565.7451
Maximum of Months | 152272.5338 | 169.3502 | 749.3031 | 0 | 0.0025 | 150385.0131 | 57491.051
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 460571000000 | 301020.344 | 21-JAN-11:15 | 62886.42 | 41401.92 | 39591.947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157140.057 | 0 | 0
February | 415663000000 | 299049.268 | 27-FEB-11:15 | 62886.42 | 41401.92 | 39591.947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155168.98 | 0 | 0
March | 460039000000 | 302209.24 | 09-MAR-11:15 | 62886.42 | 41401.92 | 39591.947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158328.953 | 0 | 0
April | 432341000000 | 301603.858 | 14-APR-10:15 | 62886.42 | 41401.92 | 39591.947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157723.571 | 0 | 0
May | 457816000000 | 321189.12 | 31-MAY-10:15 | 62886.42 | 41401.92 | 39591.947 | 0 | 2177.063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175131.77 | 0 | 0
June | 490802000000 | 346261.242 | 21-JUN-17:15 | 41924.28 | 36859.929 | 39591.947 | 0 | 8808.314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219076.771 | 0 | 0
July | 529898000000 | 345873.378 | 11-JUL-17:15 | 41924.28 | 36859.929 | 39591.947 | 0 | 9623.386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 217873.835 | 0 | 0
August | 512467000000 | 343595.237 | 15-AUG-17:15 | 41924.28 | 36859.929 | 39591.947 | 0 | 9259.423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215959.658 | 0 | 0
September | 452274000000 | 316680.035 | 01-SEP-17:15 | 41924.28 | 36859.929 | 39591.947 | 0 | 1859.948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196443.931 | 0 | 0
October | 452499000000 | 308253.917 | 02-OCT-10:15 | 62886.42 | 41401.92 | 39591.947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164373.63 | 0 | 0
November | 444120000000 | 299348.842 | 14-NOV-11:15 | 62886.42 | 41401.92 | 39591.947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155468.555 | 0 | 0
December | 460633000000 | 303434.75 | 18-DEC-11:15 | 62886.42 | 41401.92 | 39591.947 | 0 | 0 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 155549.463 | 0 | 0
Annual Sum or Average | 5569120000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 415663000000 | 299049.268 |  | 41924.28 | 36859.929 | 39591.947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155168.98 | 0 | 0
Maximum of Months | 529898000000 | 346261.242 |  | 62886.42 | 41401.92 | 39591.947 | 0 | 9623.386 | 4005 | 0 | 0 | 0 | 0 | 0 | 0 | 219076.771 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 137984.43 | 29381.86 | 0 | 167366.29
Cost per Total Building Area ($/m2) | 33 | 7.03 | 0 | 40.03
Cost per Net Conditioned Building Area ($/m2) | 33 | 7.03 | 0 | 40.03

## Picture
DOE Commercial Building Benchmark - Super Market
Sales
Bakery
Deli
Produce
Office
DryStorage

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 112 | 5840
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 112 | 5840
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | 11.3 | 72.2 | 3764.71
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | 9.9
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 5.8
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0 | 0 | 7.6 | 49 | 2555
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | 7.6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 3.4
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | 13.9 | 91.6 | 4776.29
|  |  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15 | 12.3
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.15 | 0.15 | 9.8
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.22 | 0.64 | 0.74 | 0.68 | 0.68 | 0.71 | 0.72 | 0.72 | 0.73 | 0.68 | 0.68 | 0.58 | 0.54 | 0 | 0 | 0 | 8.44 | 52.69 | 2747.41
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.21 | 0.56 | 0.66 | 0.68 | 0.68 | 0.69 | 0.7 | 0.69 | 0.66 | 0.58 | 0.47 | 0.43 | 0.43 | 0.08 | 0 | 0 | 7.61
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.13 | 0.35 | 0.37 | 0.37 | 0.39 | 0.41 | 0.38 | 0.34 | 0.03 | 0 | 0 | 0 | 0 | 0 | 2.88
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0.23 | 0.13 | 0.08 | 6.62 | 44.59 | 2325.05
|  |  | Sat, WinterDesign | 0.11 | 0.1 | 0.08 | 0.06 | 0.06 | 0.06 | 0.07 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0.16 | 0.13 | 6.9
|  |  | Sun, Hol, Other | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07 | 0.1 | 0.12 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.1 | 0.06 | 4.59
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
INFIL_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8 | 56 | 2920
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16 | 115.5 | 6022.5
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19.5
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | WD, WinterDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8 | 3225.6 | 168192
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8
|  |  | Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624 | 4368 | 227760
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 112 | 5840
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
Deli Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Deli Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Deli Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Deli Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Deli_Case:1_ MULTIDECKDIARYANDDELICASE_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Deli_Case:1_ MULTIDECKDIARYANDDELICASE_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Deli_Case:1_ MULTIDECKDIARYANDDELICASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 595 | 31025
Deli_Case:1_ MULTIDECKDIARYANDDELICASE_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2 | 10.4 | 72.8 | 3796
Deli_Case:2_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Deli_Case:2_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Deli_Case:2_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Deli_Case:2_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Sales_Case:1_MEATDISPLAYCASE_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Sales_Case:1_MEATDISPLAYCASE_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Sales_Case:1_MEATDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 595 | 31025
Sales_Case:2_ MULTIDECKDIARYANDDELICASE_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Sales_Case:2_ MULTIDECKDIARYANDDELICASE_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Sales_Case:2_ MULTIDECKDIARYANDDELICASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 595 | 31025
Sales_Case:2_ MULTIDECKDIARYANDDELICASE_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2 | 10.4 | 72.8 | 3796
Sales_Case:3_GLASSDOORFROZENFOOD_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57 | 3.97 | 206.83
Sales_Case:3_GLASSDOORFROZENFOOD_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73 | 5.13 | 267.67
Sales_Case:3_GLASSDOORFROZENFOOD_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 595 | 31025
Sales_Case:3_GLASSDOORFROZENFOOD_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2 | 10.4 | 72.8 | 3796
Sales_Case:4_OPENWELLICECREAMDISPLAYCASE_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Sales_Case:4_OPENWELLICECREAMDISPLAYCASE_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Sales_Case:4_OPENWELLICECREAMDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 595 | 31025
Sales_Case:4_OPENWELLICECREAMDISPLAYCASE_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2 | 10.4 | 72.8 | 3796
Sales_Case:5_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Sales_Case:5_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Sales_Case:5_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Sales_Case:5_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Sales_Case:6_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Sales_Case:6_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Sales_Case:6_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Sales_Case:6_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Sales_Case:7_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Sales_Case:7_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Sales_Case:7_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Sales_Case:7_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Produce_Case:1_ MULTIDECKDIARYANDDELICASE_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Produce_Case:1_ MULTIDECKDIARYANDDELICASE_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Produce_Case:1_ MULTIDECKDIARYANDDELICASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 595 | 31025
Produce_Case:1_ MULTIDECKDIARYANDDELICASE_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2 | 10.4 | 72.8 | 3796
Bakery Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Bakery Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Bakery Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Bakery Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Bakery_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Bakery_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Bakery_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Bakery_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720