## BuildingSummary
Building Summary Warehouse new construction
|  | Value | Data Source
Program
| Building Name | Warehouse
| Available Fuel Types | gas, electricity
| Principal Building Activity | Nonrefrigerated warehouse
Form
| Total Floor Area (m2) | 4835.13 | Liu, B, R.E. Jarnagin, W. Jiang, and K. Gowri. (2007). Technical Support Document: The Development of the Advanced Energy Design Guide for Small Warehouse and Self-Storage Buildings. PNNL-17056. Richland, WA: Pacific Northwest National Laboratory
| Building Shape | Rectangle
| Aspect Ratio | 0.45
| Number of Floors | 1
Window Fraction (Window to Wall Ratio)
| South | 0.0286
| East | 0
| North | 0
| West | 0.0076
| Total | 0.0058
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | Bulk storage, fine storage, office
| Floor to Ceiling Height (m) | 8.53
| Floor to Floor Height (m) | 8.53
| Roof type | Metal building roof | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Metal building wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1977.67
| Net Dimensions - Total Area (m2) | 1324.84
| Wall to Skin Ratio | 0.35192
Roof
| Construction Type | Metal building roof | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 4598.25
| Net Dimensions - Total Area (m2) | 4598.25
| Roof to Skin Ratio | 0.64808
Window Dimensions (m2)
| South | 11.15
| East | 0
| North | 0
| West | 6.51
| Total Area (m2) | 17.66
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 8in slab-on-grade
| Dimensions - Total Area (m2) | 4598.25
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 539.71
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 9670.26
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.21 | See Benchmark Technical Report
HVAC
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | PACU | 2003 CBECS
| Fan Control | SZ CAV | 2003 CBECS
Service Water Heating
| SWH Type | n/a
| Fuel | n/a
| Thermal Efficiency (%) | n/a
| Temperature Setpoint (ºC ) | n/a
| Water Consumption (m3 ) | n/a

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Office | Yes | 1 | 236.88 | 1010.76 | 4.267 | 149.56 | 17.66 | 47.376 | 5 | 11.836 | 8.074 | 0 | 0 | 10 | 0 | 50 | 0 | 0.16104
FineStorage | Yes | 1 | 1393.41 | 10880.57 | 8.534 | 760.8 | 0 | 0 | 0 | 15.064 | 0 | 0 | 0 | 0 | 0.25 | 348.3525 | 0 | 0.21548
BulkStorage | Yes | 1 | 3204.84 | 27350.07 | 8.534 | 1586.63 | 0 | 0 | 0 | 9.684 | 2.559 | 0 | 0 | 0 | 0.25 | 801.21 | 0 | 0.19067
Total Conditioned Zones |  |  | 4835.13 | 39241.4 |  | 2496.99 | 17.66 |  | 5
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report
[5] Liu, B, R.E. Jarnagin, W. Jiang, and K. Gowri. (2007). Technical Support Document: The Development of the Advanced Energy Design Guide for Small Warehouse and Self-Storage Buildings. PNNL-17056. Richland, WA: Pacific Northwest National Laboratory

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 88.7974 | 658.6289 | 147.5727 | 754.1966 |  | 584.3224 | 39.0954 | 621.8326 | 17.2482 | 110.7246 | 910.1259 | 175.0078 | 118.4487 | 12.4546 | 10.9617 | 0.56144
Fabric | [6 empty] | weighting factor is for all of 3B
Exterior walls
| Construction Type | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall
| R-value (m2·K / W) | 0.2291 | 0.7657 | 0.7657 | 0.7657 | 0.7657 | 0.7657 | 0.7657 | 1.1223 | 1.1223 | 1.1223 | 1.2407 | 1.2407 | 1.3661 | 1.3661 | 1.3661 | 1.3661
Roof
| Construction Type | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof
| R-value (m2·K / W) | 0.18847 | 1.0515 | 1.0515 | 1.8116 | 1.8116 | 1.8116 | 1.8116 | 1.8116 | 1.8116 | 1.8116 | 1.8657 | 1.8657 | 1.8657 | 1.8657 | 1.8116 | 2.5
Window
| U-Factor (W / m2·K) | 5.838 | 5.838 | 5.838 | 5.838 | 5.838 | 5.838 | 5.838 | 5.838 | 5.838 | 5.838 | 5.838 | 5.838 | 5.838 | 5.838 | 5.838 | 5.838
| SHGC | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
| Visible transmittance | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade
| R-value (m2·K / W) | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809
HVAC
HVAC Sizing
Air Conditioning (kW)
| FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | 22.5778 | 18.1932 | 18.1448 | 16.8213 | 11.8945 | 15.8773 | 9.8335 | 16.4853 | 14.0405 | 11.9699 | 17.8424 | 17.1513 | 19.0023 | 19.0601 | 19.7521 | 22.864
| FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | 336.634 | 106.108 | 107.5871 | 75.9067 | 37.1255 | 64.3406 | 23.2586 | 68.667 | 54.1244 | 39.349 | 97.8141 | 83.0521 | 113.9462 | 89.2685 | 126.5153 | 104.8717
Heating (kW)
| BULKSTORAGE UNIT HEATER COIL | 39.3476 | 39.2032 | 37.8007 | 37.9092 | 39.2079 | 36.3558 | 39.3336 | 39.1382 | 32.3667 | 38.791 | 58.2948 | 47.3298 | 87.3617 | 87.797 | 107.9459 | 189.9027
| FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | 15.7484 | 16.3693 | 13.8179 | 19.5407 | 11.0789 | 16.5876 | 13.261 | 19.365 | 17.534 | 15.8335 | 23.8649 | 21.5268 | 25.9839 | 25.4914 | 27.468 | 35.0305
| FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | 82.7974 | 71.9193 | 51.988 | 81.2796 | 25.4964 | 61.4068 | 40.0886 | 92.3597 | 79.2506 | 65.9373 | 128.654 | 112.5083 | 148.4851 | 146.1691 | 160.779 | 208.1658
HVAC Efficiency
Air Conditioning (COP)
| FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | 3.68 | 3.85 | 3.95 | 3.91 | 4.02 | 4.01 | 4.04 | 3.88 | 4.04 | 4.04 | 3.87 | 4.01 | 3.9 | 4.01 | 3.71 | 3.77
| FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | 3.53 | 3.54 | 3.67 | 3.11 | 3.47 | 3.3 | 3.6 | 3.19 | 3.36 | 3.56 | 3.51 | 3.8 | 3.51 | 4.02 | 3.49 | 4.14
Heating Efficiency (%)
| BULKSTORAGE UNIT HEATER COIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.8 | 0.78 | 0.8 | 0.8 | 0.8 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
HVAC Control - Economizer
| FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| BULKSTORAGE UNIT HEATERFAN | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 1.42 | 1.67 | 1.94 | 3.58
| FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | 1.25 | 0.95 | 1.04 | 0.93 | 0.71 | 0.96 | 0.59 | 0.87 | 0.85 | 0.72 | 0.95 | 1.04 | 1.04 | 1.15 | 1.13 | 1.38
| FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | 17.78 | 4.39 | 5.04 | 3.09 | 1.57 | 3.17 | 1.18 | 2.77 | 2.91 | 1.98 | 3.94 | 4.15 | 4.59 | 5.1 | 5.09 | 6.34
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.097554 | 0.12278 | 0.11119 | 0.10332 | 0.13644 | 0.10304 | 0.15189 | 0.08207 | 0.037774 | 0.07844 | 0.053155 | 0.037719 | 0.065969 | 0.081067 | 0.064727 | 0.10542
| Total Cost ($/m2) | 9 | 6.77 | 6.47 | 4.96 | 6.11 | 5.15 | 6.71 | 3.88 | 1.78 | 3.53 | 2.68 | 1.9 | 3.39 | 4.17 | 3.35 | 5.75
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011415 | 0.0080583 | 0.0080569 | 0.0093742 | 0.0087402 | 0.007558 | 0.008788 | 0.0096302 | 0.0068235 | 0.0084772 | 0.00823 | 0.0068478 | 0.0079058 | 0.0079312 | 0.0078803 | 0.0041097
| Total Cost ($/m2) | 0.03 | 0.13 | 0.1 | 0.34 | 0.03 | 0.18 | 0.13 | 0.65 | 0.36 | 0.4 | 0.79 | 0.53 | 1.15 | 0.93 | 1.52 | 1.63
Total Utility Costs
| Cost Intensity ($/m2) | 9.04 | 6.9 | 6.56 | 5.3 | 6.13 | 5.33 | 6.84 | 4.53 | 2.14 | 3.92 | 3.47 | 2.43 | 4.54 | 5.11 | 4.87 | 7.38
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 129822.2222 | 26888.8889 | 35686.1111 | 10044.4444 | 1411.1111 | 18825 | 277.7778 | 6958.3333 | 5694.4444 | 338.8889 | 4588.8889 | 3072.2222 | 3591.6667 | 1422.2222 | 927.7778 | 127.7778
| Interior Lighting | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778
| Exterior Lighting | 25855.5556 | 25844.4444 | 25838.8889 | 25836.1111 | 25816.6667 | 25811.1111 | 25825 | 25808.3333 | 25816.6667 | 25766.6667 | 25811.1111 | 25797.2222 | 25794.4444 | 25788.8889 | 25775 | 25616.6667
| Interior Equipment | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 110188.8889 | 33483.3333 | 39344.4444 | 15819.4444 | 8716.6667 | 16794.4444 | 7066.6667 | 15163.8889 | 15588.8889 | 10980.5556 | 32555.5556 | 34177.7778 | 38577.7778 | 41161.1111 | 43397.2222 | 57669.4444
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 446275 | 266627.7778 | 281277.7778 | 232111.1111 | 216355.5556 | 241841.6667 | 213577.7778 | 228338.8889 | 227511.1111 | 217494.4444 | 243366.6667 | 243458.3333 | 248377.7778 | 248783.3333 | 250508.3333 | 263825
Gas (MJ)
| Heating | 13680 | 77020 | 57270 | 177670 | 14510 | 114040 | 74070 | 328350 | 257670 | 225920 | 465310 | 377050 | 705650 | 569580 | 930090 | 1920370
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 13680 | 77020 | 57270 | 177670 | 14510 | 114040 | 74070 | 328350 | 257670 | 225920 | 465310 | 377050 | 705650 | 569580 | 930090 | 1920370
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 1620280 | 1036880 | 1069870 | 1013270 | 793390 | 984670 | 842940 | 1150380 | 1076700 | 1008910 | 1341420 | 1253500 | 1599800 | 1465200 | 1831920 | 2870140
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 96.6592 | 20.0201 | 26.5701 | 7.4786 | 1.0506 | 14.0162 | 0.20682 | 5.1808 | 4.2398 | 0.25232 | 3.4167 | 2.2874 | 2.6742 | 1.0589 | 0.69078 | 0.095137
| Interior Lighting (elec) | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271
| Exterior Lighting (elec) | 19.2508 | 19.2425 | 19.2384 | 19.2363 | 19.2218 | 19.2177 | 19.228 | 19.2156 | 19.2218 | 19.1846 | 19.2177 | 19.2073 | 19.2053 | 19.2011 | 19.1908 | 19.0729
| Interior Equipment (elec) | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 82.0412 | 24.93 | 29.2939 | 11.7784 | 6.49 | 12.5043 | 5.2615 | 11.2903 | 11.6067 | 8.1756 | 24.2393 | 25.4471 | 28.7231 | 30.6465 | 32.3114 | 42.9378
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 332.2744 | 198.5179 | 209.4256 | 172.8185 | 161.0877 | 180.0634 | 159.0195 | 170.0099 | 169.3936 | 161.9357 | 181.1989 | 181.2671 | 184.9299 | 185.2318 | 186.5162 | 196.4311
Gas (MJ/m2)
| Heating (gas) | 2.8293 | 15.9293 | 11.8446 | 36.7457 | 3.001 | 23.5857 | 15.3191 | 67.9092 | 53.2912 | 46.7247 | 96.2353 | 77.9814 | 145.9423 | 117.8003 | 192.3609 | 397.1703
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 2.8293 | 15.9293 | 11.8446 | 36.7457 | 3.001 | 23.5857 | 15.3191 | 67.9092 | 53.2912 | 46.7247 | 96.2353 | 77.9814 | 145.9423 | 117.8003 | 192.3609 | 397.1703
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 335.1058 | 214.4472 | 221.2702 | 209.5642 | 164.0887 | 203.6491 | 174.3366 | 237.9212 | 222.6827 | 208.6624 | 277.432 | 259.2485 | 330.8701 | 303.0322 | 378.8771 | 593.6014
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 142.8535 | 75.6964 | 70.3129 | 63.4905 | 67.0365 | 68.981 | 66.4597 | 68.4634 | 62.6783 | 67.4273 | 73.0226 | 73.5262 | 74.3631 | 75.2973 | 75.2651 | 78.1411
| Feb | 150.2767 | 79.8258 | 75.4472 | 63.3688 | 62.1099 | 63.7662 | 61.1774 | 62.5484 | 63.2695 | 61.5123 | 73.0226 | 67.6112 | 68.4481 | 69.3823 | 69.4556 | 78.1411
| Mar | 155.4261 | 77.5806 | 86.4447 | 64.1594 | 62.1768 | 64.1294 | 60.5447 | 63.3699 | 63.2962 | 61.9031 | 67.4505 | 68.2977 | 68.4481 | 69.9239 | 69.3501 | 72.2261
| Apr | 164.3722 | 85.5769 | 89.4282 | 71.444 | 62.4392 | 76.6569 | 61.2988 | 63.7072 | 65.6085 | 61.6099 | 67.8265 | 69.8087 | 68.9791 | 69.5186 | 69.3501 | 71.9683
| May | 176.1426 | 96.6757 | 98.5506 | 80.2888 | 62.2939 | 83.4389 | 61.3898 | 70.1906 | 73.1814 | 62.522 | 76.2609 | 75.2074 | 77.1474 | 70.4011 | 70.3171 | 72.6332
| Jun | 177.0762 | 98.2431 | 106.7621 | 86.2901 | 64.1492 | 88.3574 | 62.0451 | 85.3436 | 80.546 | 65.9097 | 88.4579 | 81.451 | 89.7948 | 84.174 | 79.0854 | 75.1626
| Jul | 182.7289 | 100.591 | 106.6993 | 91.8558 | 69.0969 | 88.2134 | 66.9565 | 88.3217 | 81.0654 | 70.2138 | 90.6754 | 85.2674 | 87.5069 | 84.1616 | 86.6041 | 75.625
| Aug | 182.8415 | 99.4311 | 106.6805 | 86.8983 | 71.6556 | 88.218 | 61.7174 | 87.6105 | 81.5356 | 67.8255 | 88.4053 | 85.4023 | 87.4492 | 80.3536 | 81.9738 | 73.4288
| Sep | 176.5013 | 96.1433 | 102.2554 | 82.3748 | 70.9752 | 87.3599 | 69.1257 | 77.9113 | 72.3076 | 65.8481 | 80.0022 | 77.1088 | 77.7938 | 74.3433 | 70.889 | 71.9683
| Oct | 165.0825 | 89.0958 | 88.5405 | 68.9801 | 65.5328 | 75.2576 | 61.5346 | 67.5088 | 64.0706 | 62.1335 | 68.3971 | 70.6958 | 69.207 | 70.2722 | 69.4059 | 77.8833
| Nov | 146.0596 | 79.2588 | 80.298 | 63.9105 | 67.4993 | 69.3626 | 66.4597 | 68.4634 | 68.5933 | 67.4273 | 73.0226 | 73.5262 | 74.3631 | 75.2973 | 75.2651 | 78.1411
| Dec | 139.7728 | 74.566 | 70.1915 | 63.2456 | 67.4033 | 69.0781 | 66.4597 | 68.4634 | 68.5933 | 67.4273 | 73.0226 | 73.5262 | 74.3631 | 75.2973 | 75.2651 | 78.1411
Time of Peak Electrical Demand
| Jan | 25-JAN-13:30 | 03-JAN-13:00 | 26-JAN-15:39 | 23-JAN-15:00 | 02-JAN-16:00 | 02-JAN-16:40 | 02-JAN-16:00 | 02-JAN-16:49 | 02-JAN-09:09 | 02-JAN-16:30 | 02-JAN-16:30 | 02-JAN-16:49 | 02-JAN-16:40 | 02-JAN-16:49 | 02-JAN-16:30 | 02-JAN-09:09
| Feb | 24-FEB-13:09 | 23-FEB-14:00 | 28-FEB-15:39 | 27-FEB-15:00 | 13-FEB-11:00 | 27-FEB-15:20 | 15-FEB-15:00 | 01-FEB-09:09 | 14-FEB-15:00 | 01-FEB-09:09 | 01-FEB-16:00 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09
| Mar | 27-MAR-13:30 | 28-MAR-14:00 | 17-MAR-14:00 | 28-MAR-14:00 | 31-MAR-14:39 | 31-MAR-14:50 | 01-MAR-09:09 | 09-MAR-15:00 | 02-MAR-15:00 | 29-MAR-14:00 | 31-MAR-15:50 | 30-MAR-14:00 | 01-MAR-09:09 | 28-MAR-15:39 | 01-MAR-09:09 | 13-MAR-08:09
| Apr | 04-APR-13:30 | 17-APR-14:00 | 26-APR-14:50 | 14-APR-15:00 | 11-APR-15:00 | 21-APR-14:00 | 13-APR-14:00 | 04-APR-14:00 | 21-APR-15:00 | 18-APR-15:00 | 07-APR-14:00 | 25-APR-14:00 | 14-APR-15:00 | 06-APR-15:00 | 03-APR-08:09 | 03-APR-08:09
| May | 24-MAY-12:39 | 26-MAY-14:00 | 30-MAY-14:00 | 15-MAY-14:00 | 30-MAY-14:30 | 31-MAY-15:00 | 17-MAY-13:00 | 15-MAY-14:20 | 31-MAY-15:00 | 04-MAY-14:00 | 05-MAY-13:00 | 23-MAY-15:00 | 31-MAY-12:39 | 16-MAY-15:00 | 31-MAY-15:00 | 24-MAY-14:00
| Jun | 20-JUN-13:09 | 13-JUN-14:00 | 28-JUN-15:00 | 19-JUN-14:00 | 30-JUN-14:00 | 27-JUN-15:00 | 16-JUN-14:00 | 30-JUN-14:00 | 29-JUN-15:30 | 28-JUN-14:00 | 08-JUN-12:00 | 28-JUN-13:00 | 29-JUN-14:00 | 30-JUN-14:00 | 14-JUN-15:00 | 20-JUN-15:00
| Jul | 10-JUL-13:30 | 31-JUL-14:39 | 11-JUL-15:00 | 03-JUL-14:00 | 10-JUL-15:00 | 25-JUL-15:00 | 03-JUL-13:09 | 25-JUL-12:00 | 31-JUL-14:00 | 24-JUL-14:00 | 13-JUL-14:00 | 17-JUL-15:39 | 13-JUL-15:39 | 21-JUL-15:00 | 06-JUL-15:30 | 21-JUL-15:00
| Aug | 18-AUG-12:00 | 28-AUG-13:00 | 01-AUG-15:00 | 17-AUG-13:00 | 08-AUG-13:30 | 04-AUG-15:09 | 15-AUG-12:39 | 04-AUG-14:00 | 01-AUG-14:39 | 07-AUG-15:30 | 04-AUG-14:00 | 30-AUG-13:00 | 25-AUG-15:30 | 09-AUG-15:00 | 11-AUG-14:00 | 15-AUG-14:39
| Sep | 06-SEP-12:30 | 15-SEP-13:00 | 08-SEP-14:20 | 11-SEP-13:00 | 25-SEP-12:00 | 01-SEP-14:00 | 28-SEP-14:00 | 08-SEP-14:00 | 01-SEP-14:00 | 01-SEP-15:00 | 05-SEP-14:20 | 06-SEP-14:00 | 14-SEP-14:00 | 01-SEP-15:00 | 07-SEP-14:00 | 01-SEP-08:09
| Oct | 06-OCT-13:30 | 13-OCT-12:39 | 02-OCT-14:50 | 12-OCT-15:00 | 05-OCT-12:00 | 03-OCT-14:00 | 13-OCT-14:00 | 03-OCT-14:00 | 13-OCT-14:00 | 17-OCT-14:00 | 31-OCT-13:30 | 05-OCT-15:39 | 06-OCT-14:00 | 06-OCT-15:00 | 06-OCT-14:00 | 23-OCT-08:09
| Nov | 07-NOV-13:00 | 03-NOV-12:00 | 13-NOV-14:50 | 22-NOV-14:00 | 20-NOV-16:49 | 09-NOV-16:40 | 10-NOV-16:00 | 06-NOV-16:00 | 13-NOV-16:00 | 06-NOV-16:49 | 06-NOV-16:40 | 06-NOV-16:49 | 06-NOV-16:00 | 08-NOV-16:00 | 06-NOV-16:49 | 01-NOV-08:09
| Dec | 14-DEC-13:09 | 19-DEC-15:20 | 11-DEC-15:39 | 01-DEC-15:30 | 18-DEC-16:49 | 05-DEC-16:30 | 01-DEC-16:49 | 01-DEC-16:40 | 01-DEC-16:00 | 01-DEC-16:19 | 01-DEC-16:19 | 01-DEC-16:40 | 01-DEC-16:30 | 01-DEC-16:40 | 01-DEC-16:19 | 07-DEC-14:39
Source Energy
| Total Source Energy (GJ) | 5344.01 | 3570.31 | 3265.4 | 3004.99 | 2426.48 | 3238.76 | 2460.55 | 3298.12 | 2998.94 | 1610.67 | 3614.83 | 3319.8 | 3843.78 | 3735.15 | 4115.24 | 5489.62
| Total Source Energy (MJ/m2) | 1105.25 | 738.41 | 675.35 | 621.49 | 501.84 | 669.84 | 508.89 | 682.12 | 620.24 | 333.12 | 747.62 | 686.6 | 794.97 | 772.5 | 851.11 | 1135.36
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emissions
| Carbon Equivalent (kg) | 122637.6889 | 90325.2065 | 85943.9147 | 74702.9305 | 25546.2673 | 83623.2541 | 26295.4563 | 67539.8938 | 97583.9609 | 19915.1409 | 138141.2174 | 106251.3625 | 97742.3123 | 101185.5202 | 102519.1242 | 108866.5125
| CO2 (kg) | 284115.7215 | 227179.5045 | 202669.2377 | 171530.8566 | 68261.6191 | 199133.462 | 70497.431 | 155289.4076 | 229977.8894 | 49400.918 | 323612.0197 | 251377.4666 | 232763.1846 | 241130.2831 | 246138.4185 | 286016.2687
| NOX (kg) | 500.4579 | 296.9753 | 340.2098 | 321.7553 | 58.456 | 322.215 | 60.531 | 291.8135 | 392.1391 | 71.1483 | 567.1297 | 424.419 | 391.0395 | 402.2942 | 404.7246 | 323.8122
| SO2 (kg) | 1910.241 | 1271.8299 | 1131.0942 | 814.7615 | 629.5743 | 1330.3472 | 621.5016 | 833.621 | 993.5617 | 168.1673 | 1640.218 | 1063.2328 | 586.3978 | 664.4319 | 591.4882 | 1343.4912
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0087 | 0.0036 | 0.0031 | 0.003 | 0.0003 | 0.0025 | 0.0003 | 0.0034 | 0.0039 | 0.0007 | 0.005 | 0.0042 | 0.0044 | 0.0047 | 0.0044 | 0.0048
| Water for Electricity (m3) | 236.418 | 433.8329 | 8355.22 | 1449.22 | 3798.73 | 6634.65 | 3749.92 | 51.8418 | 1033.08 | 2222.11 | 377.568 | 1105.49 | 385.3416 | 15758.9 | 388.6481 | 269.5451

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1620.28 | 335.11 | 335.11
Net Site Energy | 1620.28 | 335.11 | 335.11
Total Source Energy | 5344.01 | 1105.25 | 1105.25
Net Source Energy | 5344.01 | 1105.25 | 1105.25
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 13.68 | 0 | 0 | 0 | 0
Cooling | 467.36 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 545.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 93.08 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 396.68 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1606.59 | 13.68 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 9.68 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 15.06 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 11.84 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 4.365 | 12.593 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 4.365 | 12.593 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 4.365 | 12.593 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 5.306 | 30004 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 4.365 | 12.593 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 4.365 | 12.593 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 4.365 | 12.593 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 4.365 | 12.593 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 4.365 | 12.593 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 5.306 | 30004 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 4.365 | 12.593 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 4.365 | 12.593 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 4.365 | 12.593 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 4.365 | 12.593 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-90.1-2004-SEMI-OPER | 5.58 | 5.58 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-90.1-2004-SEMI-OPER | 5.58 | 5.58 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-90.1-2004-SEMI-OPER | 3.25 | 3.25 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-90.1-2004-SEMI-OPER | 3.25 | 3.25 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 5.84 | 0.7 | 0.603
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 5.84 | 0.7 | 0.603
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 22577.83 | 17340.31 | 5237.52 | 0.77 | 3.68
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 336634.02 | 253319.23 | 83314.79 | 0.75 | 3.53
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 39347.64 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15748.39 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 82797.39 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.25 | 1424.32 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.6 | 1017.59 | 17.78 | 29935.94 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 20434.5674 | 35.6861 | 134.9629 | 0 | 0.0006 | 16703.2365 | 8789.6066
February | 18974.5606 | 33.3679 | 127.1418 | 0 | 0.0006 | 15735.4698 | 8184.8006
March | 22809.0363 | 40.1365 | 153.0357 | 0 | 0.0007 | 18940.191 | 9841.3776
April | 23624.6173 | 41.6607 | 159.2084 | 0 | 0.0007 | 19704.2126 | 10202.1946
May | 26532.8629 | 46.7935 | 178.8411 | 0 | 0.0008 | 22134.0331 | 11458.5389
June | 27110.8739 | 47.8129 | 182.7371 | 0 | 0.0008 | 22616.2169 | 11708.1599
July | 27656.9909 | 48.776 | 186.4182 | 0 | 0.0008 | 23071.7942 | 11944.0072
August | 28741.0063 | 50.6878 | 193.7248 | 0 | 0.0009 | 23976.0929 | 12412.1524
September | 24693.882 | 43.5503 | 166.4457 | 0 | 0.0008 | 20599.9332 | 10664.3526
October | 23665.0433 | 41.7352 | 159.5066 | 0 | 0.0007 | 19741.1256 | 10219.9809
November | 20600.1938 | 36.327 | 138.8241 | 0 | 0.0006 | 17181.381 | 8896.079
December | 19272.0866 | 33.924 | 129.3945 | 0 | 0.0006 | 16014.2932 | 8316.4385
Annual Sum or Average | 284115.7215 | 500.4579 | 1910.241 | 0 | 0.0087 | 236417.9799 | 122637.6889
Minimum of Months | 18974.5606 | 33.3679 | 127.1418 | 0 | 0.0006 | 15735.4698 | 8184.8006
Maximum of Months | 28741.0063 | 50.6878 | 193.7248 | 0 | 0.0009 | 23976.0929 | 12412.1524
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 113508000000 | 142853.535 | 25-JAN-13:30 | 49331.021 | 9104.397 | 31360.268 | 0 | 53057.848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 106931000000 | 150276.68 | 24-FEB-13:09 | 49331.021 | 9104.397 | 31360.268 | 0 | 60480.994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 128709000000 | 155426.121 | 27-MAR-13:30 | 49331.021 | 9104.397 | 31360.268 | 0 | 65630.435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 133901000000 | 164372.151 | 04-APR-13:30 | 49331.021 | 9104.397 | 31360.268 | 0 | 74576.464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 150413000000 | 176142.602 | 24-MAY-12:39 | 49331.021 | 9104.397 | 31360.268 | 0 | 86346.916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 153690000000 | 177076.192 | 20-JUN-13:09 | 49331.021 | 9104.397 | 31360.268 | 0 | 87280.506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 156786000000 | 182728.925 | 10-JUL-13:30 | 49331.021 | 9104.397 | 31360.268 | 0 | 92933.239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 162931000000 | 182841.522 | 18-AUG-12:00 | 49331.021 | 9104.397 | 31360.268 | 0 | 93045.836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 139988000000 | 176501.276 | 06-SEP-12:30 | 49331.021 | 9104.397 | 31360.268 | 0 | 86705.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 134152000000 | 165082.486 | 06-OCT-13:30 | 49331.021 | 9104.397 | 31360.268 | 0 | 75286.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 116757000000 | 146059.577 | 07-NOV-13:00 | 49331.021 | 9104.397 | 31360.268 | 0 | 56263.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 108826000000 | 139772.814 | 14-DEC-13:09 | 49331.021 | 9104.397 | 31360.268 | 0 | 49977.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1606590000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 106931000000 | 139772.814 |  | 49331.021 | 9104.397 | 31360.268 | 0 | 49977.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 162931000000 | 182841.522 |  | 49331.021 | 9104.397 | 31360.268 | 0 | 93045.836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 43535.75 | 156.16 | 0 | 43691.9
Cost per Total Building Area ($/m2) | 9 | 0.03 | 0 | 9.04
Cost per Net Conditioned Building Area ($/m2) | 9 | 0.03 | 0 | 9.04

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1036.88 | 214.45 | 214.45
Net Site Energy | 1036.88 | 214.45 | 214.45
Total Source Energy | 3570.31 | 738.41 | 738.41
Net Source Energy | 3570.31 | 738.41 | 738.41
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 77.02 | 0 | 0 | 0 | 0
Cooling | 96.8 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 545.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 93.04 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 120.54 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 959.86 | 77.02 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 9.68 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 15.06 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 11.84 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.951 | 1.159 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.951 | 1.159 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-90.1-2004-SEMI-OPER | 5.58 | 5.58 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-90.1-2004-SEMI-OPER | 5.58 | 5.58 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-90.1-2004-SEMI-OPER | 3.25 | 3.25 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-90.1-2004-SEMI-OPER | 3.25 | 3.25 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 5.84 | 0.7 | 0.603
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 5.84 | 0.7 | 0.603
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18193.24 | 13621.67 | 4571.57 | 0.75 | 3.85
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 106107.95 | 72464.13 | 33643.82 | 0.68 | 3.54
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 39203.23 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 16369.34 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 71919.25 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.95 | 1081.99 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 4.39 | 8378.03 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 18756.1541 | 24.0631 | 98.6247 | 0 | 0.0003 | 33639.7819 | 7398.6274
February | 16597.9048 | 21.3995 | 88.7506 | 0 | 0.0003 | 30272.3316 | 6560.8466
March | 18139.9088 | 23.747 | 102.0294 | 0 | 0.0003 | 34803.3119 | 7216.6984
April | 16976.948 | 22.3088 | 96.6686 | 0 | 0.0003 | 32975.0562 | 6764.8949
May | 19607.9148 | 25.7721 | 111.7345 | 0 | 0.0003 | 38114.2874 | 7814.0517
June | 21293.1227 | 27.9879 | 121.3479 | 0 | 0.0003 | 41393.5558 | 8485.7276
July | 21407.0971 | 28.1377 | 121.9974 | 0 | 0.0003 | 41615.1206 | 8531.1487
August | 22272.7793 | 29.2755 | 126.9309 | 0 | 0.0004 | 43297.9955 | 8876.14
September | 18984.6634 | 24.9536 | 108.1922 | 0 | 0.0003 | 36905.9406 | 7565.7613
October | 18107.1095 | 23.7964 | 103.1384 | 0 | 0.0003 | 35182.0121 | 7215.5543
November | 17036.1335 | 22.3345 | 96.2756 | 0 | 0.0003 | 32840.7816 | 6781.7605
December | 17999.7687 | 23.1993 | 96.1397 | 0 | 0.0003 | 32792.6966 | 7113.9952
Annual Sum or Average | 227179.5045 | 296.9753 | 1271.8299 | 0 | 0.0036 | 433832.8715 | 90325.2065
Minimum of Months | 16597.9048 | 21.3995 | 88.7506 | 0 | 0.0003 | 30272.3316 | 6560.8466
Maximum of Months | 22272.7793 | 29.2755 | 126.9309 | 0 | 0.0004 | 43297.9955 | 8876.14
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 74428100000 | 75696.392 | 03-JAN-13:00 | 49331.021 | 9104.397 | 9534.423 | 0 | 7726.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 66977600000 | 79825.761 | 23-FEB-14:00 | 49331.021 | 9104.397 | 9534.423 | 0 | 11855.919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 77002400000 | 77580.555 | 28-MAR-14:00 | 49331.021 | 9104.397 | 9534.423 | 0 | 9610.713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 72957400000 | 85576.937 | 17-APR-14:00 | 49331.021 | 9104.397 | 9534.423 | 0 | 17607.095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 84327900000 | 96675.711 | 26-MAY-14:00 | 49331.021 | 9104.397 | 9534.423 | 0 | 28705.869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 91583300000 | 98243.147 | 13-JUN-14:00 | 49331.021 | 9104.397 | 9534.423 | 0 | 30273.305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 92073500000 | 100590.997 | 31-JUL-14:39 | 49331.021 | 9104.397 | 9534.423 | 0 | 32621.155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 95796900000 | 99431.081 | 28-AUG-13:00 | 49331.021 | 9104.397 | 9534.423 | 0 | 31461.239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 81654500000 | 96143.258 | 15-SEP-13:00 | 49331.021 | 9104.397 | 9534.423 | 0 | 28173.416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 77840300000 | 89095.796 | 13-OCT-12:39 | 49331.021 | 9104.397 | 9534.423 | 0 | 21125.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 72660300000 | 79258.762 | 03-NOV-12:00 | 49331.021 | 9104.397 | 9534.423 | 0 | 11288.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 72553900000 | 74566.006 | 19-DEC-15:20 | 49331.021 | 9104.397 | 9534.423 | 0 | 6596.164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 959856000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 66977600000 | 74566.006 |  | 49331.021 | 9104.397 | 9534.423 | 0 | 6596.164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 95796900000 | 100590.997 |  | 49331.021 | 9104.397 | 9534.423 | 0 | 32621.155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 32736.95 | 620.65 | 0 | 33357.61
Cost per Total Building Area ($/m2) | 6.77 | 0.13 | 0 | 6.9
Cost per Net Conditioned Building Area ($/m2) | 6.77 | 0.13 | 0 | 6.9

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1069.87 | 221.27 | 221.27
Net Site Energy | 1069.87 | 221.27 | 221.27
Total Source Energy | 3265.4 | 675.35 | 675.35
Net Source Energy | 3265.4 | 675.35 | 675.35
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 57.27 | 0 | 0 | 0 | 0
Cooling | 128.47 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 545.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 93.02 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 141.64 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1012.6 | 57.27 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 9.68 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 15.06 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 11.84 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.951 | 1.159 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.951 | 1.159 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-90.1-2004-SEMI-OPER | 5.58 | 5.58 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-90.1-2004-SEMI-OPER | 5.58 | 5.58 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-90.1-2004-SEMI-OPER | 3.25 | 3.25 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-90.1-2004-SEMI-OPER | 3.25 | 3.25 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 5.84 | 0.7 | 0.603
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 5.84 | 0.7 | 0.603
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18144.82 | 14138.33 | 4006.49 | 0.78 | 3.95
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 107587.13 | 77013.55 | 30573.58 | 0.72 | 3.67
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 37800.65 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13817.88 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 51988 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.04 | 1182.6 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 5.04 | 9445.76 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 15700.3952 | 25.8695 | 84.1085 | 0 | 0.0002 | 621272.8848 | 6608.7721
February | 14085.3707 | 23.2423 | 75.7022 | 0 | 0.0002 | 559180.8559 | 5932.3915
March | 15743.6192 | 26.5102 | 88.46 | 0 | 0.0002 | 653444.4227 | 6684.5569
April | 15046.9379 | 25.4188 | 85.1366 | 0 | 0.0002 | 628898.8424 | 6397.017
May | 17473.0397 | 29.5314 | 98.9665 | 0 | 0.0003 | 731060.1802 | 7429.8815
June | 20152.1765 | 34.0604 | 114.148 | 0 | 0.0003 | 843205.284 | 8569.2014
July | 20249.1183 | 34.2243 | 114.6971 | 0 | 0.0003 | 847261.5132 | 8610.4234
August | 20655.9868 | 34.912 | 117.0017 | 0 | 0.0003 | 864285.6641 | 8783.4339
September | 17537.7319 | 29.6416 | 99.339 | 0 | 0.0003 | 733811.9635 | 7457.4752
October | 15560.4793 | 26.2935 | 88.0942 | 0 | 0.0002 | 650746.9522 | 6616.0691
November | 14588.885 | 24.5879 | 82.1314 | 0 | 0.0002 | 606697.3899 | 6196.5024
December | 15875.4972 | 25.9178 | 83.3091 | 0 | 0.0002 | 615355.4514 | 6658.1903
Annual Sum or Average | 202669.2377 | 340.2098 | 1131.0942 | 0 | 0.0031 | 8355220 | 85943.9147
Minimum of Months | 14085.3707 | 23.2423 | 75.7022 | 0 | 0.0002 | 559180.8559 | 5932.3915
Maximum of Months | 20655.9868 | 34.912 | 117.0017 | 0 | 0.0003 | 864285.6641 | 8783.4339
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 75294700000 | 70312.879 | 26-JAN-15:39 | 49331.021 | 9104.397 | 10702.769 | 0 | 1174.692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 67769500000 | 75447.236 | 28-FEB-15:39 | 49331.021 | 9104.397 | 10702.769 | 0 | 6309.049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 79193700000 | 86444.695 | 17-MAR-14:00 | 49331.021 | 9104.397 | 10702.769 | 0 | 17306.508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 76218900000 | 89428.157 | 26-APR-14:50 | 49331.021 | 9104.397 | 10702.769 | 0 | 20289.969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 88600200000 | 98550.571 | 30-MAY-14:00 | 49331.021 | 9104.397 | 10702.769 | 0 | 29412.384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 102192000000 | 106762.059 | 28-JUN-15:00 | 49331.021 | 9104.397 | 10628.363 | 0 | 37698.278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 102683000000 | 106699.297 | 11-JUL-15:00 | 49331.021 | 9104.397 | 10702.769 | 0 | 37561.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 104746000000 | 106680.457 | 01-AUG-15:00 | 49331.021 | 9104.397 | 10628.363 | 0 | 37616.676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 88933700000 | 102255.437 | 08-SEP-14:20 | 49331.021 | 9104.397 | 10702.769 | 0 | 33117.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 78866700000 | 88540.491 | 02-OCT-14:50 | 49331.021 | 9104.397 | 10702.769 | 0 | 19402.304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 73528200000 | 80298.036 | 13-NOV-14:50 | 49331.021 | 9104.397 | 10702.769 | 0 | 11159.849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 74577500000 | 70191.521 | 11-DEC-15:39 | 49331.021 | 9104.397 | 10702.769 | 0 | 1053.334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1012600000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 67769500000 | 70191.521 |  | 49331.021 | 9104.397 | 10628.363 | 0 | 1053.334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 104746000000 | 106762.059 |  | 49331.021 | 9104.397 | 10702.769 | 0 | 37698.278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 31276.55 | 461.42 | 0 | 31737.97
Cost per Total Building Area ($/m2) | 6.47 | 0.1 | 0 | 6.56
Cost per Net Conditioned Building Area ($/m2) | 6.47 | 0.1 | 0 | 6.56

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1013.27 | 209.56 | 209.56
Net Site Energy | 1013.27 | 209.56 | 209.56
Total Source Energy | 3004.99 | 621.49 | 621.49
Net Source Energy | 3004.99 | 621.49 | 621.49
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 177.67 | 0 | 0 | 0 | 0
Cooling | 36.16 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 545.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 93.01 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 56.95 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 835.6 | 177.67 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 9.68 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 15.06 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 11.84 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.552 | 0.616 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.552 | 0.616 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-90.1-2004-SEMI-OPER | 5.58 | 5.58 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-90.1-2004-SEMI-OPER | 5.58 | 5.58 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-90.1-2004-SEMI-OPER | 3.25 | 3.25 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-90.1-2004-SEMI-OPER | 3.25 | 3.25 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 5.84 | 0.7 | 0.603
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 5.84 | 0.7 | 0.603
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16821.31 | 12898.62 | 3922.69 | 0.77 | 3.91
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 75906.66 | 51517.22 | 24389.44 | 0.68 | 3.11
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 37909.17 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 19540.67 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 81279.63 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.93 | 1057.33 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 3.09 | 3378.53 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 16427.2281 | 28.6601 | 67.4697 | 0 | 0.0003 | 119987.9546 | 6955.2563
February | 14282.8732 | 25.2582 | 60.3258 | 0 | 0.0002 | 107286.9825 | 6078.6779
March | 14364.4604 | 27.1161 | 69.0708 | 0 | 0.0003 | 122857.7902 | 6271.6603
April | 12700.657 | 24.2818 | 62.5728 | 0 | 0.0002 | 111302.5648 | 5573.5314
May | 13674.5592 | 26.4005 | 68.6298 | 0 | 0.0003 | 122078.9432 | 6024.6331
June | 14512.0588 | 28.0228 | 72.8592 | 0 | 0.0003 | 129602.1754 | 6394.1042
July | 14545.4606 | 28.0873 | 73.0269 | 0 | 0.0003 | 129900.4758 | 6408.8213
August | 15336.8466 | 29.6154 | 77.0001 | 0 | 0.0003 | 136968.0695 | 6757.5109
September | 13355.8937 | 25.7901 | 67.0539 | 0 | 0.0002 | 119275.6973 | 5884.6782
October | 13180.6319 | 25.3757 | 65.8016 | 0 | 0.0002 | 117047.4721 | 5800.4418
November | 13838.7244 | 25.873 | 65.3142 | 0 | 0.0002 | 116173.4554 | 6018.9717
December | 15311.4627 | 27.2743 | 65.6366 | 0 | 0.0002 | 116734.0615 | 6534.6434
Annual Sum or Average | 171530.8566 | 321.7553 | 814.7615 | 0 | 0.003 | 1449220 | 74702.9305
Minimum of Months | 12700.657 | 24.2818 | 60.3258 | 0 | 0.0002 | 107286.9825 | 5573.5314
Maximum of Months | 16427.2281 | 29.6154 | 77.0001 | 0 | 0.0003 | 136968.0695 | 6955.2563
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 69183900000 | 63490.537 | 23-JAN-15:00 | 49331.021 | 9104.397 | 4510.267 | 0 | 544.851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 61860700000 | 63368.827 | 27-FEB-15:00 | 49331.021 | 9104.397 | 4510.267 | 0 | 423.142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 70838600000 | 64159.394 | 28-MAR-14:00 | 49331.021 | 9104.397 | 4510.267 | 0 | 1213.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 64176000000 | 71444.048 | 14-APR-15:00 | 49331.021 | 9104.397 | 4510.267 | 0 | 8498.363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 70389600000 | 80288.84 | 15-MAY-14:00 | 49331.021 | 9104.397 | 4510.267 | 0 | 17343.154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 74727400000 | 86290.11 | 19-JUN-14:00 | 49331.021 | 9104.397 | 4510.267 | 0 | 23344.425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 74899400000 | 91855.792 | 03-JUL-14:00 | 49331.021 | 9104.397 | 4510.267 | 0 | 28910.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 78974500000 | 86898.308 | 17-AUG-13:00 | 49331.021 | 9104.397 | 4510.267 | 0 | 23952.622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 68773200000 | 82374.761 | 11-SEP-13:00 | 49331.021 | 9104.397 | 4510.267 | 0 | 19429.075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 67488500000 | 68980.067 | 12-OCT-15:00 | 49331.021 | 9104.397 | 4510.267 | 0 | 6034.382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 66984500000 | 63910.531 | 22-NOV-14:00 | 49331.021 | 9104.397 | 4510.267 | 0 | 964.845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 67307800000 | 63245.615 | 01-DEC-15:30 | 49331.021 | 9104.397 | 4510.267 | 0 | 299.929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 835604000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 61860700000 | 63245.615 |  | 49331.021 | 9104.397 | 4510.267 | 0 | 299.929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 78974500000 | 91855.792 |  | 49331.021 | 9104.397 | 4510.267 | 0 | 28910.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 23981.86 | 1665.52 | 0 | 25647.39
Cost per Total Building Area ($/m2) | 4.96 | 0.34 | 0 | 5.3
Cost per Net Conditioned Building Area ($/m2) | 4.96 | 0.34 | 0 | 5.3

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 793.39 | 164.09 | 164.09
Net Site Energy | 793.39 | 164.09 | 164.09
Total Source Energy | 2426.48 | 501.84 | 501.84
Net Source Energy | 2426.48 | 501.84 | 501.84
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 14.51 | 0 | 0 | 0 | 0
Cooling | 5.08 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 545.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.94 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 31.38 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 778.88 | 14.51 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 9.68 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 15.06 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 11.84 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.552 | 0.616 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.552 | 0.616 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-90.1-2004-SEMI-OPER | 5.58 | 5.58 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-90.1-2004-SEMI-OPER | 5.58 | 5.58 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-90.1-2004-SEMI-OPER | 3.25 | 3.25 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-90.1-2004-SEMI-OPER | 3.25 | 3.25 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 5.84 | 0.7 | 0.603
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 5.84 | 0.7 | 0.603
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 11894.47 | 9456.74 | 2437.73 | 0.8 | 4.02
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 37125.54 | 25544.91 | 11580.62 | 0.69 | 3.47
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 39207.88 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11078.89 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 25496.42 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.71 | 825.28 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.57 | 1786.44 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 5940.8701 | 5.094 | 53.6261 | 0 | 0 | 323565.5372 | 2219.7562
February | 5289.8224 | 4.5336 | 48.1346 | 0 | 0 | 290432.5218 | 1977.6731
March | 6073.5462 | 5.2033 | 55.6234 | 0 | 0 | 335619.4936 | 2271.7694
April | 5432.5714 | 4.6521 | 50.1172 | 0 | 0 | 302397.4919 | 2033.1277
May | 5728.8841 | 4.9041 | 53.1691 | 0 | 0 | 320813.3074 | 2144.9933
June | 5625.3542 | 4.8146 | 52.3706 | 0 | 0 | 315995.5913 | 2106.7251
July | 5446.1668 | 4.6607 | 50.7903 | 0 | 0 | 306460.6373 | 2039.8866
August | 6012.6085 | 5.1454 | 56.0745 | 0 | 0 | 338344.9475 | 2252.0551
September | 5496.1367 | 4.7035 | 51.2538 | 0 | 0 | 309257.5182 | 2058.5956
October | 5723.6275 | 4.8987 | 53.2848 | 0 | 0 | 321511.7473 | 2143.5269
November | 5699.9527 | 4.8805 | 52.6826 | 0 | 0 | 317876.882 | 2133.4957
December | 5792.0785 | 4.9655 | 52.4472 | 0 | 0 | 316452.9521 | 2164.6625
Annual Sum or Average | 68261.6191 | 58.456 | 629.5743 | 0 | 0.0003 | 3798730 | 25546.2673
Minimum of Months | 5289.8224 | 4.5336 | 48.1346 | 0 | 0 | 290432.5218 | 1977.6731
Maximum of Months | 6073.5462 | 5.2033 | 56.0745 | 0 | 0 | 338344.9475 | 2271.7694
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 66343100000 | 67036.541 | 02-JAN-16:00 | 49331.021 | 9104.397 | 2686.122 | 0 | 0 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 59549600000 | 62109.949 | 13-FEB-11:00 | 49331.021 | 9104.397 | 2686.122 | 0 | 988.408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 68814600000 | 62176.835 | 31-MAR-14:39 | 49331.021 | 9104.397 | 2686.122 | 0 | 1055.295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 62002800000 | 62439.213 | 11-APR-15:00 | 49331.021 | 9104.397 | 2686.122 | 0 | 1317.672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 65778800000 | 62293.949 | 30-MAY-14:30 | 49331.021 | 9104.397 | 2686.122 | 0 | 1172.409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 64791000000 | 64149.18 | 30-JUN-14:00 | 49331.021 | 9104.397 | 2686.122 | 0 | 3027.639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 62835900000 | 69096.885 | 10-JUL-15:00 | 49331.021 | 9104.397 | 2686.122 | 0 | 7975.345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 69373400000 | 71655.608 | 08-AUG-13:30 | 49331.021 | 9104.397 | 2686.122 | 0 | 10534.067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 63409400000 | 70975.223 | 25-SEP-12:00 | 49331.021 | 9104.397 | 2686.122 | 0 | 9853.682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 65922000000 | 65532.788 | 05-OCT-12:00 | 49331.021 | 9104.397 | 2686.122 | 0 | 4411.247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 65176700000 | 67499.256 | 20-NOV-16:49 | 49331.021 | 9104.397 | 2686.122 | 0 | 462.716 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 64884700000 | 67403.284 | 18-DEC-16:49 | 49331.021 | 9104.397 | 2686.122 | 0 | 366.743 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 778882000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 59549600000 | 62109.949 |  | 49331.021 | 9104.397 | 2686.122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 69373400000 | 71655.608 |  | 49331.021 | 9104.397 | 2686.122 | 0 | 10534.067 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 29520.32 | 126.82 | 0 | 29647.14
Cost per Total Building Area ($/m2) | 6.11 | 0.03 | 0 | 6.13
Cost per Net Conditioned Building Area ($/m2) | 6.11 | 0.03 | 0 | 6.13

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 984.67 | 203.65 | 203.65
Net Site Energy | 984.67 | 203.65 | 203.65
Total Source Energy | 3238.76 | 669.84 | 669.84
Net Source Energy | 3238.76 | 669.84 | 669.84
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 114.04 | 0 | 0 | 0 | 0
Cooling | 67.77 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 545.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.92 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 60.46 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 870.63 | 114.04 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 9.68 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 15.06 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 11.84 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.552 | 0.616 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.552 | 0.616 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-90.1-2004-SEMI-OPER | 5.58 | 5.58 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-90.1-2004-SEMI-OPER | 5.58 | 5.58 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-90.1-2004-SEMI-OPER | 3.25 | 3.25 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-90.1-2004-SEMI-OPER | 3.25 | 3.25 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 5.84 | 0.7 | 0.603
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 5.84 | 0.7 | 0.603
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15877.33 | 12680.51 | 3196.82 | 0.8 | 4.01
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 64340.64 | 47005.42 | 17335.23 | 0.73 | 3.3
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 36355.77 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 16587.63 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 61406.84 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.96 | 1092.66 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 3.17 | 3463.56 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 17646.666 | 27.3138 | 106.2366 | 0 | 0.0002 | 529774.1552 | 7281.5824
February | 14365.1237 | 23.0548 | 94.1904 | 0 | 0.0002 | 469735.863 | 6012.7631
March | 16496.4627 | 26.537 | 108.7438 | 0 | 0.0002 | 542317.0958 | 6911.2671
April | 14427.4224 | 23.633 | 99.0936 | 0 | 0.0002 | 494206.2433 | 6088.5422
May | 16083.7496 | 26.3698 | 110.6924 | 0 | 0.0002 | 552053.1584 | 6789.9911
June | 18299.9344 | 30.0104 | 126.0118 | 0 | 0.0002 | 628455.5642 | 7726.3279
July | 18619.9673 | 30.5354 | 128.2168 | 0 | 0.0002 | 639452.3885 | 7861.4614
August | 19464.8254 | 31.9209 | 134.0345 | 0 | 0.0003 | 668466.7539 | 8218.1655
September | 16243.129 | 26.6376 | 111.8499 | 0 | 0.0002 | 557825.9751 | 6857.9453
October | 15288.1139 | 25.0519 | 105.0903 | 0 | 0.0002 | 524113.5977 | 6452.705
November | 15358.1784 | 24.8511 | 102.6057 | 0 | 0.0002 | 511711.1674 | 6449.4768
December | 16839.8893 | 26.2993 | 103.5813 | 0 | 0.0002 | 516542.0668 | 6973.026
Annual Sum or Average | 199133.462 | 322.215 | 1330.3472 | 0 | 0.0025 | 6634650 | 83623.2541
Minimum of Months | 14365.1237 | 23.0548 | 94.1904 | 0 | 0.0002 | 469735.863 | 6012.7631
Maximum of Months | 19464.8254 | 31.9209 | 134.0345 | 0 | 0.0003 | 668466.7539 | 8218.1655
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 69519100000 | 68981.04 | 02-JAN-16:40 | 49331.021 | 9104.397 | 4630.621 | 0 | 0 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 61640600000 | 63766.17 | 27-FEB-15:20 | 49331.021 | 9104.397 | 4630.621 | 0 | 700.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 71165000000 | 64129.372 | 31-MAR-14:50 | 49331.021 | 9104.397 | 4630.621 | 0 | 1063.332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 64851700000 | 76656.884 | 21-APR-14:00 | 49331.021 | 9104.397 | 4630.621 | 0 | 13590.844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 72442600000 | 83438.85 | 31-MAY-15:00 | 49331.021 | 9104.397 | 4630.621 | 0 | 20372.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 82468500000 | 88357.442 | 27-JUN-15:00 | 49331.021 | 9104.397 | 4630.621 | 0 | 25291.403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 83911500000 | 88213.352 | 25-JUL-15:00 | 49331.021 | 9104.397 | 4630.621 | 0 | 25147.313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 87718900000 | 88218.009 | 04-AUG-15:09 | 49331.021 | 9104.397 | 4630.621 | 0 | 25151.969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 73200200000 | 87359.879 | 01-SEP-14:00 | 49331.021 | 9104.397 | 4630.621 | 0 | 24293.839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 68776300000 | 75257.634 | 03-OCT-14:00 | 49331.021 | 9104.397 | 4630.621 | 0 | 12191.594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 67148800000 | 69362.621 | 09-NOV-16:40 | 49331.021 | 9104.397 | 4630.621 | 0 | 381.581 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 67782700000 | 69078.091 | 05-DEC-16:30 | 49331.021 | 9104.397 | 4630.621 | 0 | 97.051 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 870626000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 61640600000 | 63766.17 |  | 49331.021 | 9104.397 | 4630.621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 87718900000 | 88357.442 |  | 49331.021 | 9104.397 | 4630.621 | 0 | 25291.403 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 24920.48 | 861.92 | 0 | 25782.4
Cost per Total Building Area ($/m2) | 5.15 | 0.18 | 0 | 5.33
Cost per Net Conditioned Building Area ($/m2) | 5.15 | 0.18 | 0 | 5.33

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 842.94 | 174.34 | 174.34
Net Site Energy | 842.94 | 174.34 | 174.34
Total Source Energy | 2460.55 | 508.89 | 508.89
Net Source Energy | 2460.55 | 508.89 | 508.89
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 74.07 | 0 | 0 | 0 | 0
Cooling | 1 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 545.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.97 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 25.44 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 768.88 | 74.07 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 9.68 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 15.06 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 11.84 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.552 | 0.616 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.552 | 0.616 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-90.1-2004-SEMI-OPER | 5.58 | 5.58 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-90.1-2004-SEMI-OPER | 5.58 | 5.58 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-90.1-2004-SEMI-OPER | 3.25 | 3.25 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-90.1-2004-SEMI-OPER | 3.25 | 3.25 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 5.84 | 0.7 | 0.603
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 5.84 | 0.7 | 0.603
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 9833.54 | 7853.61 | 1979.93 | 0.8 | 4.04
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 23258.62 | 17214.32 | 6044.31 | 0.74 | 3.6
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 39333.64 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13260.98 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 40088.55 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.59 | 689.04 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.18 | 1345.82 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 6992.8323 | 6.0495 | 53.556 | 0 | 0 | 323109.4754 | 2583.6282
February | 5446.5206 | 4.6776 | 47.8153 | 0 | 0 | 288500.1444 | 2030.9326
March | 6371.7413 | 5.4766 | 55.1589 | 0 | 0 | 332805.9171 | 2373.558
April | 5535.3932 | 4.7486 | 49.5637 | 0 | 0 | 299052.5937 | 2067.0257
May | 5735.1234 | 4.9137 | 52.4566 | 0 | 0 | 316511.3349 | 2144.9788
June | 5606.1424 | 4.8014 | 51.597 | 0 | 0 | 311325.6554 | 2097.7156
July | 5380.3547 | 4.6071 | 49.69 | 0 | 0 | 299820.1022 | 2013.7521
August | 5885.7297 | 5.0402 | 54.2931 | 0 | 0 | 327594.1812 | 2202.7071
September | 5432.2844 | 4.6514 | 50.1973 | 0 | 0 | 302881.2277 | 2033.2728
October | 5725.4579 | 4.9042 | 52.5939 | 0 | 0 | 317340.3492 | 2142.0524
November | 5862.5972 | 5.0305 | 52.271 | 0 | 0 | 315386.6901 | 2188.5313
December | 6523.254 | 5.6301 | 52.309 | 0 | 0 | 315595.6205 | 2417.3017
Annual Sum or Average | 70497.431 | 60.531 | 621.5016 | 0 | 0.0003 | 3749920 | 26295.4563
Minimum of Months | 5380.3547 | 4.6071 | 47.8153 | 0 | 0 | 288500.1444 | 2013.7521
Maximum of Months | 6992.8323 | 6.0495 | 55.1589 | 0 | 0 | 332805.9171 | 2583.6282
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 66249600000 | 66459.676 | 02-JAN-16:00 | 49331.021 | 9104.397 | 2109.258 | 0 | 0 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 59153400000 | 61177.432 | 15-FEB-15:00 | 49331.021 | 9104.397 | 2109.258 | 0 | 632.756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 68237700000 | 60544.676 | 01-MAR-09:09 | 49331.021 | 9104.397 | 2109.258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 61317000000 | 61298.796 | 13-APR-14:00 | 49331.021 | 9104.397 | 2109.258 | 0 | 754.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 64896700000 | 61389.776 | 17-MAY-13:00 | 49331.021 | 9104.397 | 2109.258 | 0 | 845.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 63833500000 | 62045.051 | 16-JUN-14:00 | 49331.021 | 9104.397 | 2109.258 | 0 | 1500.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 61474400000 | 66956.516 | 03-JUL-13:09 | 49331.021 | 9104.397 | 2109.258 | 0 | 6411.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 67169100000 | 61717.393 | 15-AUG-12:39 | 49331.021 | 9104.397 | 2109.258 | 0 | 1172.717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 62102000000 | 69125.702 | 28-SEP-14:00 | 49331.021 | 9104.397 | 2109.258 | 0 | 8581.025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 65066700000 | 61534.588 | 13-OCT-14:00 | 49331.021 | 9104.397 | 2109.258 | 0 | 989.912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 64666100000 | 66459.676 | 10-NOV-16:00 | 49331.021 | 9104.397 | 2109.258 | 0 | 0 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 64709000000 | 66459.676 | 01-DEC-16:49 | 49331.021 | 9104.397 | 2109.258 | 0 | 0 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 768875000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 59153400000 | 60544.676 |  | 49331.021 | 9104.397 | 2109.258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 68237700000 | 69125.702 |  | 49331.021 | 9104.397 | 2109.258 | 0 | 8581.025 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 32440.12 | 650.93 | 0 | 33091.05
Cost per Total Building Area ($/m2) | 6.71 | 0.13 | 0 | 6.84
Cost per Net Conditioned Building Area ($/m2) | 6.71 | 0.13 | 0 | 6.84

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1150.38 | 237.92 | 237.92
Net Site Energy | 1150.38 | 237.92 | 237.92
Total Source Energy | 3298.12 | 682.12 | 682.12
Net Source Energy | 3298.12 | 682.12 | 682.12
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 328.35 | 0 | 0 | 0 | 0
Cooling | 25.05 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 545.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.91 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 54.59 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 822.02 | 328.35 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 9.68 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 15.06 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 11.84 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.891 | 1.028 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.891 | 1.028 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.891 | 1.028 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.552 | 0.616 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.891 | 1.028 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.891 | 1.028 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.891 | 1.028 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.891 | 1.028 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.891 | 1.028 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.552 | 0.616 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.891 | 1.028 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.891 | 1.028 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.891 | 1.028 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.891 | 1.028 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-90.1-2004-SEMI-OPER | 5.58 | 5.58 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-90.1-2004-SEMI-OPER | 5.58 | 5.58 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-90.1-2004-SEMI-OPER | 3.25 | 3.25 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-90.1-2004-SEMI-OPER | 3.25 | 3.25 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 5.84 | 0.7 | 0.603
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 5.84 | 0.7 | 0.603
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16485.28 | 12427.94 | 4057.34 | 0.75 | 3.88
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 68666.96 | 46424.58 | 22242.38 | 0.68 | 3.19
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 39138.15 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 19364.98 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 92359.7 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.87 | 1014.45 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.77 | 3024.12 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 17029.5523 | 28.2745 | 70.8401 | 0 | 0.0003 | 4404.2289 | 7065.8857
February | 14229.4427 | 24.3484 | 63.1842 | 0 | 0.0003 | 3928.5545 | 5970.175
March | 13635.5335 | 25.3687 | 71.7921 | 0 | 0.0003 | 4464.5747 | 5907.2106
April | 11064.6351 | 21.6563 | 64.168 | 0 | 0.0003 | 3990.8077 | 4891.3413
May | 11336.6093 | 22.6049 | 68.0437 | 0 | 0.0003 | 4231.9773 | 5049.6349
June | 12074.9286 | 24.1417 | 72.8323 | 0 | 0.0003 | 4529.8239 | 5384.4165
July | 12052.6047 | 24.098 | 72.7028 | 0 | 0.0003 | 4521.7702 | 5374.5472
August | 13011.1079 | 26.0144 | 78.4841 | 0 | 0.0003 | 4881.3412 | 5801.9589
September | 11019.0643 | 22.0226 | 66.4189 | 0 | 0.0003 | 4130.9414 | 4912.8484
October | 11725.4017 | 22.9881 | 68.2127 | 0 | 0.0003 | 4242.3758 | 5186.969
November | 12667.291 | 23.8149 | 68.0614 | 0 | 0.0003 | 4232.6546 | 5510.3871
December | 15443.2365 | 26.4809 | 68.8806 | 0 | 0.0003 | 4282.7579 | 6484.5192
Annual Sum or Average | 155289.4076 | 291.8135 | 833.621 | 0 | 0.0034 | 51841.8082 | 67539.8938
Minimum of Months | 11019.0643 | 21.6563 | 63.1842 | 0 | 0.0003 | 3928.5545 | 4891.3413
Maximum of Months | 17029.5523 | 28.2745 | 78.4841 | 0 | 0.0003 | 4881.3412 | 7065.8857
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 69835200000 | 68463.389 | 02-JAN-16:49 | 49331.021 | 9104.397 | 4112.971 | 0 | 0 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 62292700000 | 62548.389 | 01-FEB-09:09 | 49331.021 | 9104.397 | 4112.971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 70792100000 | 63369.886 | 09-MAR-15:00 | 49331.021 | 9104.397 | 4112.971 | 0 | 821.497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 63279900000 | 63707.187 | 04-APR-14:00 | 49331.021 | 9104.397 | 4112.971 | 0 | 1158.797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 67103900000 | 70190.614 | 15-MAY-14:20 | 49331.021 | 9104.397 | 4112.971 | 0 | 7642.225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 71826700000 | 85343.559 | 30-JUN-14:00 | 49331.021 | 9104.397 | 4112.971 | 0 | 22795.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 71699000000 | 88321.693 | 25-JUL-12:00 | 49331.021 | 9104.397 | 4112.971 | 0 | 25773.303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 77400500000 | 87610.518 | 04-AUG-14:00 | 49331.021 | 9104.397 | 4112.971 | 0 | 25062.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 65501900000 | 77911.252 | 08-SEP-14:00 | 49331.021 | 9104.397 | 4112.971 | 0 | 15362.863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 67268800000 | 67508.759 | 03-OCT-14:00 | 49331.021 | 9104.397 | 4112.971 | 0 | 4960.369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 67114700000 | 68463.389 | 06-NOV-16:00 | 49331.021 | 9104.397 | 4112.971 | 0 | 0 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 67909100000 | 68463.389 | 01-DEC-16:40 | 49331.021 | 9104.397 | 4112.971 | 0 | 0 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 822025000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 62292700000 | 62548.389 |  | 49331.021 | 9104.397 | 4112.971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 77400500000 | 88321.693 |  | 49331.021 | 9104.397 | 4112.971 | 0 | 25773.303 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 18739.72 | 3162.08 | 0 | 21901.8
Cost per Total Building Area ($/m2) | 3.88 | 0.65 | 0 | 4.53
Cost per Net Conditioned Building Area ($/m2) | 3.88 | 0.65 | 0 | 4.53

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1076.7 | 222.68 | 222.68
Net Site Energy | 1076.7 | 222.68 | 222.68
Total Source Energy | 2998.94 | 620.24 | 620.24
Net Source Energy | 2998.94 | 620.24 | 620.24
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 257.67 | 0 | 0 | 0 | 0
Cooling | 20.5 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 545.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.94 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 56.12 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 819.04 | 257.67 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 9.68 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 15.06 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 11.84 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.891 | 1.028 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.891 | 1.028 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.891 | 1.028 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.552 | 0.616 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.891 | 1.028 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.891 | 1.028 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.891 | 1.028 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.891 | 1.028 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.891 | 1.028 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.552 | 0.616 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.891 | 1.028 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.891 | 1.028 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.891 | 1.028 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.891 | 1.028 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-90.1-2004-SEMI-OPER | 5.58 | 5.58 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-90.1-2004-SEMI-OPER | 5.58 | 5.58 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-90.1-2004-SEMI-OPER | 3.25 | 3.25 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-90.1-2004-SEMI-OPER | 3.25 | 3.25 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 5.84 | 0.7 | 0.603
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 5.84 | 0.7 | 0.603
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14040.54 | 11213.55 | 2826.99 | 0.8 | 4.04
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 54124.43 | 41050.1 | 13074.32 | 0.76 | 3.36
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 32366.69 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 17534 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 79250.59 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.85 | 983.82 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.91 | 3184.65 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 21789.6185 | 35.3106 | 84.1598 | 0 | 0.0003 | 87494.8074 | 9064.9409
February | 18581.5468 | 30.7228 | 75.0759 | 0 | 0.0003 | 78055.4445 | 7790.244
March | 20341.3996 | 34.3528 | 86.0846 | 0 | 0.0003 | 89506.256 | 8598.7039
April | 17161.4284 | 29.802 | 77.0632 | 0 | 0.0003 | 80131.923 | 7334.8652
May | 18117.8034 | 31.761 | 82.9715 | 0 | 0.0003 | 86277.3672 | 7772.8677
June | 18748.7572 | 32.8944 | 86.0088 | 0 | 0.0003 | 89435.859 | 8046.2372
July | 18818.5306 | 33.0178 | 86.3346 | 0 | 0.0003 | 89774.7113 | 8076.286
August | 19765.7648 | 34.6797 | 90.6799 | 0 | 0.0004 | 94293.0668 | 8482.7991
September | 17346.4693 | 30.4329 | 79.5693 | 0 | 0.0003 | 82739.7785 | 7444.3106
October | 18126.839 | 31.4994 | 81.5113 | 0 | 0.0003 | 84757.3018 | 7749.5327
November | 19529.7418 | 32.791 | 81.6159 | 0 | 0.0003 | 84858.6294 | 8236.8657
December | 21649.99 | 34.8748 | 82.4869 | 0 | 0.0003 | 85754.0104 | 8986.3079
Annual Sum or Average | 229977.8894 | 392.1391 | 993.5617 | 0 | 0.0039 | 1033080 | 97583.9609
Minimum of Months | 17161.4284 | 29.802 | 75.0759 | 0 | 0.0003 | 78055.4445 | 7334.8652
Maximum of Months | 21789.6185 | 35.3106 | 90.6799 | 0 | 0.0004 | 94293.0668 | 9064.9409
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 69366900000 | 62678.292 | 02-JAN-09:09 | 49331.021 | 9104.397 | 4242.873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 61883300000 | 63269.477 | 14-FEB-15:00 | 49331.021 | 9104.397 | 4242.873 | 0 | 591.185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 70961600000 | 63296.165 | 02-MAR-15:00 | 49331.021 | 9104.397 | 4242.873 | 0 | 617.873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 63529600000 | 65608.508 | 21-APR-15:00 | 49331.021 | 9104.397 | 4242.873 | 0 | 2930.216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 68401700000 | 73181.388 | 31-MAY-15:00 | 49331.021 | 9104.397 | 4242.873 | 0 | 10503.096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 70905800000 | 80546.021 | 29-JUN-15:30 | 49331.021 | 9104.397 | 4242.873 | 0 | 17867.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 71174500000 | 81065.434 | 31-JUL-14:00 | 49331.021 | 9104.397 | 4242.873 | 0 | 18387.142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 74756700000 | 81535.593 | 01-AUG-14:39 | 49331.021 | 9104.397 | 4242.873 | 0 | 18857.301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 65597100000 | 72307.635 | 01-SEP-14:00 | 49331.021 | 9104.397 | 4242.873 | 0 | 9629.343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 67196600000 | 64070.593 | 13-OCT-14:00 | 49331.021 | 9104.397 | 4242.873 | 0 | 1392.301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 67276900000 | 68593.292 | 13-NOV-16:00 | 49331.021 | 9104.397 | 4242.873 | 0 | 0 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 67986800000 | 68593.292 | 01-DEC-16:00 | 49331.021 | 9104.397 | 4242.873 | 0 | 0 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 819038000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 61883300000 | 62678.292 |  | 49331.021 | 9104.397 | 4242.873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 74756700000 | 81535.593 |  | 49331.021 | 9104.397 | 4242.873 | 0 | 18857.301 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 8594.05 | 1758.22 | 0 | 10352.27
Cost per Total Building Area ($/m2) | 1.78 | 0.36 | 0 | 2.14
Cost per Net Conditioned Building Area ($/m2) | 1.78 | 0.36 | 0 | 2.14

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1008.91 | 208.66 | 208.66
Net Site Energy | 1008.91 | 208.66 | 208.66
Total Source Energy | 1610.67 | 333.12 | 333.12
Net Source Energy | 1610.67 | 333.12 | 333.12
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 225.92 | 0 | 0 | 0 | 0
Cooling | 1.22 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 545.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.76 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 39.53 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 782.98 | 225.92 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 9.68 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 15.06 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 11.84 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.891 | 1.028 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.891 | 1.028 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.891 | 1.028 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.552 | 0.616 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.891 | 1.028 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.891 | 1.028 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.891 | 1.028 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.891 | 1.028 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.891 | 1.028 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.552 | 0.616 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.891 | 1.028 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.891 | 1.028 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.891 | 1.028 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.891 | 1.028 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-90.1-2004-SEMI-OPER | 5.58 | 5.58 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-90.1-2004-SEMI-OPER | 5.58 | 5.58 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-90.1-2004-SEMI-OPER | 3.25 | 3.25 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-90.1-2004-SEMI-OPER | 3.25 | 3.25 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 5.84 | 0.7 | 0.603
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 5.84 | 0.7 | 0.603
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 11969.85 | 9559.78 | 2410.07 | 0.8 | 4.04
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 39349.01 | 29000.42 | 10348.59 | 0.74 | 3.56
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 38791.02 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15833.46 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 65937.28 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.72 | 838.73 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.98 | 2163.71 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 6159.0711 | 7.8926 | 14.7231 | 0 | 0.0001 | 194421.3654 | 2378.1994
February | 4510.5959 | 6.1366 | 13.0585 | 0 | 0.0001 | 172504.7572 | 1779.8532
March | 4980.8496 | 6.8644 | 14.982 | 0 | 0.0001 | 197927.4909 | 1974.8406
April | 3717.138 | 5.461 | 13.3401 | 0 | 0.0001 | 176285.2114 | 1510.0155
May | 3287.9418 | 5.1785 | 14.0219 | 0 | 0.0001 | 185337.0074 | 1372.9368
June | 3134.7895 | 4.9985 | 13.7595 | 0 | 0.0001 | 181875.6177 | 1315.5407
July | 2990.6826 | 4.7931 | 13.283 | 0 | 0.0001 | 175579.2454 | 1257.6818
August | 3280.829 | 5.263 | 14.6025 | 0 | 0.0001 | 193021.0286 | 1380.2148
September | 3088.7746 | 4.9139 | 13.4859 | 0 | 0.0001 | 178258.4641 | 1295.0292
October | 3541.2524 | 5.4392 | 14.2195 | 0 | 0.0001 | 187935.6632 | 1463.9059
November | 4754.6538 | 6.5521 | 14.298 | 0 | 0.0001 | 188891.0677 | 1885.0963
December | 5954.3396 | 7.6553 | 14.3934 | 0 | 0.0001 | 190072.9819 | 2301.8265
Annual Sum or Average | 49400.918 | 71.1483 | 168.1673 | 0 | 0.0007 | 2222110 | 19915.1409
Minimum of Months | 2990.6826 | 4.7931 | 13.0585 | 0 | 0.0001 | 172504.7572 | 1257.6818
Maximum of Months | 6159.0711 | 7.8926 | 14.982 | 0 | 0.0001 | 197927.4909 | 2378.1994
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 68506500000 | 67427.263 | 02-JAN-16:30 | 49331.021 | 9104.397 | 3076.845 | 0 | 0 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 60783900000 | 61512.263 | 01-FEB-09:09 | 49331.021 | 9104.397 | 3076.845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 69741900000 | 61903.081 | 29-MAR-14:00 | 49331.021 | 9104.397 | 3076.845 | 0 | 390.818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 62116000000 | 61609.874 | 18-APR-15:00 | 49331.021 | 9104.397 | 3076.845 | 0 | 97.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 65305500000 | 62522 | 04-MAY-14:00 | 49331.021 | 9104.397 | 3076.845 | 0 | 1009.737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 64085800000 | 65909.685 | 28-JUN-14:00 | 49331.021 | 9104.397 | 3076.845 | 0 | 4397.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 61867200000 | 70213.823 | 24-JUL-14:00 | 49331.021 | 9104.397 | 3076.845 | 0 | 8701.559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 68013000000 | 67825.452 | 07-AUG-15:30 | 49331.021 | 9104.397 | 3076.845 | 0 | 6313.189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 62811300000 | 65848.137 | 01-SEP-15:00 | 49331.021 | 9104.397 | 3076.845 | 0 | 4335.873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 66221200000 | 62133.474 | 17-OCT-14:00 | 49331.021 | 9104.397 | 3076.845 | 0 | 621.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 66557800000 | 67427.263 | 06-NOV-16:49 | 49331.021 | 9104.397 | 3076.845 | 0 | 0 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 66974300000 | 67427.263 | 01-DEC-16:19 | 49331.021 | 9104.397 | 3076.845 | 0 | 0 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 782984000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 60783900000 | 61512.263 |  | 49331.021 | 9104.397 | 3076.845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 69741900000 | 70213.823 |  | 49331.021 | 9104.397 | 3076.845 | 0 | 8701.559 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 17060.19 | 1915.16 | 0 | 18975.35
Cost per Total Building Area ($/m2) | 3.53 | 0.4 | 0 | 3.92
Cost per Net Conditioned Building Area ($/m2) | 3.53 | 0.4 | 0 | 3.92

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1341.42 | 277.43 | 277.43
Net Site Energy | 1341.42 | 277.43 | 277.43
Total Source Energy | 3614.83 | 747.62 | 747.62
Net Source Energy | 3614.83 | 747.62 | 747.62
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 465.31 | 0 | 0 | 0 | 0
Cooling | 16.52 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 545.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.92 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 117.2 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 876.12 | 465.31 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 9.68 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 15.06 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 11.84 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.806 | 0.917 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.806 | 0.917 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.806 | 0.917 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.536 | 0.596 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.806 | 0.917 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.806 | 0.917 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.806 | 0.917 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.806 | 0.917 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.806 | 0.917 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.536 | 0.596 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.806 | 0.917 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.806 | 0.917 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.806 | 0.917 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.806 | 0.917 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-90.1-2004-SEMI-OPER | 5.58 | 5.58 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-90.1-2004-SEMI-OPER | 5.58 | 5.58 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-90.1-2004-SEMI-OPER | 3.25 | 3.25 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-90.1-2004-SEMI-OPER | 3.25 | 3.25 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 5.84 | 0.7 | 0.603
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 5.84 | 0.7 | 0.603
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17842.39 | 13483.48 | 4358.92 | 0.76 | 3.87
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 97814.09 | 66130.47 | 31683.63 | 0.68 | 3.51
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 58294.83 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23864.87 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 128653.97 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.95 | 1084.43 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.94 | 7513.32 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 33155.5804 | 54.0852 | 143.9499 | 0 | 0.0004 | 33130.7464 | 13768.8761
February | 27907.5781 | 46.544 | 127.2773 | 0 | 0.0004 | 29295.1389 | 11686.9687
March | 29475.3626 | 50.7917 | 144.2164 | 0 | 0.0004 | 33196.5155 | 12499.6409
April | 24150.8426 | 43.1493 | 127.3533 | 0 | 0.0004 | 29317.0933 | 10388.2168
May | 24601.4838 | 44.7031 | 134.2175 | 0 | 0.0004 | 30898.2775 | 10653.6336
June | 25350.288 | 46.1577 | 138.8661 | 0 | 0.0004 | 31968.5457 | 10986.8866
July | 25446.18 | 46.3347 | 139.4059 | 0 | 0.0004 | 32092.8244 | 11028.6785
August | 26568.4658 | 48.3776 | 145.5504 | 0 | 0.0004 | 33507.3424 | 11515.0274
September | 23608.0123 | 42.9725 | 129.2451 | 0 | 0.0004 | 29753.6671 | 10230.5514
October | 25069.3936 | 45.147 | 134.3348 | 0 | 0.0004 | 30924.738 | 10817.4168
November | 27117.8695 | 47.2502 | 135.8044 | 0 | 0.0004 | 31260.9405 | 11549.7003
December | 31160.9631 | 51.6167 | 139.9969 | 0 | 0.0004 | 32222.2194 | 13015.6204
Annual Sum or Average | 323612.0197 | 567.1297 | 1640.218 | 0 | 0.005 | 377568.049 | 138141.2174
Minimum of Months | 23608.0123 | 42.9725 | 127.2773 | 0 | 0.0004 | 29295.1389 | 10230.5514
Maximum of Months | 33155.5804 | 54.0852 | 145.5504 | 0 | 0.0004 | 33507.3424 | 13768.8761
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 76877400000 | 73022.57 | 02-JAN-16:30 | 49331.021 | 9104.397 | 8672.152 | 0 | 0 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 67977200000 | 73022.57 | 01-FEB-16:00 | 49331.021 | 9104.397 | 8672.152 | 0 | 0 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 77030000000 | 67450.453 | 31-MAR-15:50 | 49331.021 | 9104.397 | 8672.152 | 0 | 342.883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 68028100000 | 67826.538 | 07-APR-14:00 | 49331.021 | 9104.397 | 8672.152 | 0 | 718.968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 71697100000 | 76260.854 | 05-MAY-13:00 | 49331.021 | 9104.397 | 8672.152 | 0 | 9153.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 74180600000 | 88457.856 | 08-JUN-12:00 | 49331.021 | 9104.397 | 8672.152 | 0 | 21350.286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 74469000000 | 90675.394 | 13-JUL-14:00 | 49331.021 | 9104.397 | 8672.152 | 0 | 23567.824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 77751300000 | 88405.311 | 04-AUG-14:00 | 49331.021 | 9104.397 | 8672.152 | 0 | 21297.741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 69041100000 | 80002.168 | 05-SEP-14:20 | 49331.021 | 9104.397 | 8672.152 | 0 | 12894.598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 71758500000 | 68397.134 | 31-OCT-13:30 | 49331.021 | 9104.397 | 8672.152 | 0 | 1289.564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 72538700000 | 73022.57 | 06-NOV-16:40 | 49331.021 | 9104.397 | 8672.152 | 0 | 0 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 74769200000 | 73022.57 | 01-DEC-16:19 | 49331.021 | 9104.397 | 8672.152 | 0 | 0 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 876118000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 67977200000 | 67450.453 |  | 49331.021 | 9104.397 | 8672.152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 77751300000 | 90675.394 |  | 49331.021 | 9104.397 | 8672.152 | 0 | 23567.824 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 12936.1 | 3829.51 | 0 | 16765.61
Cost per Total Building Area ($/m2) | 2.68 | 0.79 | 0 | 3.47
Cost per Net Conditioned Building Area ($/m2) | 2.68 | 0.79 | 0 | 3.47

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1253.5 | 259.25 | 259.25
Net Site Energy | 1253.5 | 259.25 | 259.25
Total Source Energy | 3319.8 | 686.6 | 686.6
Net Source Energy | 3319.8 | 686.6 | 686.6
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 377.05 | 0 | 0 | 0 | 0
Cooling | 11.06 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 545.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.87 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 123.04 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 876.45 | 377.05 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 9.68 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 15.06 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 11.84 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.806 | 0.917 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.806 | 0.917 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.806 | 0.917 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.536 | 0.596 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.806 | 0.917 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.806 | 0.917 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.806 | 0.917 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.806 | 0.917 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.806 | 0.917 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.536 | 0.596 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.806 | 0.917 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.806 | 0.917 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.806 | 0.917 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.806 | 0.917 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-90.1-2004-SEMI-OPER | 5.58 | 5.58 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-90.1-2004-SEMI-OPER | 5.58 | 5.58 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-90.1-2004-SEMI-OPER | 3.25 | 3.25 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-90.1-2004-SEMI-OPER | 3.25 | 3.25 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 5.84 | 0.7 | 0.603
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 5.84 | 0.7 | 0.603
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17151.27 | 13697.96 | 3453.32 | 0.8 | 4.01
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 83052.15 | 61068.99 | 21983.17 | 0.74 | 3.8
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 47329.75 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21526.79 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 112508.33 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.04 | 1180.33 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 4.15 | 7921.04 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 24883.6029 | 39.7379 | 92.9353 | 0 | 0.0004 | 96613.6621 | 10294.5705
February | 21366.3603 | 34.6351 | 82.5817 | 0 | 0.0003 | 85854.1817 | 8889.8826
March | 22909.349 | 38.1495 | 94.0294 | 0 | 0.0004 | 97763.1533 | 9631.2581
April | 19034.1305 | 32.6515 | 83.2937 | 0 | 0.0003 | 86607.9065 | 8095.7787
May | 19357.0957 | 33.7405 | 87.6021 | 0 | 0.0003 | 91091.3211 | 8285.6133
June | 19101.8661 | 33.4849 | 87.4718 | 0 | 0.0003 | 90956.9493 | 8194.9346
July | 19175.6672 | 33.6443 | 87.9722 | 0 | 0.0003 | 91477.5529 | 8229.5415
August | 20691.4368 | 36.3027 | 94.9203 | 0 | 0.0004 | 98702.4821 | 8879.9527
September | 18418.0285 | 32.253 | 84.161 | 0 | 0.0003 | 87514.0528 | 7898.31
October | 19821.3375 | 34.2102 | 87.8656 | 0 | 0.0003 | 91363.0963 | 8451.0267
November | 21897.5316 | 36.3194 | 89.0902 | 0 | 0.0004 | 92626.8296 | 9191.6336
December | 24721.0606 | 39.2901 | 91.3094 | 0 | 0.0004 | 94921.9017 | 10208.8603
Annual Sum or Average | 251377.4666 | 424.419 | 1063.2328 | 0 | 0.0042 | 1105490 | 106251.3625
Minimum of Months | 18418.0285 | 32.253 | 82.5817 | 0 | 0.0003 | 85854.1817 | 7898.31
Maximum of Months | 24883.6029 | 39.7379 | 94.9203 | 0 | 0.0004 | 98702.4821 | 10294.5705
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 76596500000 | 73526.197 | 02-JAN-16:49 | 49331.021 | 9104.397 | 9175.779 | 0 | 0 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 68066200000 | 67611.197 | 01-FEB-09:09 | 49331.021 | 9104.397 | 9175.779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 77507800000 | 68297.714 | 30-MAR-14:00 | 49331.021 | 9104.397 | 9175.779 | 0 | 686.516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 68663800000 | 69808.713 | 25-APR-14:00 | 49331.021 | 9104.397 | 9175.779 | 0 | 2197.516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 72218300000 | 75207.383 | 23-MAY-15:00 | 49331.021 | 9104.397 | 9175.779 | 0 | 7596.186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 72111800000 | 81450.984 | 28-JUN-13:00 | 49331.021 | 9104.397 | 9175.779 | 0 | 13839.787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 72524500000 | 85267.379 | 17-JUL-15:39 | 49331.021 | 9104.397 | 9175.779 | 0 | 17656.182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 78252500000 | 85402.279 | 30-AUG-13:00 | 49331.021 | 9104.397 | 9175.779 | 0 | 17791.082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 69382200000 | 77108.845 | 06-SEP-14:00 | 49331.021 | 9104.397 | 9175.779 | 0 | 9497.648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 72433800000 | 70695.829 | 05-OCT-15:39 | 49331.021 | 9104.397 | 9175.779 | 0 | 3084.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 73435700000 | 73526.197 | 06-NOV-16:49 | 49331.021 | 9104.397 | 9175.779 | 0 | 0 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 75255200000 | 73526.197 | 01-DEC-16:40 | 49331.021 | 9104.397 | 9175.779 | 0 | 0 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 876448000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 68066200000 | 67611.197 |  | 49331.021 | 9104.397 | 9175.779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 78252500000 | 85402.279 |  | 49331.021 | 9104.397 | 9175.779 | 0 | 17791.082 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 9182.95 | 2581.97 | 0 | 11764.92
Cost per Total Building Area ($/m2) | 1.9 | 0.53 | 0 | 2.43
Cost per Net Conditioned Building Area ($/m2) | 1.9 | 0.53 | 0 | 2.43

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1599.8 | 330.87 | 330.87
Net Site Energy | 1599.8 | 330.87 | 330.87
Total Source Energy | 3843.78 | 794.97 | 794.97
Net Source Energy | 3843.78 | 794.97 | 794.97
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 705.65 | 0 | 0 | 0 | 0
Cooling | 12.93 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 545.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.86 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 138.88 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 894.16 | 705.65 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 9.68 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 15.06 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 11.84 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.536 | 0.596 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.536 | 0.596 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-90.1-2004-SEMI-OPER | 5.58 | 5.58 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-90.1-2004-SEMI-OPER | 5.58 | 5.58 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-90.1-2004-SEMI-OPER | 3.25 | 3.25 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-90.1-2004-SEMI-OPER | 3.25 | 3.25 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 5.84 | 0.7 | 0.603
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 5.84 | 0.7 | 0.603
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19002.31 | 14525.1 | 4477.21 | 0.76 | 3.9
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 113946.23 | 77037.13 | 36909.1 | 0.68 | 3.51
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 87361.67 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 25983.94 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 148485.1 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 1.42 | 132.3 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.04 | 1185.82 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 4.59 | 8752.47 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 28687.1877 | 42.1769 | 52.678 | 0 | 0.0004 | 34590.1482 | 11471.1991
February | 22729.6186 | 34.8199 | 46.3037 | 0 | 0.0004 | 30412.9704 | 9222.958
March | 21155.0628 | 35.0496 | 51.6981 | 0 | 0.0004 | 33970.4184 | 8836.5716
April | 16181.1238 | 28.6099 | 45.4075 | 0 | 0.0003 | 29845.0153 | 6931.0901
May | 16145.2084 | 29.3707 | 47.991 | 0 | 0.0003 | 31546.2939 | 6994.5039
June | 16369.579 | 29.868 | 48.9479 | 0 | 0.0004 | 32175.6491 | 7100.2198
July | 15981.9213 | 29.1636 | 47.7983 | 0 | 0.0003 | 31419.9719 | 6932.3558
August | 17334.0362 | 31.6314 | 51.8439 | 0 | 0.0004 | 34079.3455 | 7518.9039
September | 15285.5675 | 27.8539 | 45.5888 | 0 | 0.0003 | 29967.4541 | 6626.5809
October | 17027.1876 | 30.1923 | 48.0634 | 0 | 0.0004 | 31590.9789 | 7301.7643
November | 20113.6457 | 33.286 | 49.0287 | 0 | 0.0004 | 32216.1976 | 8397.914
December | 25753.0461 | 39.0172 | 51.0486 | 0 | 0.0004 | 33527.119 | 10408.2508
Annual Sum or Average | 232763.1846 | 391.0395 | 586.3978 | 0 | 0.0044 | 385341.5622 | 97742.3123
Minimum of Months | 15285.5675 | 27.8539 | 45.4075 | 0 | 0.0003 | 29845.0153 | 6626.5809
Maximum of Months | 28687.1877 | 42.1769 | 52.678 | 0 | 0.0004 | 34590.1482 | 11471.1991
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 80263800000 | 74363.113 | 02-JAN-16:40 | 49331.021 | 9104.397 | 10012.694 | 0 | 0 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 70571000000 | 68448.113 | 01-FEB-09:09 | 49331.021 | 9104.397 | 10012.694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 78825800000 | 68448.113 | 01-MAR-09:09 | 49331.021 | 9104.397 | 10012.694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 69253100000 | 68979.058 | 14-APR-15:00 | 49331.021 | 9104.397 | 10012.694 | 0 | 530.945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 73200800000 | 77147.366 | 31-MAY-12:39 | 49331.021 | 9104.397 | 10012.694 | 0 | 8699.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 74661200000 | 89794.813 | 29-JUN-14:00 | 49331.021 | 9104.397 | 10012.694 | 0 | 21346.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 72907700000 | 87506.902 | 13-JUL-15:39 | 49331.021 | 9104.397 | 10012.694 | 0 | 19058.789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 79078600000 | 87449.175 | 25-AUG-15:30 | 49331.021 | 9104.397 | 10012.694 | 0 | 19001.063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 69537200000 | 77793.813 | 14-SEP-14:00 | 49331.021 | 9104.397 | 10012.694 | 0 | 9345.701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 73304500000 | 69207.019 | 06-OCT-14:00 | 49331.021 | 9104.397 | 10012.694 | 0 | 758.906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 74755300000 | 74363.113 | 06-NOV-16:00 | 49331.021 | 9104.397 | 10012.694 | 0 | 0 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 77797200000 | 74363.113 | 01-DEC-16:30 | 49331.021 | 9104.397 | 10012.694 | 0 | 0 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 894156000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 69253100000 | 68448.113 |  | 49331.021 | 9104.397 | 10012.694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 80263800000 | 89794.813 |  | 49331.021 | 9104.397 | 10012.694 | 0 | 21346.7 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 16385.33 | 5578.71 | 0 | 21964.04
Cost per Total Building Area ($/m2) | 3.39 | 1.15 | 0 | 4.54
Cost per Net Conditioned Building Area ($/m2) | 3.39 | 1.15 | 0 | 4.54

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1465.2 | 303.03 | 303.03
Net Site Energy | 1465.2 | 303.03 | 303.03
Total Source Energy | 3735.15 | 772.5 | 772.5
Net Source Energy | 3735.15 | 772.5 | 772.5
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 569.58 | 0 | 0 | 0 | 0
Cooling | 5.12 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 545.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.84 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 148.18 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 895.62 | 569.58 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 9.68 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 15.06 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 11.84 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.536 | 0.596 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.536 | 0.596 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-90.1-2004-SEMI-OPER | 5.58 | 5.58 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-90.1-2004-SEMI-OPER | 5.58 | 5.58 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-90.1-2004-SEMI-OPER | 3.25 | 3.25 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-90.1-2004-SEMI-OPER | 3.25 | 3.25 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 5.84 | 0.7 | 0.603
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 5.84 | 0.7 | 0.603
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19060.12 | 15222.46 | 3837.65 | 0.8 | 4.01
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 89268.48 | 69491.4 | 19777.08 | 0.78 | 4.02
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 87797.01 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 25491.39 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 146169.08 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 1.67 | 155.21 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.15 | 1311.69 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 5.1 | 9560.79 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 26919.8532 | 40.9174 | 59.7299 | 0 | 0.0004 | 1416030 | 10910.2194
February | 22160.8087 | 34.6645 | 52.7173 | 0 | 0.0004 | 1249970 | 9076.2511
March | 21843.5278 | 36.1143 | 59.0006 | 0 | 0.0004 | 1399320 | 9134.4204
April | 18049.3181 | 30.8083 | 52.2494 | 0 | 0.0004 | 1239360 | 7641.2504
May | 17678.2751 | 31.0801 | 54.4488 | 0 | 0.0004 | 1291660 | 7571.6638
June | 17379.5329 | 30.7918 | 54.3857 | 0 | 0.0004 | 1290200 | 7466.6192
July | 16898.9506 | 29.9952 | 53.0802 | 0 | 0.0004 | 1259240 | 7265.4535
August | 18236.6184 | 32.3603 | 57.2484 | 0 | 0.0004 | 1358120 | 7839.6694
September | 16729.7736 | 29.5749 | 52.1145 | 0 | 0.0004 | 1236310 | 7181.1098
October | 18686.589 | 32.2132 | 55.2412 | 0 | 0.0004 | 1310370 | 7941.6992
November | 21082.8605 | 34.6504 | 56.1999 | 0 | 0.0004 | 1332860 | 8796.3878
December | 25464.1753 | 39.124 | 58.016 | 0 | 0.0004 | 1375480 | 10360.7761
Annual Sum or Average | 241130.2831 | 402.2942 | 664.4319 | 0 | 0.0047 | 15758900 | 101185.5202
Minimum of Months | 16729.7736 | 29.5749 | 52.1145 | 0 | 0.0004 | 1236310 | 7181.1098
Maximum of Months | 26919.8532 | 40.9174 | 59.7299 | 0 | 0.0004 | 1416030 | 10910.2194
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 80476100000 | 75297.312 | 02-JAN-16:49 | 49331.021 | 9104.397 | 10946.893 | 0 | 0 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 71039000000 | 69382.312 | 01-FEB-09:09 | 49331.021 | 9104.397 | 10946.893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 79526500000 | 69923.926 | 28-MAR-15:39 | 49331.021 | 9104.397 | 10946.893 | 0 | 541.614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 70435600000 | 69518.55 | 06-APR-15:00 | 49331.021 | 9104.397 | 10946.893 | 0 | 136.238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 73408400000 | 70401.143 | 16-MAY-15:00 | 49331.021 | 9104.397 | 10946.893 | 0 | 1018.831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 73325300000 | 84173.976 | 30-JUN-14:00 | 49331.021 | 9104.397 | 10946.893 | 0 | 14791.664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 71565600000 | 84161.558 | 21-JUL-15:00 | 49331.021 | 9104.397 | 10946.893 | 0 | 14779.246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 77185300000 | 80353.649 | 09-AUG-15:00 | 49331.021 | 9104.397 | 10946.893 | 0 | 10971.337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 70262600000 | 74343.275 | 01-SEP-15:00 | 49331.021 | 9104.397 | 10946.893 | 0 | 4960.964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 74471500000 | 70272.245 | 06-OCT-15:00 | 49331.021 | 9104.397 | 10946.893 | 0 | 889.933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 75749600000 | 75297.312 | 08-NOV-16:00 | 49331.021 | 9104.397 | 10946.893 | 0 | 0 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 78171700000 | 75297.312 | 01-DEC-16:40 | 49331.021 | 9104.397 | 10946.893 | 0 | 0 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 895617000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 70262600000 | 69382.312 |  | 49331.021 | 9104.397 | 10946.893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 80476100000 | 84173.976 |  | 49331.021 | 9104.397 | 10946.893 | 0 | 14791.664 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 20168.03 | 4517.48 | 0 | 24685.5
Cost per Total Building Area ($/m2) | 4.17 | 0.93 | 0 | 5.11
Cost per Net Conditioned Building Area ($/m2) | 4.17 | 0.93 | 0 | 5.11

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1831.92 | 378.88 | 378.88
Net Site Energy | 1831.92 | 378.88 | 378.88
Total Source Energy | 4115.24 | 851.11 | 851.11
Net Source Energy | 4115.24 | 851.11 | 851.11
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 930.09 | 0 | 0 | 0 | 0
Cooling | 3.34 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 545.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.79 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 156.23 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 901.83 | 930.09 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 9.68 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 15.06 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 11.84 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.552 | 0.616 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.552 | 0.616 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-90.1-2004-SEMI-OPER | 5.58 | 5.58 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-90.1-2004-SEMI-OPER | 5.58 | 5.58 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-90.1-2004-SEMI-OPER | 3.25 | 3.25 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-90.1-2004-SEMI-OPER | 3.25 | 3.25 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 5.84 | 0.7 | 0.603
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 5.84 | 0.7 | 0.603
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19752.05 | 15365.11 | 4386.94 | 0.78 | 3.71
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 126515.28 | 85534.86 | 40980.42 | 0.68 | 3.49
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 107945.85 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 27467.96 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 160779 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 1.94 | 179.89 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.13 | 1282.57 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 5.09 | 9557.74 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 29895.7224 | 43.5755 | 53.6659 | 0 | 0.0004 | 35236.5703 | 11918.3122
February | 25575.4496 | 37.844 | 47.7525 | 0 | 0.0004 | 31357.3221 | 10250.0497
March | 23912.8972 | 38.0293 | 53.2618 | 0 | 0.0004 | 34990.7426 | 9836.5931
April | 17944.0095 | 30.5672 | 46.5787 | 0 | 0.0003 | 30610.2485 | 7575.3703
May | 16801.2438 | 30.0348 | 48.2172 | 0 | 0.0004 | 31693.08 | 7228.113
June | 15877.9849 | 28.9312 | 47.3483 | 0 | 0.0003 | 31124.0117 | 6883.1874
July | 15605.2991 | 28.4665 | 46.6398 | 0 | 0.0003 | 30658.4189 | 6768.0495
August | 16849.7845 | 30.7061 | 50.26 | 0 | 0.0004 | 33038.0305 | 7304.8731
September | 15740.8606 | 28.4125 | 46.0642 | 0 | 0.0003 | 30278.9166 | 6798.0511
October | 18073.7725 | 31.4385 | 49.0326 | 0 | 0.0004 | 32225.6417 | 7692.2995
November | 22046.6824 | 35.4482 | 50.3647 | 0 | 0.0004 | 33089.3383 | 9105.8972
December | 27814.7121 | 41.2708 | 52.3025 | 0 | 0.0004 | 34345.8256 | 11158.328
Annual Sum or Average | 246138.4185 | 404.7246 | 591.4882 | 0 | 0.0044 | 388648.147 | 102519.1242
Minimum of Months | 15605.2991 | 28.4125 | 46.0642 | 0 | 0.0003 | 30278.9166 | 6768.0495
Maximum of Months | 29895.7224 | 43.5755 | 53.6659 | 0 | 0.0004 | 35236.5703 | 11918.3122
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 81763800000 | 75265.134 | 02-JAN-16:30 | 49331.021 | 9104.397 | 10914.715 | 0 | 0 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 72762300000 | 69455.617 | 01-FEB-09:09 | 49331.021 | 9104.397 | 11020.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 81193400000 | 69350.134 | 01-MAR-09:09 | 49331.021 | 9104.397 | 10914.715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 71028800000 | 69350.134 | 03-APR-08:09 | 49331.021 | 9104.397 | 10914.715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 73541400000 | 70317.109 | 31-MAY-15:00 | 49331.021 | 9104.397 | 10914.715 | 0 | 966.975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 72220900000 | 79085.411 | 14-JUN-15:00 | 49331.021 | 9104.397 | 10914.715 | 0 | 9735.277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 71140600000 | 86604.096 | 06-JUL-15:30 | 49331.021 | 9104.397 | 10914.715 | 0 | 17253.962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 76662300000 | 81973.832 | 11-AUG-14:00 | 49331.021 | 9104.397 | 10914.715 | 0 | 12623.698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 70259900000 | 70889.044 | 07-SEP-14:00 | 49331.021 | 9104.397 | 10914.715 | 0 | 1538.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 74777200000 | 69405.851 | 06-OCT-14:00 | 49331.021 | 9104.397 | 10914.715 | 0 | 55.717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 76781300000 | 75265.134 | 06-NOV-16:49 | 49331.021 | 9104.397 | 10914.715 | 0 | 0 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 79696900000 | 75265.134 | 01-DEC-16:19 | 49331.021 | 9104.397 | 10914.715 | 0 | 0 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 901829000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 70259900000 | 69350.134 |  | 49331.021 | 9104.397 | 10914.715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 81763800000 | 86604.096 |  | 49331.021 | 9104.397 | 11020.199 | 0 | 17253.962 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 16214.76 | 7329.41 | 0 | 23544.18
Cost per Total Building Area ($/m2) | 3.35 | 1.52 | 0 | 4.87
Cost per Net Conditioned Building Area ($/m2) | 3.35 | 1.52 | 0 | 4.87

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2870.14 | 593.6 | 593.6
Net Site Energy | 2870.14 | 593.6 | 593.6
Total Source Energy | 5489.62 | 1135.36 | 1135.36
Net Source Energy | 5489.62 | 1135.36 | 1135.36
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1920.37 | 0 | 0 | 0 | 0
Cooling | 0.46 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 545.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.22 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 207.61 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 949.77 | 1920.37 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 9.68 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 15.06 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 11.84 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.4 | 0.433 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.4 | 0.433 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.732 | 0.821 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-90.1-2004-SEMI-OPER | 5.58 | 5.58 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-90.1-2004-SEMI-OPER | 5.58 | 5.58 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-90.1-2004-SEMI-OPER | 3.25 | 3.25 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-90.1-2004-SEMI-OPER | 3.25 | 3.25 | 5.838 | 0.7 | 0.603 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 5.84 | 0.7 | 0.603
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 5.84 | 0.7 | 0.603
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 22864.02 | 18260.47 | 4603.55 | 0.8 | 3.77
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 104871.69 | 83756.33 | 21115.36 | 0.8 | 4.14
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 189902.74 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 35030.54 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 208165.83 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 3.58 | 332.28 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.38 | 1573.47 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 6.34 | 11884.96 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 42378.5667 | 44.6199 | 128.7927 | 0 | 0.0005 | 25824.2646 | 15613.6977
February | 34794.4756 | 36.9726 | 112.813 | 0 | 0.0004 | 22622.5818 | 12871.4595
March | 28138.1403 | 31.3809 | 122.2217 | 0 | 0.0004 | 24519.1835 | 10637.0437
April | 18759.082 | 22.0007 | 104.0727 | 0 | 0.0004 | 20883.6496 | 7257.6477
May | 15017.2983 | 18.6203 | 104.4019 | 0 | 0.0004 | 20953.6413 | 5965.1146
June | 14072.9359 | 17.6014 | 101.0178 | 0 | 0.0003 | 20274.9198 | 5613.3981
July | 13527.3511 | 16.9344 | 97.4229 | 0 | 0.0003 | 19553.4401 | 5398.1396
August | 15255.4549 | 19.0622 | 109.1243 | 0 | 0.0004 | 21901.8891 | 6082.2716
September | 15501.5273 | 18.9963 | 103.0724 | 0 | 0.0004 | 20686.1118 | 6122.9171
October | 21486.4628 | 24.9411 | 113.7991 | 0 | 0.0004 | 22834.3909 | 8273.0819
November | 30541.5011 | 33.5061 | 121.0467 | 0 | 0.0004 | 24280.7084 | 11460.1552
December | 36543.4728 | 39.1763 | 125.7059 | 0 | 0.0005 | 25210.3064 | 13571.5858
Annual Sum or Average | 286016.2687 | 323.8122 | 1343.4912 | 0 | 0.0048 | 269545.0874 | 108866.5125
Minimum of Months | 13527.3511 | 16.9344 | 97.4229 | 0 | 0.0003 | 19553.4401 | 5398.1396
Maximum of Months | 42378.5667 | 44.6199 | 128.7927 | 0 | 0.0005 | 25824.2646 | 15613.6977
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 90994600000 | 78141.131 | 02-JAN-09:09 | 49331.021 | 9104.397 | 13790.713 | 0 | 0 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 79713100000 | 78141.131 | 01-FEB-09:09 | 49331.021 | 9104.397 | 13790.713 | 0 | 0 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 86396000000 | 72226.131 | 13-MAR-08:09 | 49331.021 | 9104.397 | 13790.713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 73585800000 | 71968.254 | 03-APR-08:09 | 49331.021 | 9104.397 | 13532.835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 73832400000 | 72633.213 | 24-MAY-14:00 | 49331.021 | 9104.397 | 13532.835 | 0 | 664.959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 71440900000 | 75162.575 | 20-JUN-15:00 | 49331.021 | 9104.397 | 13532.835 | 0 | 3194.321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 68898700000 | 75624.989 | 21-JUL-15:00 | 49331.021 | 9104.397 | 13532.835 | 0 | 3656.736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 77173700000 | 73428.848 | 15-AUG-14:39 | 49331.021 | 9104.397 | 13532.835 | 0 | 1460.595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 72889800000 | 71968.254 | 01-SEP-08:09 | 49331.021 | 9104.397 | 13532.835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 80459400000 | 77883.254 | 23-OCT-08:09 | 49331.021 | 9104.397 | 13532.835 | 0 | 0 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 85555700000 | 78141.131 | 01-NOV-08:09 | 49331.021 | 9104.397 | 13790.713 | 0 | 0 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 88831200000 | 78141.131 | 07-DEC-14:39 | 49331.021 | 9104.397 | 13790.713 | 0 | 0 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 949771000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 68898700000 | 71968.254 |  | 49331.021 | 9104.397 | 13532.835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 90994600000 | 78141.131 |  | 49331.021 | 9104.397 | 13790.713 | 0 | 3656.736 | 5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 27811.91 | 7892.07 | 0 | 35703.98
Cost per Total Building Area ($/m2) | 5.75 | 1.63 | 0 | 7.38
Cost per Net Conditioned Building Area ($/m2) | 5.75 | 1.63 | 0 | 7.38

## Picture
DOE Commercial Building Benchmark - Warehouse

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 64 | 3337.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 64 | 3337.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 9.8 | 54.22 | 2827.19
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.24 | 0.24 | 0.24 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.82
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.7 | 0.9 | 0.9 | 0.9 | 0.5 | 0.85 | 0.85 | 0.85 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8 | 35.2 | 1835.43
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 10.1 | 56.3 | 2935.64
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.4
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 3.5 | 182.5
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INFIL_SCH | Fraction | Through 12/31 | WD, SummerDesign | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
|  |  | Sat | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
|  |  | Sat | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.07 | 0.07 | 0.1 | 0.3 | 0.36 | 0.36 | 0.46 | 0.57 | 0.43 | 0.38 | 0.4 | 0.3 | 0.18 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 4.29 | 22.88 | 1193.03
|  |  | Sat, WinterDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.06 | 0.12 | 0.12 | 0.17 | 0.04 | 0.04 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.91
|  |  | Sun, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.04 | 0.04 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.52
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 432.5 | 2956 | 154134.29
|  |  | SummerDesign | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 372
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Sat | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 421.5
|  |  | Sun, Hol, Other | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 372
HTGSETP_FineStorage_SCH | Temperature | Through 12/31 | All | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 372 | 2604 | 135780
HTGSETP_BulkStorage_SCH | Temperature | Through 12/31 | All | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 172.8 | 1209.6 | 63072
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 660 | 4692 | 244654.29
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 672
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
CLGSETP_FineStorage_SCH | Temperature | Through 12/31 | All | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 640.8 | 4485.6 | 233892
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 58 | 3024.29
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
|  | Through 9/30 | All | [24 empty] | 24 | 168 | bar: 1 to 24
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -240 | -1680 | -87600
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600