## BuildingSummary
Building Summary Fast Food Restaurant new construction version 1.0_3.0
|  | Value | Data Source
Program
| Building Name | Benchmark Fast Food New
| Available Fuel Types | gas, electricity
| Principal Building Activity | Food Service
Form |  |  | Time Saver Standards; FF Restaurant studies (EPRI, MEOS, LBL) cited in Huang et al. 1991 for all Form parameters
| Total Floor Area (m2) | 232.2
| Building Shape | Rectangle
| Aspect Ratio | 1
| Number of Floors | 1
Window Fraction (Window to Wall Ratio)
| South | 0.28
| East | 0.14
| North | 0
| West | 0.14
| Total | 0.14
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | 2 zones plus attic
| Floor to Ceiling Height (m) | 10
| Roof type | Attic | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Wood-Framed | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 185.9
| Net Dimensions - Total Area (m2) | 159.9
| Wall to Skin Ratio | 0.418
Roof
| Construction Type | Attic | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 258.86
| Net Dimensions - Total Area (m2) | 258.86
| Roof to Skin Ratio | 0.582
| Window Dimensions (m2) |  | Time Saver Standards; FF Restaurant studies (EPRI, MEOS, LBL) cited in Huang et al. 1991
| South | 13.01
| East | 6.51
| North | 0
| West | 6.51
| Total Area (m2) | 26.03
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 10 cm slab-on-grade
| Dimensions - Total Area (m2) | 232.2
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
Dimensions - Total Area (m2)
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 46.47
| Thermal diffusivity (m2/s) | 1.84e-07
| Air Barrier System |  | See Benchmark Technical Report
| Infiltration (ACH) | 0.64
HVAC |  |  | 2003 CBECS
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | Unitary DX | 2003 CBECS
| Fan Control | Constant volume
Service Water Heating
| SWH Type | Storage Tank
| Fuel | Natural Gas | Standard 90.1-2004
| Thermal Efficiency (%) | 80
| Temperature Setpoint (ºC ) | 140
| Water Consumption (m3 ) | 413.75

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Dining | Yes | 1 | 116.17 | 354.18 | 3.0488 | 92.94 | 26.02 | 1.3935 | 83.3628 | 22.596 | 129.12 | 0 | 0 | 10 | 0 | 833.6282 | 0 | 0.64258
Kitchen | Yes | 1 | 116.17 | 354.18 | 3.0488 | 92.94 | 0 | 18.5806 | 6.2522 | 12.912 | 301.28 | 1893.76 | 151.416 | 8 | 0 | 50.0177 | 2359.735 | 0.64258
Attic | No | 1 | 232.34 | 262.34 | 1.1291 | 0 | 0 | N/A | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 1
Total Conditioned Zones |  |  | 232.34 | 708.36 |  | 185.88 | 26.02 |  | 89.615
Data Source | [7 empty] | 1 |  | 2 | 4, 5 | 4, 5 | 4, 5 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report
[5] Smith, V. A. and D.R. Fisher. (2001). Estimating Food Service Loads and Profiles. ASHRAE Transactions 2001. V. 107. Pt 2. Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.

## Query (hidden)
01-Miami
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 2144.03 | 9227.88 | 9227.88
Net Site Energy | 2144.03 | 9227.88 | 9227.88
Total Source Energy | 5048.75 | 21729.72 | 21729.72
Net Source Energy | 5048.75 | 21729.72 | 21729.72
Area (m2)
Total Building Area | 232.34
Net Conditioned Building Area | 232.34
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 2.92 | 0 | 0 | 0 | 0
Cooling | 411.53 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 75.06 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 15.74 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 441.62 | 881.7 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 203.08 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 42.58 | 0 | 0 | 0 | 413.75
Refrigeration | 69.8 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1216.84 | 927.2 | 0 | 0 | 0 | 413.75
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 1216.84 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 1216.84 | 100
Total On-Site and Utility Electric Sources | 1216.84 | 100
Total Electricity End Uses | 1216.84 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS | 0.22 | 0.505 | 0.55 | 46.47 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 116.17 | 0 | 180
KITCHEN_WALL_NORTH | EXT-WALLS | 0.22 | 0.505 | 0.55 | 46.47 | 0 | 90 | N
KITCHEN_WALL_EAST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 90 | 90 | E
KITCHEN_WALL_WEST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 116.17 | 0 | 180
WEST-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 27.38 | 270 | 45
EAST-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 27.38 | 90 | 45
NORTH-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 102.05 | 0 | 18.44
SOUTH-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 102.05 | 180 | 18.44
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
DINING_WALL_EAST_WINDOW | WINDOW_EAST | 6.51 | 6.88 | 0.25 | 0.25 | No | DINING_WALL_EAST
DINING_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 13.01 | 6.88 | 0.25 | 0.25 | No | DINING_WALL_SOUTH
DINING_WALL_WEST_WINDOW | WINDOW_WEST | 6.51 | 6.88 | 0.25 | 0.25 | No | DINING_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 33606.59 | 2.96
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 58597.96 | 2.78
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.83 | 0.01 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.01 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 1.35 | 2566.27 | 1 | Fan Energy
PSZ-AC_2:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.36 | 4474.66 | 1 | Fan Energy
Nominal Capacity [W]
PSZ-AC_1:1_HEATC | 15718.72
PSZ-AC_2:2_HEATC | 27407.86
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 19715.7008 | 31.1911 | 104.7168 | 0 | 0.0005 | 12957.4736 | 8155.7849
February | 17994.5035 | 28.5327 | 96.0839 | 0 | 0.0004 | 11889.3176 | 7450.2578
March | 20400.3538 | 32.4433 | 109.6841 | 0 | 0.0005 | 13572.271 | 8455.9473
April | 21087.3586 | 33.7977 | 115.4383 | 0 | 0.0005 | 14284.5451 | 8766.943
May | 23396.0581 | 37.7705 | 130.222 | 0 | 0.0006 | 16114.1523 | 9754.0808
June | 23514.5592 | 38.1007 | 131.9746 | 0 | 0.0006 | 16331.15 | 9817.4002
July | 25152.935 | 40.883 | 142.1751 | 0 | 0.0007 | 17593.5224 | 10514.2239
August | 24887.6851 | 40.4114 | 140.3568 | 0 | 0.0006 | 17368.4869 | 10399.286
September | 23679.7509 | 38.3865 | 133.0446 | 0 | 0.0006 | 16463.5707 | 9888.1869
October | 22948.9526 | 36.9732 | 127.1395 | 0 | 0.0006 | 15732.6518 | 9560.1171
November | 20570.1195 | 32.8763 | 111.88 | 0 | 0.0005 | 13844.1453 | 8542.6509
December | 19608.9785 | 31.0479 | 104.3516 | 0 | 0.0005 | 12912.3109 | 8114.2044
Annual Sum or Average | 262956.9554 | 422.4143 | 1447.0673 | 0 | 0.0067 | 179063.5978 | 109419.0833
Minimum of Months | 17994.5035 | 28.5327 | 96.0839 | 0 | 0.0004 | 11889.3176 | 7450.2578
Maximum of Months | 25152.935 | 40.883 | 142.1751 | 0 | 0.0007 | 17593.5224 | 10514.2239
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 88053200000 | 53296.747 | 06-JAN-12:20 | 3712.724 | 16310.475 | 7040.94 | 0 | 23300.879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2931.729 | 0 | 0
February | 80794500000 | 53946.498 | 23-FEB-12:09 | 3712.724 | 16310.475 | 7040.94 | 0 | 23950.626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2931.733 | 0 | 0
March | 92231100000 | 53950.562 | 13-MAR-11:20 | 3712.724 | 16310.475 | 7040.94 | 0 | 23954.704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2931.719 | 0 | 0
April | 97071400000 | 54569.137 | 04-APR-11:20 | 3712.724 | 16310.475 | 7040.94 | 0 | 24573.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2931.717 | 0 | 0
May | 109505000000 | 59315.74 | 23-MAY-11:20 | 3712.724 | 16310.475 | 7040.94 | 0 | 29319.878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2931.724 | 0 | 0
June | 110979000000 | 61101.549 | 26-JUN-10:20 | 3712.724 | 16310.475 | 7040.94 | 0 | 29445.076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4592.334 | 0 | 0
July | 119558000000 | 60986.02 | 11-JUL-11:20 | 3712.724 | 16310.475 | 7040.94 | 0 | 30990.161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2931.72 | 0 | 0
August | 118029000000 | 60969.845 | 21-AUG-13:00 | 3712.724 | 16310.475 | 7040.94 | 0 | 31738.901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2166.806 | 0 | 0
September | 111879000000 | 59290.125 | 01-SEP-11:20 | 3712.724 | 16310.475 | 7040.94 | 0 | 29294.256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2931.73 | 0 | 0
October | 106912000000 | 58570.909 | 06-OCT-11:20 | 3712.724 | 16310.475 | 7040.94 | 0 | 28575.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2931.733 | 0 | 0
November | 94078700000 | 55758.241 | 01-NOV-12:09 | 3712.724 | 16310.475 | 7040.94 | 0 | 25762.368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2931.734 | 0 | 0
December | 87746300000 | 51175.78 | 15-DEC-12:20 | 3712.724 | 16310.475 | 7040.94 | 0 | 21179.923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2931.717 | 0 | 0
Annual Sum or Average | 1216840000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 80794500000 | 51175.78 |  | 3712.724 | 16310.475 | 7040.94 | 0 | 21179.923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2166.806 | 0 | 0
Maximum of Months | 119558000000 | 61101.549 |  | 3712.724 | 16310.475 | 7040.94 | 0 | 31738.901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4592.334 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 25629.59 | 10635.49 | 0 | 36265.08
Cost per Total Building Area ($/m2) | 110.31 | 45.77 | 0 | 156.08
Cost per Net Conditioned Building Area ($/m2) | 110.31 | 45.77 | 0 | 156.08
02-Houston
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 2097.4 | 9027.17 | 9027.17
Net Site Energy | 2097.4 | 9027.17 | 9027.17
Total Source Energy | 1095.73 | 4715.99 | 4715.99
Net Source Energy | 1095.73 | 4715.99 | 4715.99
Area (m2)
Total Building Area | 232.34
Net Conditioned Building Area | 232.34
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 69.8 | 0 | 0 | 0 | 0
Cooling | 293 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 75.06 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 15.73 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 441.62 | 881.7 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 200.18 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 51.91 | 0 | 0 | 0 | 413.75
Refrigeration | 68.4 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1093.99 | 1003.41 | 0 | 0 | 0 | 413.75
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 1093.99 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 1093.99 | 100
Total On-Site and Utility Electric Sources | 1093.99 | 100
Total Electricity End Uses | 1093.99 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS | 0.22 | 0.505 | 0.55 | 46.47 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 116.17 | 0 | 180
KITCHEN_WALL_NORTH | EXT-WALLS | 0.22 | 0.505 | 0.55 | 46.47 | 0 | 90 | N
KITCHEN_WALL_EAST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 90 | 90 | E
KITCHEN_WALL_WEST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 116.17 | 0 | 180
WEST-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 27.38 | 270 | 45
EAST-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 27.38 | 90 | 45
NORTH-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 102.05 | 0 | 18.44
SOUTH-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 102.05 | 180 | 18.44
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
DINING_WALL_EAST_WINDOW | WINDOW_EAST | 6.51 | 6.88 | 0.25 | 0.25 | No | DINING_WALL_EAST
DINING_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 13.01 | 6.88 | 0.25 | 0.25 | No | DINING_WALL_SOUTH
DINING_WALL_WEST_WINDOW | WINDOW_WEST | 6.51 | 6.88 | 0.25 | 0.25 | No | DINING_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 34360.92 | 2.96
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 58597.96 | 2.78
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.83 | 0.01 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.01 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 1.38 | 2623.87 | 1 | Fan Energy
PSZ-AC_2:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.36 | 4474.66 | 1 | Fan Energy
Nominal Capacity [W]
PSZ-AC_1:1_HEATC | 21216.64
PSZ-AC_2:2_HEATC | 36182.14
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 22729.2689 | 27.7061 | 99.1486 | 0 | 0.0003 | 33811.6802 | 8778.4252
February | 19739.0856 | 24.0218 | 85.5533 | 0 | 0.0003 | 29175.1835 | 7618.489
March | 22457.2873 | 27.7202 | 102.803 | 0 | 0.0003 | 35059.8405 | 8717.9332
April | 23931.9499 | 29.8097 | 113.3247 | 0 | 0.0003 | 38649.6017 | 9325.1054
May | 27595.1677 | 34.5936 | 133.7651 | 0 | 0.0004 | 45622.0077 | 10780.9574
June | 29251.1876 | 36.837 | 144.1368 | 0 | 0.0004 | 49160.232 | 11449.5113
July | 31821.3594 | 40.1673 | 158.1124 | 0 | 0.0005 | 53927.2907 | 12467.5937
August | 31152.3769 | 39.286 | 154.2722 | 0 | 0.0004 | 52617.3429 | 12200.7362
September | 27956.5025 | 35.1331 | 136.7283 | 0 | 0.0004 | 46633.0707 | 10933.276
October | 25513.4317 | 31.8424 | 121.6929 | 0 | 0.0004 | 41503.9386 | 9949.4254
November | 22420.7839 | 27.7622 | 103.8542 | 0 | 0.0003 | 35418.8264 | 8714.9755
December | 22061.3287 | 26.9044 | 96.4097 | 0 | 0.0003 | 32877.7453 | 8522.0643
Annual Sum or Average | 306629.7301 | 381.7838 | 1449.8011 | 0 | 0.0042 | 494456.7602 | 119458.4927
Minimum of Months | 19739.0856 | 24.0218 | 85.5533 | 0 | 0.0003 | 29175.1835 | 7618.489
Maximum of Months | 31821.3594 | 40.1673 | 158.1124 | 0 | 0.0005 | 53927.2907 | 12467.5937
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 74808400000 | 51129.578 | 03-JAN-12:20 | 3712.724 | 16310.475 | 7098.542 | 0 | 21076.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2931.727 | 0 | 0
February | 64550200000 | 46839.738 | 21-FEB-12:20 | 3712.724 | 16310.475 | 7098.542 | 0 | 16786.277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2931.719 | 0 | 0
March | 77570000000 | 50117.915 | 25-MAR-11:00 | 3300.199 | 16310.475 | 7098.542 | 0 | 21268.663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2140.035 | 0 | 0
April | 85512300000 | 54321.175 | 29-APR-11:20 | 3300.199 | 16310.475 | 7098.542 | 0 | 24698.357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2913.601 | 0 | 0
May | 100939000000 | 58801.259 | 18-MAY-11:20 | 3712.724 | 16310.475 | 7098.542 | 0 | 28747.796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2931.721 | 0 | 0
June | 108767000000 | 58651.286 | 28-JUN-11:20 | 3712.724 | 16310.475 | 7098.542 | 0 | 28597.819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2931.725 | 0 | 0
July | 119314000000 | 61583.8 | 18-JUL-12:00 | 3712.724 | 16310.475 | 7098.542 | 0 | 32276.172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2185.886 | 0 | 0
August | 116416000000 | 62227.958 | 31-AUG-11:20 | 3712.724 | 16310.475 | 7098.542 | 0 | 32163.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2943.196 | 0 | 0
September | 103176000000 | 61122.174 | 16-SEP-10:20 | 3300.199 | 16310.475 | 7098.542 | 0 | 29838.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4574.217 | 0 | 0
October | 91827500000 | 56419.493 | 31-OCT-12:09 | 3712.724 | 16310.475 | 7098.542 | 0 | 26366.015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2931.736 | 0 | 0
November | 78364200000 | 53144.635 | 26-NOV-11:00 | 2887.674 | 16310.475 | 7098.542 | 0 | 23952.431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2895.511 | 0 | 0
December | 72742100000 | 52885.673 | 02-DEC-12:20 | 3300.199 | 16310.475 | 7098.542 | 0 | 23262.857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2913.599 | 0 | 0
Annual Sum or Average | 1093990000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 64550200000 | 46839.738 |  | 2887.674 | 16310.475 | 7098.542 | 0 | 16786.277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2140.035 | 0 | 0
Maximum of Months | 119314000000 | 62227.958 |  | 3712.724 | 16310.475 | 7098.542 | 0 | 32276.172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4574.217 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 32766.41 | 8234.85 | 0 | 41001.26
Cost per Total Building Area ($/m2) | 141.03 | 35.44 | 0 | 176.47
Cost per Net Conditioned Building Area ($/m2) | 141.03 | 35.44 | 0 | 176.47
03-Phoenix
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 2025.44 | 8717.48 | 8717.48
Net Site Energy | 2025.44 | 8717.48 | 8717.48
Total Source Energy | 4415.29 | 19003.34 | 19003.34
Net Source Energy | 4415.29 | 19003.34 | 19003.34
Area (m2)
Total Building Area | 232.34
Net Conditioned Building Area | 232.34
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 33.23 | 0 | 0 | 0 | 0
Cooling | 255.05 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 75.06 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 15.73 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 441.62 | 881.7 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 209.02 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 46.54 | 0 | 0 | 0 | 413.75
Refrigeration | 67.51 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1063.98 | 961.46 | 0 | 0 | 0 | 413.75
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 1063.98 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 1063.98 | 100
Total On-Site and Utility Electric Sources | 1063.98 | 100
Total Electricity End Uses | 1063.98 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS | 0.22 | 0.505 | 0.55 | 46.47 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 116.17 | 0 | 180
KITCHEN_WALL_NORTH | EXT-WALLS | 0.22 | 0.505 | 0.55 | 46.47 | 0 | 90 | N
KITCHEN_WALL_EAST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 90 | 90 | E
KITCHEN_WALL_WEST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 116.17 | 0 | 180
WEST-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 27.38 | 270 | 45
EAST-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 27.38 | 90 | 45
NORTH-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 102.05 | 0 | 18.44
SOUTH-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 102.05 | 180 | 18.44
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
DINING_WALL_EAST_WINDOW | WINDOW_EAST | 6.51 | 6.88 | 0.25 | 0.25 | No | DINING_WALL_EAST
DINING_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 13.01 | 6.88 | 0.25 | 0.25 | No | DINING_WALL_SOUTH
DINING_WALL_WEST_WINDOW | WINDOW_WEST | 6.51 | 6.88 | 0.25 | 0.25 | No | DINING_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 38864.64 | 2.96
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 44794.29 | 2.78
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.83 | 0.01 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.01 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 1.57 | 2967.78 | 1 | Fan Energy
PSZ-AC_2:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.36 | 4474.66 | 1 | Fan Energy
Nominal Capacity [W]
PSZ-AC_1:1_HEATC | 20246.59
PSZ-AC_2:2_HEATC | 30526.69
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 18235.9051 | 27.2392 | 77.3779 | 0 | 0.0002 | 571412.854 | 7392.0897
February | 16617.6661 | 24.8251 | 70.5342 | 0 | 0.0002 | 520874.088 | 6736.4393
March | 19673.7688 | 29.9161 | 87.3067 | 0 | 0.0002 | 644768.366 | 8028.4469
April | 20298.0162 | 31.1513 | 92.1462 | 0 | 0.0003 | 680525.8022 | 8312.1136
May | 22689.2308 | 35.1458 | 105.3503 | 0 | 0.0003 | 778062.0276 | 9324.1587
June | 25333.6619 | 39.749 | 121.2963 | 0 | 0.0003 | 895860.6538 | 10462.1549
July | 27461.3938 | 43.2558 | 132.7016 | 0 | 0.0004 | 980106.1666 | 11357.8764
August | 26775.8336 | 42.092 | 128.7814 | 0 | 0.0004 | 951147.7378 | 11065.8426
September | 24266.9505 | 37.936 | 115.1811 | 0 | 0.0003 | 850687.4522 | 10007.5421
October | 21400.7569 | 32.9425 | 97.8671 | 0 | 0.0003 | 722782.45 | 8773.6826
November | 18702.7569 | 28.3985 | 82.7009 | 0 | 0.0002 | 610751.5014 | 7628.0497
December | 18453.5413 | 27.451 | 77.482 | 0 | 0.0002 | 572174.0816 | 7468.8565
Annual Sum or Average | 259909.4819 | 400.1024 | 1188.7258 | 0 | 0.0033 | 8779153.1812 | 106557.2531
Minimum of Months | 16617.6661 | 24.8251 | 70.5342 | 0 | 0.0002 | 520874.088 | 6736.4393
Maximum of Months | 27461.3938 | 43.2558 | 132.7016 | 0 | 0.0004 | 980106.1666 | 11357.8764
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 69251900000 | 39587.109 | 28-JAN-14:00 | 3300.199 | 16310.475 | 7442.456 | 0 | 10442.272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2091.706 | 0 | 0
February | 63126900000 | 41512.362 | 28-FEB-13:00 | 3712.724 | 16310.475 | 7442.456 | 0 | 11931.323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2115.384 | 0 | 0
March | 78142200000 | 47802.007 | 17-MAR-16:10 | 3712.724 | 16310.475 | 7442.456 | 0 | 18302.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2033.582 | 0 | 0
April | 82475800000 | 49607.759 | 01-APR-17:10 | 3712.724 | 16310.475 | 7442.456 | 0 | 20101.051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2041.053 | 0 | 0
May | 94296600000 | 58189.939 | 28-MAY-16:00 | 2475.15 | 16310.475 | 7442.456 | 0 | 30006.246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1955.613 | 0 | 0
June | 108573000000 | 65282.051 | 28-JUN-16:30 | 3712.724 | 16310.475 | 7442.456 | 0 | 35627.792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2188.604 | 0 | 0
July | 118783000000 | 64600.164 | 19-JUL-17:10 | 3712.724 | 16310.475 | 7442.456 | 0 | 34988.514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2145.995 | 0 | 0
August | 115274000000 | 64983.137 | 01-AUG-16:00 | 3712.724 | 16310.475 | 7442.456 | 0 | 35377.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2139.782 | 0 | 0
September | 103098000000 | 59412.888 | 12-SEP-17:10 | 3712.724 | 16310.475 | 7442.456 | 0 | 29882.779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2064.454 | 0 | 0
October | 87597000000 | 49345.349 | 24-OCT-13:00 | 3712.724 | 16310.475 | 7442.456 | 0 | 19756.281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2123.413 | 0 | 0
November | 74019500000 | 47028.66 | 12-NOV-13:00 | 2887.674 | 16310.475 | 7442.456 | 0 | 18331.657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2056.398 | 0 | 0
December | 69344200000 | 38535.422 | 09-DEC-14:00 | 3300.199 | 16310.475 | 7442.456 | 0 | 9392.309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2089.983 | 0 | 0
Annual Sum or Average | 1063980000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 63126900000 | 38535.422 |  | 2475.15 | 16310.475 | 7442.456 | 0 | 9392.309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1955.613 | 0 | 0
Maximum of Months | 118783000000 | 65282.051 |  | 3712.724 | 16310.475 | 7442.456 | 0 | 35627.792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2188.604 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 28507.07 | 8297.44 | 0 | 36804.5
Cost per Total Building Area ($/m2) | 122.69 | 35.71 | 0 | 158.41
Cost per Net Conditioned Building Area ($/m2) | 122.69 | 35.71 | 0 | 158.41
04-Atlanta
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 2053.42 | 8837.9 | 8837.9
Net Site Energy | 2053.42 | 8837.9 | 8837.9
Total Source Energy | 4452.98 | 19165.54 | 19165.54
Net Source Energy | 4452.98 | 19165.54 | 19165.54
Area (m2)
Total Building Area | 232.34
Net Conditioned Building Area | 232.34
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 137.83 | 0 | 0 | 0 | 0
Cooling | 174.9 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 75.06 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 15.73 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 441.62 | 881.7 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 198.79 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 60.91 | 0 | 0 | 0 | 413.75
Refrigeration | 66.9 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 972.99 | 1080.43 | 0 | 0 | 0 | 413.75
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 972.99 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 972.99 | 100
Total On-Site and Utility Electric Sources | 972.99 | 100
Total Electricity End Uses | 972.99 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS | 0.22 | 0.505 | 0.55 | 46.47 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 116.17 | 0 | 180
KITCHEN_WALL_NORTH | EXT-WALLS | 0.22 | 0.505 | 0.55 | 46.47 | 0 | 90 | N
KITCHEN_WALL_EAST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 90 | 90 | E
KITCHEN_WALL_WEST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 116.17 | 0 | 180
WEST-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 27.38 | 270 | 45
EAST-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 27.38 | 90 | 45
NORTH-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 102.05 | 0 | 18.44
SOUTH-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 102.05 | 180 | 18.44
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
DINING_WALL_EAST_WINDOW | WINDOW_EAST | 6.51 | 3.24 | 0.25 | 0.318 | No | DINING_WALL_EAST
DINING_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 13.01 | 3.24 | 0.25 | 0.318 | No | DINING_WALL_SOUTH
DINING_WALL_WEST_WINDOW | WINDOW_WEST | 6.51 | 3.24 | 0.25 | 0.318 | No | DINING_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 35141.19 | 2.96
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 58597.96 | 2.78
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.83 | 0.01 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.01 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 1.42 | 2683.45 | 1 | Fan Energy
PSZ-AC_2:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.36 | 4474.66 | 1 | Fan Energy
Nominal Capacity [W]
PSZ-AC_1:1_HEATC | 23407.01
PSZ-AC_2:2_HEATC | 39031.21
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 19409.4694 | 30.9442 | 65.4098 | 0 | 0.0003 | 116292.7205 | 7948.3653
February | 17401.3278 | 27.9733 | 59.7732 | 0 | 0.0002 | 106274.3596 | 7147.3154
March | 18365.193 | 30.5768 | 68.2509 | 0 | 0.0003 | 121361.1866 | 7640.5489
April | 18883.4187 | 32.0854 | 73.3427 | 0 | 0.0003 | 130422.9811 | 7915.7922
May | 21289.9056 | 36.8385 | 85.9448 | 0 | 0.0003 | 152840.5782 | 8985.9038
June | 22581.81 | 39.5062 | 93.2796 | 0 | 0.0003 | 165889.3066 | 9571.1137
July | 24780.4993 | 43.6353 | 103.7468 | 0 | 0.0004 | 184507.4043 | 10529.1031
August | 24290.1731 | 42.6879 | 101.2819 | 0 | 0.0004 | 180122.7888 | 10313.0022
September | 22112.1378 | 38.6046 | 90.9476 | 0 | 0.0003 | 161741.2434 | 9364.6643
October | 19425.1982 | 33.1198 | 76.0048 | 0 | 0.0003 | 135158.395 | 8153.4135
November | 17734.8972 | 29.3778 | 65.1751 | 0 | 0.0002 | 115890.1395 | 7364.5073
December | 18971.5343 | 30.6266 | 65.7997 | 0 | 0.0003 | 116990.9241 | 7804.1755
Annual Sum or Average | 245245.5645 | 415.9764 | 948.9567 | 0 | 0.0036 | 1687492.0276 | 102737.9051
Minimum of Months | 17401.3278 | 27.9733 | 59.7732 | 0 | 0.0002 | 106274.3596 | 7147.3154
Maximum of Months | 24780.4993 | 43.6353 | 103.7468 | 0 | 0.0004 | 184507.4043 | 10529.1031
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 67053300000 | 32968.211 | 23-JAN-13:00 | 3712.724 | 16310.475 | 7158.125 | 0 | 3644.921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2141.966 | 0 | 0
February | 61276800000 | 36228.785 | 18-FEB-13:00 | 3300.199 | 16310.475 | 7158.125 | 0 | 7344.701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2115.284 | 0 | 0
March | 69975700000 | 39816.156 | 28-MAR-12:00 | 3712.724 | 16310.475 | 7158.125 | 0 | 10493.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2141.761 | 0 | 0
April | 75200700000 | 46852.174 | 15-APR-11:20 | 3300.199 | 16310.475 | 7158.125 | 0 | 17197.795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2885.579 | 0 | 0
May | 88126400000 | 52459.962 | 31-MAY-17:30 | 3712.724 | 16310.475 | 7158.125 | 0 | 23180.646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2097.992 | 0 | 0
June | 95650200000 | 56036.83 | 19-JUN-11:09 | 3712.724 | 16310.475 | 7158.125 | 0 | 25940.095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2915.409 | 0 | 0
July | 106385000000 | 60832.807 | 03-JUL-11:00 | 3712.724 | 16310.475 | 7158.125 | 0 | 31486.575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2164.908 | 0 | 0
August | 103857000000 | 58830.381 | 17-AUG-11:20 | 3712.724 | 16310.475 | 7158.125 | 0 | 28717.345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2931.711 | 0 | 0
September | 93258500000 | 53954.872 | 11-SEP-11:20 | 3712.724 | 16310.475 | 7158.125 | 0 | 23841.835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2931.712 | 0 | 0
October | 77931100000 | 48979.855 | 12-OCT-15:00 | 3712.724 | 16310.475 | 7158.125 | 0 | 19727.181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2071.349 | 0 | 0
November | 66821200000 | 40064.418 | 22-NOV-12:20 | 3712.724 | 16310.475 | 7158.125 | 0 | 9974.168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2908.925 | 0 | 0
December | 67455900000 | 37237.594 | 31-DEC-12:20 | 2887.674 | 16310.475 | 7158.125 | 0 | 8003.811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2877.508 | 0 | 0
Annual Sum or Average | 972992000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 61276800000 | 32968.211 |  | 2887.674 | 16310.475 | 7158.125 | 0 | 3644.921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2071.349 | 0 | 0
Maximum of Months | 106385000000 | 60832.807 |  | 3712.724 | 16310.475 | 7158.125 | 0 | 31486.575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2931.712 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 28454.56 | 11684.21 | 0 | 40138.76
Cost per Total Building Area ($/m2) | 122.47 | 50.29 | 0 | 172.76
Cost per Net Conditioned Building Area ($/m2) | 122.47 | 50.29 | 0 | 172.76
05-Los Angeles
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 1791.62 | 7711.1 | 7711.1
Net Site Energy | 1791.62 | 7711.1 | 7711.1
Total Source Energy | 3629.75 | 15622.39 | 15622.39
Net Source Energy | 3629.75 | 15622.39 | 15622.39
Area (m2)
Total Building Area | 232.34
Net Conditioned Building Area | 232.34
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 15.36 | 0 | 0 | 0 | 0
Cooling | 38.61 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 75.06 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 15.71 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 441.62 | 881.7 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 196.44 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 59.16 | 0 | 0 | 0 | 413.75
Refrigeration | 67.95 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 835.4 | 956.22 | 0 | 0 | 0 | 413.75
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 835.4 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 835.4 | 100
Total On-Site and Utility Electric Sources | 835.4 | 100
Total Electricity End Uses | 835.4 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS | 0.22 | 0.505 | 0.55 | 46.47 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 116.17 | 0 | 180
KITCHEN_WALL_NORTH | EXT-WALLS | 0.22 | 0.505 | 0.55 | 46.47 | 0 | 90 | N
KITCHEN_WALL_EAST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 90 | 90 | E
KITCHEN_WALL_WEST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 116.17 | 0 | 180
WEST-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 27.38 | 270 | 45
EAST-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 27.38 | 90 | 45
NORTH-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 102.05 | 0 | 18.44
SOUTH-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 102.05 | 180 | 18.44
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
DINING_WALL_EAST_WINDOW | WINDOW_EAST | 6.51 | 3.24 | 0.25 | 0.318 | No | DINING_WALL_EAST
DINING_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 13.01 | 3.24 | 0.25 | 0.318 | No | DINING_WALL_SOUTH
DINING_WALL_WEST_WINDOW | WINDOW_WEST | 6.51 | 3.24 | 0.25 | 0.318 | No | DINING_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 24460.12 | 2.96
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 39062.08 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.83 | 0.01 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.01 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 1.34 | 2545.53 | 1 | Fan Energy
PSZ-AC_2:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.36 | 4474.66 | 1 | Fan Energy
Nominal Capacity [W]
PSZ-AC_1:1_HEATC | 16216.03
PSZ-AC_2:2_HEATC | 28505.35
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 10230.9853 | 8.9823 | 54.8173 | 0 | 0 | 330624.0267 | 3708.2068
February | 9216.7432 | 8.0917 | 49.4045 | 0 | 0 | 297976.9687 | 3340.6614
March | 10183.022 | 8.9374 | 55.0631 | 0 | 0 | 332109.0045 | 3692.3563
April | 9870.0619 | 8.6599 | 53.8677 | 0 | 0 | 324902.1801 | 3580.3933
May | 10277.0336 | 9.0132 | 56.7759 | 0 | 0 | 342446.7214 | 3730.1197
June | 9978.9862 | 8.75 | 55.4436 | 0 | 0 | 334412.5005 | 3622.9001
July | 10664.3528 | 9.3427 | 60.7383 | 0 | 0 | 366356.2515 | 3876.2605
August | 10880.4283 | 9.5277 | 62.7381 | 0 | 0 | 378423.0099 | 3957.1461
September | 10357.7528 | 9.0737 | 59.0668 | 0 | 0 | 356274.5983 | 3765.046
October | 10378.5123 | 9.0996 | 57.7961 | 0 | 0 | 348602.516 | 3768.3541
November | 9917.6944 | 8.7007 | 54.316 | 0 | 0 | 327607.3096 | 3598.2468
December | 10267.5765 | 9.0118 | 55.4815 | 0 | 0 | 334632.5534 | 3722.8974
Annual Sum or Average | 122223.1493 | 107.1908 | 675.5088 | 0 | 0.0004 | 4074367.6406 | 44362.5885
Minimum of Months | 9216.7432 | 8.0917 | 49.4045 | 0 | 0 | 297976.9687 | 3340.6614
Maximum of Months | 10880.4283 | 9.5277 | 62.7381 | 0 | 0 | 378423.0099 | 3957.1461
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 67790300000 | 41585.339 | 26-JAN-12:00 | 3712.724 | 16310.475 | 7020.202 | 0 | 12456.709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2085.228 | 0 | 0
February | 61096500000 | 41906.931 | 12-FEB-12:20 | 2887.674 | 16310.475 | 7020.202 | 0 | 12851.581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2836.999 | 0 | 0
March | 68094800000 | 40973.549 | 04-MAR-12:20 | 3300.199 | 16310.475 | 7020.202 | 0 | 11494.767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2847.906 | 0 | 0
April | 66617200000 | 41766.934 | 11-APR-16:10 | 3712.724 | 16310.475 | 7020.202 | 0 | 12687.322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2036.211 | 0 | 0
May | 70214400000 | 43467.155 | 30-MAY-11:09 | 3712.724 | 16310.475 | 7020.202 | 0 | 13506.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2917.174 | 0 | 0
June | 68567100000 | 42029.336 | 28-JUN-11:20 | 3712.724 | 16310.475 | 7020.202 | 0 | 12073.501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2912.433 | 0 | 0
July | 75116800000 | 44551.202 | 29-JUL-10:09 | 3300.199 | 16310.475 | 7020.202 | 0 | 13346.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4574.217 | 0 | 0
August | 77590900000 | 48028.65 | 08-AUG-10:09 | 3712.724 | 16310.475 | 7020.202 | 0 | 16392.914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4592.334 | 0 | 0
September | 73049700000 | 49316.228 | 24-SEP-10:00 | 2887.674 | 16310.475 | 7020.202 | 0 | 20272.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2825.147 | 0 | 0
October | 71476600000 | 45287.34 | 19-OCT-10:00 | 3712.724 | 16310.475 | 7020.202 | 0 | 15373.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2870.934 | 0 | 0
November | 67171800000 | 42503.472 | 20-NOV-12:20 | 3712.724 | 16310.475 | 7020.202 | 0 | 12570.974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2889.097 | 0 | 0
December | 68612200000 | 42383.581 | 19-DEC-12:20 | 3712.724 | 16310.475 | 7020.202 | 0 | 12474.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2866.107 | 0 | 0
Annual Sum or Average | 835398000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 61096500000 | 40973.549 |  | 2887.674 | 16310.475 | 7020.202 | 0 | 11494.767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2036.211 | 0 | 0
Maximum of Months | 77590900000 | 49316.228 |  | 3712.724 | 16310.475 | 7020.202 | 0 | 20272.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4592.334 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 29119.17 | 8024.09 | 0 | 37143.26
Cost per Total Building Area ($/m2) | 125.33 | 34.54 | 0 | 159.86
Cost per Net Conditioned Building Area ($/m2) | 125.33 | 34.54 | 0 | 159.86
06-Las Vegas
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 1968.89 | 8474.07 | 8474.07
Net Site Energy | 1968.89 | 8474.07 | 8474.07
Total Source Energy | 4581.83 | 19720.14 | 19720.14
Net Source Energy | 4581.83 | 19720.14 | 19720.14
Area (m2)
Total Building Area | 232.34
Net Conditioned Building Area | 232.34
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 55.59 | 0 | 0 | 0 | 0
Cooling | 172.61 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 75.06 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 15.71 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 441.62 | 881.7 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 207.15 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 53.01 | 0 | 0 | 0 | 413.75
Refrigeration | 66.44 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 978.59 | 990.3 | 0 | 0 | 0 | 413.75
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 978.59 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 978.59 | 100
Total On-Site and Utility Electric Sources | 978.59 | 100
Total Electricity End Uses | 978.59 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS | 0.22 | 0.505 | 0.55 | 46.47 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 116.17 | 0 | 180
KITCHEN_WALL_NORTH | EXT-WALLS | 0.22 | 0.505 | 0.55 | 46.47 | 0 | 90 | N
KITCHEN_WALL_EAST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 90 | 90 | E
KITCHEN_WALL_WEST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 116.17 | 0 | 180
WEST-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 27.38 | 270 | 45
EAST-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 27.38 | 90 | 45
NORTH-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 102.05 | 0 | 18.44
SOUTH-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 102.05 | 180 | 18.44
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
DINING_WALL_EAST_WINDOW | WINDOW_EAST | 6.51 | 3.24 | 0.25 | 0.318 | No | DINING_WALL_EAST
DINING_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 13.01 | 3.24 | 0.25 | 0.318 | No | DINING_WALL_SOUTH
DINING_WALL_WEST_WINDOW | WINDOW_WEST | 6.51 | 3.24 | 0.25 | 0.318 | No | DINING_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 34603.03 | 2.96
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 39062.08 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.83 | 0.01 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.01 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 1.58 | 2989.95 | 1 | Fan Energy
PSZ-AC_2:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.36 | 4474.66 | 1 | Fan Energy
Nominal Capacity [W]
PSZ-AC_1:1_HEATC | 22050.58
PSZ-AC_2:2_HEATC | 33000.16
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 20280.8601 | 29.3716 | 103.1133 | 0 | 0.0002 | 514117.8229 | 8158.6347
February | 17718.6687 | 26.0525 | 93.7667 | 0 | 0.0002 | 467534.8841 | 7168.6068
March | 19793.4884 | 29.1379 | 105.0736 | 0 | 0.0002 | 523914.3464 | 8011.652
April | 20804.0713 | 31.1418 | 115.2903 | 0 | 0.0002 | 574879.8848 | 8474.3513
May | 22979.8594 | 34.66 | 129.803 | 0 | 0.0003 | 647257.1946 | 9387.7881
June | 25919.8138 | 39.6149 | 151.3036 | 0 | 0.0003 | 754491.3093 | 10642.9447
July | 28249.3628 | 43.3537 | 166.5784 | 0 | 0.0003 | 830668.1004 | 11618.019
August | 27866.9643 | 42.7235 | 163.9165 | 0 | 0.0003 | 817392.4781 | 11456.2508
September | 24601.0902 | 37.4475 | 142.1774 | 0 | 0.0003 | 708975.9972 | 10085.6681
October | 21571.5071 | 32.3291 | 119.9049 | 0 | 0.0002 | 597892.0466 | 8790.9598
November | 18955.978 | 27.9704 | 101.242 | 0 | 0.0002 | 504812.6589 | 7679.4535
December | 20002.7836 | 29.1484 | 103.3871 | 0 | 0.0002 | 515491.695 | 8065.4315
Annual Sum or Average | 268744.4477 | 402.9514 | 1495.5568 | 0 | 0.0029 | 7457428.4185 | 109539.7605
Minimum of Months | 17718.6687 | 26.0525 | 93.7667 | 0 | 0.0002 | 467534.8841 | 7168.6068
Maximum of Months | 28249.3628 | 43.3537 | 166.5784 | 0 | 0.0003 | 830668.1004 | 11618.019
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 67464600000 | 32000.951 | 19-JAN-11:09 | 3712.724 | 16310.475 | 7464.623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4513.129 | 0 | 0
February | 61351800000 | 34641.909 | 08-FEB-13:00 | 3712.724 | 16310.475 | 7464.623 | 0 | 5046.916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2107.171 | 0 | 0
March | 68750200000 | 39256.957 | 31-MAR-12:00 | 3712.724 | 16310.475 | 7464.623 | 0 | 9661.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2108.004 | 0 | 0
April | 75438100000 | 47322.058 | 21-APR-17:10 | 3712.724 | 16310.475 | 7464.623 | 0 | 17792.922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2041.314 | 0 | 0
May | 84935700000 | 51938.185 | 31-MAY-16:10 | 3712.724 | 16310.475 | 7464.623 | 0 | 22421.306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2029.057 | 0 | 0
June | 99007400000 | 58916.033 | 27-JUN-15:00 | 3712.724 | 16310.475 | 7464.623 | 0 | 29229.863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2198.347 | 0 | 0
July | 109004000000 | 58120.001 | 24-JUL-16:10 | 3712.724 | 16310.475 | 7464.623 | 0 | 28511.134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2121.044 | 0 | 0
August | 107262000000 | 57321.74 | 04-AUG-16:10 | 3712.724 | 16310.475 | 7464.623 | 0 | 27716.095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2117.823 | 0 | 0
September | 93034700000 | 55734.772 | 01-SEP-14:00 | 3712.724 | 16310.475 | 7464.623 | 0 | 26090.143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2156.807 | 0 | 0
October | 78457800000 | 48420.297 | 06-OCT-11:09 | 3712.724 | 16310.475 | 7464.623 | 0 | 18042.759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2889.716 | 0 | 0
November | 66243600000 | 36708.054 | 10-NOV-12:20 | 3712.724 | 16310.475 | 7464.623 | 0 | 6356.139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2864.092 | 0 | 0
December | 67644900000 | 36478.652 | 05-DEC-13:00 | 3712.724 | 16310.475 | 7464.623 | 0 | 6884.239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2106.59 | 0 | 0
Annual Sum or Average | 978594000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 61351800000 | 32000.951 |  | 3712.724 | 16310.475 | 7464.623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2029.057 | 0 | 0
Maximum of Months | 109004000000 | 58916.033 |  | 3712.724 | 16310.475 | 7464.623 | 0 | 29229.863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4513.129 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 25488.09 | 8125.4 | 0 | 33613.49
Cost per Total Building Area ($/m2) | 109.7 | 34.97 | 0 | 144.67
Cost per Net Conditioned Building Area ($/m2) | 109.7 | 34.97 | 0 | 144.67
07-San Francisco
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 1815.81 | 7815.21 | 7815.21
Net Site Energy | 1815.81 | 7815.21 | 7815.21
Total Source Energy | 3593.29 | 15465.46 | 15465.46
Net Source Energy | 3593.29 | 15465.46 | 15465.46
Area (m2)
Total Building Area | 232.34
Net Conditioned Building Area | 232.34
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 63.25 | 0 | 0 | 0 | 0
Cooling | 11.46 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 75.06 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 15.72 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 441.62 | 881.7 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 194.13 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 66.86 | 0 | 0 | 0 | 413.75
Refrigeration | 66.01 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 804.01 | 1011.8 | 0 | 0 | 0 | 413.75
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 804.01 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 804.01 | 100
Total On-Site and Utility Electric Sources | 804.01 | 100
Total Electricity End Uses | 804.01 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS | 0.22 | 0.505 | 0.55 | 46.47 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 116.17 | 0 | 180
KITCHEN_WALL_NORTH | EXT-WALLS | 0.22 | 0.505 | 0.55 | 46.47 | 0 | 90 | N
KITCHEN_WALL_EAST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 90 | 90 | E
KITCHEN_WALL_WEST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 116.17 | 0 | 180
WEST-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 27.38 | 270 | 45
EAST-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 27.38 | 90 | 45
NORTH-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 102.05 | 0 | 18.44
SOUTH-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 102.05 | 180 | 18.44
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
DINING_WALL_EAST_WINDOW | WINDOW_EAST | 6.51 | 6.88 | 0.39 | 0.39 | No | DINING_WALL_EAST
DINING_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 13.01 | 6.88 | 0.39 | 0.39 | No | DINING_WALL_SOUTH
DINING_WALL_WEST_WINDOW | WINDOW_WEST | 6.51 | 6.88 | 0.39 | 0.39 | No | DINING_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 24137.44 | 2.96
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 39062.08 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.83 | 0.01 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.01 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 1.44 | 2728.45 | 1 | Fan Energy
PSZ-AC_2:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.36 | 4474.66 | 1 | Fan Energy
Nominal Capacity [W]
PSZ-AC_1:1_HEATC | 19212.04
PSZ-AC_2:2_HEATC | 31507.83
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 10865.4782 | 9.5624 | 54.1049 | 0 | 0 | 326303.1914 | 3925.6322
February | 9377.3436 | 8.2394 | 49.0693 | 0 | 0 | 295948.8429 | 3395.223
March | 10420.3653 | 9.1581 | 54.1228 | 0 | 0 | 326425.3156 | 3771.6326
April | 9975.7197 | 8.7625 | 52.6907 | 0 | 0 | 317792.7582 | 3613.3705
May | 10235.9353 | 8.9864 | 54.8926 | 0 | 0 | 331078.4987 | 3710.1497
June | 9900.0862 | 8.6884 | 53.6627 | 0 | 0 | 323663.7671 | 3590.1594
July | 10303.9881 | 9.0388 | 56.5683 | 0 | 0 | 341192.8152 | 3738.8154
August | 10331.6038 | 9.0629 | 56.7442 | 0 | 0 | 342253.6424 | 3748.9097
September | 10085.1289 | 8.8446 | 55.7594 | 0 | 0 | 336315.916 | 3660.5998
October | 10263.7373 | 9.0067 | 55.7785 | 0 | 0 | 336425.7796 | 3722.4748
November | 9929.6297 | 8.721 | 52.6189 | 0 | 0 | 317361.2972 | 3597.1999
December | 10709.1698 | 9.4203 | 54.1376 | 0 | 0 | 326505.1581 | 3871.6332
Annual Sum or Average | 122398.1858 | 107.4914 | 650.1501 | 0 | 0.0004 | 3921266.9822 | 44345.8003
Minimum of Months | 9377.3436 | 8.2394 | 49.0693 | 0 | 0 | 295948.8429 | 3395.223
Maximum of Months | 10865.4782 | 9.5624 | 56.7442 | 0 | 0 | 342253.6424 | 3925.6322
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 66904400000 | 31714.739 | 05-JAN-11:09 | 3712.724 | 16310.475 | 7203.116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4488.424 | 0 | 0
February | 60680600000 | 34236.443 | 14-FEB-12:00 | 3712.724 | 16310.475 | 7203.116 | 0 | 4911.319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2098.808 | 0 | 0
March | 66929500000 | 31735.86 | 01-MAR-11:20 | 3712.724 | 16310.475 | 7203.116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4509.545 | 0 | 0
April | 65159500000 | 37280.006 | 29-APR-12:00 | 3300.199 | 16310.475 | 7203.116 | 0 | 8349.595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2116.621 | 0 | 0
May | 67883500000 | 39369.005 | 17-MAY-13:00 | 3712.724 | 16310.475 | 7203.116 | 0 | 9988.209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2154.48 | 0 | 0
June | 66363200000 | 42060.828 | 16-JUN-11:20 | 3712.724 | 16310.475 | 7203.116 | 0 | 11935.992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2898.521 | 0 | 0
July | 69957300000 | 48042.975 | 02-JUL-12:00 | 2887.674 | 16310.475 | 7203.116 | 0 | 19531.421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2110.289 | 0 | 0
August | 70174900000 | 44552.488 | 15-AUG-11:20 | 3712.724 | 16310.475 | 7203.116 | 0 | 14418.826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2907.346 | 0 | 0
September | 68957400000 | 47624.779 | 28-SEP-14:00 | 3712.724 | 16310.475 | 7203.116 | 0 | 18261.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2137.432 | 0 | 0
October | 68979900000 | 39705.642 | 31-OCT-12:00 | 3712.724 | 16310.475 | 7203.116 | 0 | 10351.648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2127.679 | 0 | 0
November | 65071000000 | 31758.335 | 08-NOV-11:09 | 3712.724 | 16310.475 | 7203.116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4532.019 | 0 | 0
December | 66945800000 | 31715.816 | 04-DEC-11:20 | 3712.724 | 16310.475 | 7203.116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4489.501 | 0 | 0
Annual Sum or Average | 804007000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 60680600000 | 31714.739 |  | 2887.674 | 16310.475 | 7203.116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2098.808 | 0 | 0
Maximum of Months | 70174900000 | 48042.975 |  | 3712.724 | 16310.475 | 7203.116 | 0 | 19531.421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4532.019 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 32662.84 | 8504.27 | 0 | 41167.11
Cost per Total Building Area ($/m2) | 140.58 | 36.6 | 0 | 177.18
Cost per Net Conditioned Building Area ($/m2) | 140.58 | 36.6 | 0 | 177.18
08-Baltimore
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 2165.2 | 9318.98 | 9318.98
Net Site Energy | 2165.2 | 9318.98 | 9318.98
Total Source Energy | 4683.72 | 20158.65 | 20158.65
Net Source Energy | 4683.72 | 20158.65 | 20158.65
Area (m2)
Total Building Area | 232.34
Net Conditioned Building Area | 232.34
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 281.82 | 0 | 0 | 0 | 0
Cooling | 137.08 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 75.06 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 15.71 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 441.62 | 881.7 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 198.64 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 67.98 | 0 | 0 | 0 | 413.75
Refrigeration | 65.59 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 933.7 | 1231.5 | 0 | 0 | 0 | 413.75
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 933.7 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 933.7 | 100
Total On-Site and Utility Electric Sources | 933.7 | 100
Total Electricity End Uses | 933.7 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS | 0.22 | 0.505 | 0.55 | 46.47 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 116.17 | 0 | 180
KITCHEN_WALL_NORTH | EXT-WALLS | 0.22 | 0.505 | 0.55 | 46.47 | 0 | 90 | N
KITCHEN_WALL_EAST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 90 | 90 | E
KITCHEN_WALL_WEST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 116.17 | 0 | 180
WEST-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 27.38 | 270 | 45
EAST-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 27.38 | 90 | 45
NORTH-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 102.05 | 0 | 18.44
SOUTH-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 102.05 | 180 | 18.44
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
DINING_WALL_EAST_WINDOW | WINDOW_EAST | 6.51 | 3.24 | 0.39 | 0.495 | No | DINING_WALL_EAST
DINING_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 13.01 | 3.24 | 0.39 | 0.495 | No | DINING_WALL_SOUTH
DINING_WALL_WEST_WINDOW | WINDOW_WEST | 6.51 | 3.24 | 0.39 | 0.495 | No | DINING_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 36322.06 | 2.96
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 58597.96 | 2.78
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.83 | 0.01 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.01 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 1.46 | 2773.63 | 1 | Fan Energy
PSZ-AC_2:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.36 | 4474.66 | 1 | Fan Energy
Nominal Capacity [W]
PSZ-AC_1:1_HEATC | 26931.78
PSZ-AC_2:2_HEATC | 43448.73
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 19788.4341 | 30.2368 | 67.8594 | 0 | 0.0003 | 4217.8023 | 7971.1874
February | 17200.4243 | 26.6877 | 61.2228 | 0 | 0.0003 | 3805.5113 | 6965.75
March | 17321.4337 | 28.2531 | 69.2606 | 0 | 0.0003 | 4305.81 | 7140.7284
April | 15744.2594 | 26.5116 | 67.5425 | 0 | 0.0003 | 4199.3697 | 6566.5246
May | 17568.4763 | 30.4246 | 80.0132 | 0 | 0.0003 | 4975.0616 | 7404.2759
June | 19605.3467 | 34.7781 | 93.8515 | 0 | 0.0004 | 5835.8227 | 8338.2613
July | 21625.074 | 38.7044 | 105.4164 | 0 | 0.0004 | 6555.0713 | 9228.6665
August | 21632.2636 | 38.7201 | 105.4674 | 0 | 0.0004 | 6558.2425 | 9231.9986
September | 17995.5478 | 31.5568 | 84.1264 | 0 | 0.0003 | 5230.9644 | 7620.1709
October | 17216.9489 | 29.4098 | 76.1705 | 0 | 0.0003 | 4735.9744 | 7219.0015
November | 16624.7276 | 27.4394 | 68.2567 | 0 | 0.0003 | 4243.5408 | 6883.0208
December | 18793.705 | 29.3455 | 67.9193 | 0 | 0.0003 | 4221.8444 | 7627.9696
Annual Sum or Average | 221116.6414 | 372.0678 | 947.1065 | 0 | 0.0039 | 58885.0153 | 92197.5554
Minimum of Months | 15744.2594 | 26.5116 | 61.2228 | 0 | 0.0003 | 3805.5113 | 6566.5246
Maximum of Months | 21632.2636 | 38.7201 | 105.4674 | 0 | 0.0004 | 6558.2425 | 9231.9986
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 66879200000 | 31863.927 | 09-JAN-11:09 | 3712.724 | 16310.475 | 7248.299 | 0 | 70.836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4521.593 | 0 | 0
February | 60341700000 | 31705.873 | 13-FEB-11:09 | 3712.724 | 16310.475 | 7248.299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4434.374 | 0 | 0
March | 68274700000 | 42911.815 | 09-MAR-13:00 | 3712.724 | 16310.475 | 7248.299 | 0 | 13480.362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2159.955 | 0 | 0
April | 66586900000 | 42105.063 | 04-APR-16:10 | 3712.724 | 16310.475 | 7248.299 | 0 | 12756.761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2076.803 | 0 | 0
May | 78886600000 | 51190.736 | 15-MAY-12:00 | 3712.724 | 16310.475 | 7248.299 | 0 | 21756.507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2162.731 | 0 | 0
June | 92535200000 | 60397.261 | 30-JUN-16:00 | 3712.724 | 16310.475 | 7248.299 | 0 | 30960.861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2164.902 | 0 | 0
July | 103940000000 | 63544.36 | 25-JUL-10:20 | 3712.724 | 16310.475 | 7248.299 | 0 | 31680.527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4592.334 | 0 | 0
August | 103990000000 | 62436.83 | 17-AUG-11:20 | 3712.724 | 16310.475 | 7248.299 | 0 | 32233.597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2931.735 | 0 | 0
September | 82944300000 | 53416.215 | 05-SEP-11:20 | 3712.724 | 16310.475 | 7248.299 | 0 | 23212.991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2931.726 | 0 | 0
October | 75095500000 | 50520.278 | 03-OCT-11:20 | 3712.724 | 16310.475 | 7248.299 | 0 | 20317.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2931.72 | 0 | 0
November | 67287300000 | 47291.519 | 04-NOV-12:20 | 3300.199 | 16310.475 | 7248.299 | 0 | 17518.938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2913.607 | 0 | 0
December | 66943300000 | 31699.79 | 08-DEC-11:09 | 3712.724 | 16310.475 | 7248.299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4428.292 | 0 | 0
Annual Sum or Average | 933705000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 60341700000 | 31699.79 |  | 3300.199 | 16310.475 | 7248.299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2076.803 | 0 | 0
Maximum of Months | 103990000000 | 63544.36 |  | 3712.724 | 16310.475 | 7248.299 | 0 | 32233.597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4592.334 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 17320.6 | 12401.47 | 0 | 29722.07
Cost per Total Building Area ($/m2) | 74.55 | 53.38 | 0 | 127.92
Cost per Net Conditioned Building Area ($/m2) | 74.55 | 53.38 | 0 | 127.92
09-Albuquerque
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 1987.22 | 8552.97 | 8552.97
Net Site Energy | 1987.22 | 8552.97 | 8552.97
Total Source Energy | 4167.27 | 17935.85 | 17935.85
Net Source Energy | 4167.27 | 17935.85 | 17935.85
Area (m2)
Total Building Area | 232.34
Net Conditioned Building Area | 232.34
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 141.66 | 0 | 0 | 0 | 0
Cooling | 86.67 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 75.06 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 15.72 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 441.62 | 881.7 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 212.62 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 66.64 | 0 | 0 | 0 | 413.75
Refrigeration | 65.54 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 897.22 | 1090 | 0 | 0 | 0 | 413.75
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 897.22 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 897.22 | 100
Total On-Site and Utility Electric Sources | 897.22 | 100
Total Electricity End Uses | 897.22 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS | 0.22 | 0.505 | 0.55 | 46.47 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 116.17 | 0 | 180
KITCHEN_WALL_NORTH | EXT-WALLS | 0.22 | 0.505 | 0.55 | 46.47 | 0 | 90 | N
KITCHEN_WALL_EAST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 90 | 90 | E
KITCHEN_WALL_WEST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 116.17 | 0 | 180
WEST-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 27.38 | 270 | 45
EAST-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 27.38 | 90 | 45
NORTH-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 102.05 | 0 | 18.44
SOUTH-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 102.05 | 180 | 18.44
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
DINING_WALL_EAST_WINDOW | WINDOW_EAST | 6.51 | 3.24 | 0.39 | 0.495 | No | DINING_WALL_EAST
DINING_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 13.01 | 3.24 | 0.39 | 0.495 | No | DINING_WALL_SOUTH
DINING_WALL_WEST_WINDOW | WINDOW_WEST | 6.51 | 3.24 | 0.39 | 0.495 | No | DINING_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 28487.99 | 2.96
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 39062.08 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.83 | 0.01 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.01 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 1.72 | 3263.37 | 1 | Fan Energy
PSZ-AC_2:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.36 | 4474.66 | 1 | Fan Energy
Nominal Capacity [W]
PSZ-AC_1:1_HEATC | 25177.21
PSZ-AC_2:2_HEATC | 34522.4
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 24122.9595 | 37.1215 | 82.5078 | 0 | 0.0003 | 85762.5572 | 9842.3944
February | 21286.1091 | 33.0961 | 74.6458 | 0 | 0.0003 | 77593.2727 | 8718.2942
March | 23195.3312 | 36.3817 | 83.057 | 0 | 0.0003 | 86339.1796 | 9531.3644
April | 22582.4985 | 35.9806 | 83.8944 | 0 | 0.0003 | 87214.2654 | 9334.4865
May | 25233.9161 | 40.6816 | 96.3235 | 0 | 0.0004 | 100138.9322 | 10477.1905
June | 26153.1036 | 42.4675 | 101.4779 | 0 | 0.0004 | 105499.7194 | 10888.6619
July | 28682.3303 | 46.8153 | 112.5952 | 0 | 0.0004 | 117059.501 | 11965.3126
August | 27679.6142 | 45.0552 | 107.9905 | 0 | 0.0004 | 112271.2529 | 11534.8977
September | 24931.9412 | 40.3324 | 95.9158 | 0 | 0.0004 | 99716.0811 | 10365.3104
October | 23452.7986 | 37.4463 | 87.5553 | 0 | 0.0004 | 91020.6486 | 9701.9769
November | 22438.8116 | 35.154 | 80.1256 | 0 | 0.0003 | 83291.6482 | 9216.4661
December | 24255.501 | 37.2468 | 82.5356 | 0 | 0.0003 | 85790.7749 | 9888.7606
Annual Sum or Average | 294014.9149 | 467.779 | 1088.6244 | 0 | 0.0044 | 1131697.8333 | 121465.1163
Minimum of Months | 21286.1091 | 33.0961 | 74.6458 | 0 | 0.0003 | 77593.2727 | 8718.2942
Maximum of Months | 28682.3303 | 46.8153 | 112.5952 | 0 | 0.0004 | 117059.501 | 11965.3126
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 67993600000 | 32224.435 | 27-JAN-11:20 | 3712.724 | 16310.475 | 7738.045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4463.191 | 0 | 0
February | 61516900000 | 34734.157 | 14-FEB-15:00 | 3712.724 | 16310.475 | 7738.045 | 0 | 4867.921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2104.992 | 0 | 0
March | 68450700000 | 35998.093 | 02-MAR-14:00 | 3712.724 | 16310.475 | 7738.045 | 0 | 6122.159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2114.69 | 0 | 0
April | 69144500000 | 43473.521 | 22-APR-13:00 | 3300.199 | 16310.475 | 7738.045 | 0 | 14035.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2088.892 | 0 | 0
May | 79391400000 | 45732.261 | 31-MAY-17:10 | 3712.724 | 16310.475 | 7738.045 | 0 | 15935.947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2035.07 | 0 | 0
June | 83641400000 | 50360.913 | 29-JUN-13:00 | 3712.724 | 16310.475 | 7738.045 | 0 | 20464.495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2135.174 | 0 | 0
July | 92806200000 | 51418.045 | 31-JUL-14:00 | 3712.724 | 16310.475 | 7738.045 | 0 | 21548.804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2107.996 | 0 | 0
August | 89010000000 | 50451.444 | 01-AUG-13:00 | 3712.724 | 16310.475 | 7738.045 | 0 | 20533.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2156.259 | 0 | 0
September | 79056100000 | 45697.723 | 03-SEP-13:00 | 2887.674 | 16310.475 | 7738.045 | 0 | 16663.161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2098.368 | 0 | 0
October | 72162300000 | 42522.164 | 03-OCT-11:20 | 3712.724 | 16310.475 | 7738.045 | 0 | 11878.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2882.521 | 0 | 0
November | 66034600000 | 32689.947 | 08-NOV-14:00 | 3712.724 | 16310.475 | 7738.045 | 0 | 2810.799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2117.904 | 0 | 0
December | 68016000000 | 32195.519 | 13-DEC-11:20 | 3712.724 | 16310.475 | 7738.045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4434.275 | 0 | 0
Annual Sum or Average | 897224000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 61516900000 | 32195.519 |  | 2887.674 | 16310.475 | 7738.045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2035.07 | 0 | 0
Maximum of Months | 92806200000 | 51418.045 |  | 3712.724 | 16310.475 | 7738.045 | 0 | 21548.804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4463.191 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 9396.06 | 7863.98 | 0 | 17260.04
Cost per Total Building Area ($/m2) | 40.44 | 33.85 | 0 | 74.29
Cost per Net Conditioned Building Area ($/m2) | 40.44 | 33.85 | 0 | 74.29
10-Seattle
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 1953.07 | 8405.99 | 8405.99
Net Site Energy | 1953.07 | 8405.99 | 8405.99
Total Source Energy | 2660.64 | 11451.34 | 11451.34
Net Source Energy | 2660.64 | 11451.34 | 11451.34
Area (m2)
Total Building Area | 232.34
Net Conditioned Building Area | 232.34
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 187.59 | 0 | 0 | 0 | 0
Cooling | 18.12 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 75.06 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 15.68 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 441.62 | 881.7 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 196.82 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 71.66 | 0 | 0 | 0 | 413.75
Refrigeration | 64.83 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 812.13 | 1140.95 | 0 | 0 | 0 | 413.75
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 812.13 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 812.13 | 100
Total On-Site and Utility Electric Sources | 812.13 | 100
Total Electricity End Uses | 812.13 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS | 0.22 | 0.505 | 0.55 | 46.47 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 116.17 | 0 | 180
KITCHEN_WALL_NORTH | EXT-WALLS | 0.22 | 0.505 | 0.55 | 46.47 | 0 | 90 | N
KITCHEN_WALL_EAST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 90 | 90 | E
KITCHEN_WALL_WEST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 116.17 | 0 | 180
WEST-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 27.38 | 270 | 45
EAST-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 27.38 | 90 | 45
NORTH-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 102.05 | 0 | 18.44
SOUTH-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 102.05 | 180 | 18.44
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
DINING_WALL_EAST_WINDOW | WINDOW_EAST | 6.51 | 3.24 | 0.39 | 0.495 | No | DINING_WALL_EAST
DINING_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 13.01 | 3.24 | 0.39 | 0.495 | No | DINING_WALL_SOUTH
DINING_WALL_WEST_WINDOW | WINDOW_WEST | 6.51 | 3.24 | 0.39 | 0.495 | No | DINING_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 28215.34 | 2.96
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 39062.08 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.83 | 0.01 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.01 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 1.49 | 2822.2 | 1 | Fan Energy
PSZ-AC_2:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.36 | 4474.66 | 1 | Fan Energy
Nominal Capacity [W]
PSZ-AC_1:1_HEATC | 23698.73
PSZ-AC_2:2_HEATC | 37574.89
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 9648.9594 | 11.0135 | 14.4377 | 0 | 0.0001 | 190407.7595 | 3581.023
February | 8018.6809 | 9.3127 | 13.0203 | 0 | 0.0001 | 171760.754 | 2993.1194
March | 8808.2753 | 10.248 | 14.4188 | 0 | 0.0001 | 190214.7654 | 3289.803
April | 7875.8676 | 9.3268 | 13.9372 | 0 | 0.0001 | 183904.3961 | 2959.0818
May | 7730.5755 | 9.3188 | 14.7275 | 0 | 0.0001 | 194373.3212 | 2922.0635
June | 7413.1252 | 9.0037 | 14.5543 | 0 | 0.0001 | 192102.2512 | 2809.3098
July | 7762.1553 | 9.5168 | 15.8089 | 0 | 0.0001 | 208681.6278 | 2951.1302
August | 7766.848 | 9.53 | 15.8663 | 0 | 0.0001 | 209440.2074 | 2953.716
September | 7512.4485 | 9.1538 | 14.9373 | 0 | 0.0001 | 197163.8889 | 2850.1031
October | 7823.4371 | 9.372 | 14.5298 | 0 | 0.0001 | 191749.8266 | 2950.8791
November | 8529.0072 | 9.9264 | 13.9833 | 0 | 0.0001 | 184469.3148 | 3185.8608
December | 9584.7628 | 10.9569 | 14.4481 | 0 | 0.0001 | 190549.6215 | 3558.9832
Annual Sum or Average | 98474.1426 | 116.6792 | 174.6695 | 0 | 0.0008 | 2304817.7343 | 37005.0728
Minimum of Months | 7413.1252 | 9.0037 | 13.0203 | 0 | 0.0001 | 171760.754 | 2809.3098
Maximum of Months | 9648.9594 | 11.0135 | 15.8663 | 0 | 0.0001 | 209440.2074 | 3581.023
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 67092200000 | 31736.023 | 27-JAN-11:20 | 3712.724 | 16310.475 | 7296.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4415.954 | 0 | 0
February | 60521800000 | 31803.656 | 22-FEB-11:20 | 3712.724 | 16310.475 | 7296.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4483.587 | 0 | 0
March | 67024200000 | 31805.242 | 29-MAR-10:20 | 3712.724 | 16310.475 | 7296.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4485.173 | 0 | 0
April | 64800700000 | 34112.518 | 29-APR-14:00 | 3300.199 | 16310.475 | 7296.87 | 0 | 5071.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2133.923 | 0 | 0
May | 68489500000 | 39012.042 | 06-MAY-12:00 | 3300.199 | 16310.475 | 7296.87 | 0 | 9969.455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2135.043 | 0 | 0
June | 67689300000 | 44115.37 | 18-JUN-11:20 | 2887.674 | 16310.475 | 7296.87 | 0 | 14748.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2871.971 | 0 | 0
July | 73531200000 | 44934.518 | 31-JUL-11:20 | 3712.724 | 16310.475 | 7296.87 | 0 | 14706.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2908.432 | 0 | 0
August | 73798500000 | 42969.003 | 18-AUG-17:19 | 3712.724 | 16310.475 | 7296.87 | 0 | 13566.986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2081.948 | 0 | 0
September | 69472800000 | 51050.366 | 02-SEP-16:10 | 3712.724 | 16310.475 | 7296.87 | 0 | 21665.758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2064.539 | 0 | 0
October | 67565100000 | 35257.234 | 17-OCT-12:00 | 3712.724 | 16310.475 | 7296.87 | 0 | 5810.605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2126.56 | 0 | 0
November | 64999800000 | 31852.237 | 03-NOV-11:09 | 3712.724 | 16310.475 | 7296.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4532.167 | 0 | 0
December | 67142200000 | 31748.525 | 28-DEC-11:09 | 3712.724 | 16310.475 | 7296.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4428.456 | 0 | 0
Annual Sum or Average | 812127000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 60521800000 | 31736.023 |  | 2887.674 | 16310.475 | 7296.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2064.539 | 0 | 0
Maximum of Months | 73798500000 | 51050.366 |  | 3712.724 | 16310.475 | 7296.87 | 0 | 21665.758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4532.167 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 16309.67 | 9463.28 | 0 | 25772.95
Cost per Total Building Area ($/m2) | 70.2 | 40.73 | 0 | 110.93
Cost per Net Conditioned Building Area ($/m2) | 70.2 | 40.73 | 0 | 110.93
11-Chicago
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 2270.71 | 9773.09 | 9773.09
Net Site Energy | 2270.71 | 9773.09 | 9773.09
Total Source Energy | 4645.02 | 19992.11 | 19992.11
Net Source Energy | 4645.02 | 19992.11 | 19992.11
Area (m2)
Total Building Area | 232.34
Net Conditioned Building Area | 232.34
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 432.43 | 0 | 0 | 0 | 0
Cooling | 86.62 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 75.06 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 15.71 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 441.62 | 881.7 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 198.54 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 74.18 | 0 | 0 | 0 | 413.75
Refrigeration | 64.85 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 882.4 | 1388.31 | 0 | 0 | 0 | 413.75
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 882.4 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 882.4 | 100
Total On-Site and Utility Electric Sources | 882.4 | 100
Total Electricity End Uses | 882.4 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS | 0.22 | 0.505 | 0.55 | 46.47 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 116.17 | 0 | 180
KITCHEN_WALL_NORTH | EXT-WALLS | 0.22 | 0.505 | 0.55 | 46.47 | 0 | 90 | N
KITCHEN_WALL_EAST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 90 | 90 | E
KITCHEN_WALL_WEST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 116.17 | 0 | 180
WEST-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 27.38 | 270 | 45
EAST-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 27.38 | 90 | 45
NORTH-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 102.05 | 0 | 18.44
SOUTH-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 102.05 | 180 | 18.44
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
DINING_WALL_EAST_WINDOW | WINDOW_EAST | 6.51 | 3.24 | 0.39 | 0.495 | No | DINING_WALL_EAST
DINING_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 13.01 | 3.24 | 0.39 | 0.495 | No | DINING_WALL_SOUTH
DINING_WALL_WEST_WINDOW | WINDOW_WEST | 6.51 | 3.24 | 0.39 | 0.495 | No | DINING_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 36943.48 | 2.96
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 58597.96 | 2.78
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.83 | 0.01 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.01 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 1.49 | 2821.08 | 1 | Fan Energy
PSZ-AC_2:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.36 | 4474.66 | 1 | Fan Energy
Nominal Capacity [W]
PSZ-AC_1:1_HEATC | 32000.14
PSZ-AC_2:2_HEATC | 50757.08
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 33034.7796 | 50.9077 | 125.5581 | 0 | 0.0004 | 28892.9101 | 13433.7419
February | 28796.224 | 44.9833 | 113.0893 | 0 | 0.0004 | 26024.7725 | 11768.1852
March | 30419.7306 | 48.5149 | 125.4331 | 0 | 0.0004 | 28867.2071 | 12526.8489
April | 27367.218 | 45.1871 | 122.0813 | 0 | 0.0004 | 28098.4629 | 11417.1124
May | 29784.4595 | 50.2155 | 139.0816 | 0 | 0.0004 | 32012.938 | 12524.7031
June | 32906.2598 | 56.1843 | 157.889 | 0 | 0.0005 | 36342.9915 | 13904.9183
July | 36700.5283 | 63.007 | 178.1584 | 0 | 0.0005 | 41009.1351 | 15541.1489
August | 35082.1881 | 60.0604 | 169.2939 | 0 | 0.0005 | 38968.4062 | 14839.7636
September | 30156.7635 | 51.1632 | 142.7386 | 0 | 0.0004 | 32855.1908 | 12711.8608
October | 28683.756 | 47.8645 | 130.9732 | 0 | 0.0004 | 30145.8549 | 12014.4998
November | 28750.8608 | 46.5066 | 122.4678 | 0 | 0.0004 | 28185.8992 | 11902.0671
December | 32164.3397 | 50.102 | 125.4614 | 0 | 0.0004 | 28871.6492 | 13130.9959
Annual Sum or Average | 373847.1079 | 614.6966 | 1652.2257 | 0 | 0.0051 | 380275.4174 | 155715.8459
Minimum of Months | 27367.218 | 44.9833 | 113.0893 | 0 | 0.0004 | 26024.7725 | 11417.1124
Maximum of Months | 36700.5283 | 63.007 | 178.1584 | 0 | 0.0005 | 41009.1351 | 15541.1489
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 67043800000 | 31726.428 | 17-JAN-11:20 | 3712.724 | 16310.475 | 7295.752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4407.477 | 0 | 0
February | 60388500000 | 31852.226 | 28-FEB-11:20 | 3712.724 | 16310.475 | 7295.752 | 0 | 96.838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4436.437 | 0 | 0
March | 66984200000 | 35426.117 | 31-MAR-14:00 | 3712.724 | 16310.475 | 7295.752 | 0 | 5984.896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2122.269 | 0 | 0
April | 65200400000 | 36242.554 | 07-APR-13:00 | 3712.724 | 16310.475 | 7295.752 | 0 | 6778.838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2144.764 | 0 | 0
May | 74283600000 | 50202.899 | 30-MAY-16:10 | 3712.724 | 16310.475 | 7295.752 | 0 | 20722.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2161.028 | 0 | 0
June | 84331200000 | 60817.02 | 08-JUN-12:00 | 3712.724 | 16310.475 | 7295.752 | 0 | 31332.919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2165.15 | 0 | 0
July | 95158600000 | 61932.927 | 14-JUL-11:20 | 3712.724 | 16310.475 | 7295.752 | 0 | 31682.257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2931.719 | 0 | 0
August | 90423300000 | 59945.363 | 04-AUG-11:20 | 3712.724 | 16310.475 | 7295.752 | 0 | 29694.684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2931.727 | 0 | 0
September | 76238000000 | 53219.073 | 06-SEP-11:09 | 3712.724 | 16310.475 | 7295.752 | 0 | 22990.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2909.994 | 0 | 0
October | 69951200000 | 46005.493 | 31-OCT-12:20 | 3712.724 | 16310.475 | 7295.752 | 0 | 15754.813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2931.729 | 0 | 0
November | 65403300000 | 45969.612 | 02-NOV-12:09 | 3712.724 | 16310.475 | 7295.752 | 0 | 15718.924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2931.736 | 0 | 0
December | 66994500000 | 31762.727 | 12-DEC-11:09 | 3712.724 | 16310.475 | 7295.752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4443.775 | 0 | 0
Annual Sum or Average | 882400000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 60388500000 | 31726.428 |  | 3712.724 | 16310.475 | 7295.752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2122.269 | 0 | 0
Maximum of Months | 95158600000 | 61932.927 |  | 3712.724 | 16310.475 | 7295.752 | 0 | 31682.257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4443.775 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 13021.91 | 12265.97 | 0 | 25287.88
Cost per Total Building Area ($/m2) | 56.05 | 52.79 | 0 | 108.84
Cost per Net Conditioned Building Area ($/m2) | 56.05 | 52.79 | 0 | 108.84
12-Boulder
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 2076.91 | 8938.97 | 8938.97
Net Site Energy | 2076.91 | 8938.97 | 8938.97
Total Source Energy | 4198.44 | 18070 | 18070
Net Source Energy | 4198.44 | 18070 | 18070
Area (m2)
Total Building Area | 232.34
Net Conditioned Building Area | 232.34
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 254.12 | 0 | 0 | 0 | 0
Cooling | 58.62 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 75.06 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 15.7 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 441.62 | 881.7 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 211.45 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 73.86 | 0 | 0 | 0 | 413.75
Refrigeration | 64.78 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 867.23 | 1209.68 | 0 | 0 | 0 | 413.75
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 867.23 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 867.23 | 100
Total On-Site and Utility Electric Sources | 867.23 | 100
Total Electricity End Uses | 867.23 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS | 0.22 | 0.505 | 0.55 | 46.47 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 116.17 | 0 | 180
KITCHEN_WALL_NORTH | EXT-WALLS | 0.22 | 0.505 | 0.55 | 46.47 | 0 | 90 | N
KITCHEN_WALL_EAST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 90 | 90 | E
KITCHEN_WALL_WEST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 116.17 | 0 | 180
WEST-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 27.38 | 270 | 45
EAST-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 27.38 | 90 | 45
NORTH-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 102.05 | 0 | 18.44
SOUTH-ROOF | ROOFS | 0.22 | 0.194 | 0.2 | 102.05 | 180 | 18.44
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
DINING_WALL_EAST_WINDOW | WINDOW_EAST | 6.51 | 3.24 | 0.39 | 0.495 | No | DINING_WALL_EAST
DINING_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 13.01 | 3.24 | 0.39 | 0.495 | No | DINING_WALL_SOUTH
DINING_WALL_WEST_WINDOW | WINDOW_WEST | 6.51 | 3.24 | 0.39 | 0.495 | No | DINING_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 28837.36 | 2.96
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 39062.08 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.83 | 0.01 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.01 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 1.74 | 3303.39 | 1 | Fan Energy
PSZ-AC_2:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.36 | 4474.66 | 1 | Fan Energy
Nominal Capacity [W]
PSZ-AC_1:1_HEATC | 31149.75
PSZ-AC_2:2_HEATC | 42194.36
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 25341.4132 | 38.266 | 82.7212 | 0 | 0.0003 | 85978.175 | 10267.8761
February | 22345.28 | 34.0443 | 74.5787 | 0 | 0.0003 | 77517.766 | 9083.5772
March | 24127.7379 | 37.2686 | 83.2805 | 0 | 0.0003 | 86566.9319 | 9858.0515
April | 22545.5767 | 35.5555 | 81.7748 | 0 | 0.0003 | 85007.9462 | 9283.298
May | 23760.8953 | 37.9242 | 88.6299 | 0 | 0.0004 | 92137.6726 | 9828.0605
June | 24351.0574 | 39.2407 | 92.8581 | 0 | 0.0004 | 96536.1441 | 10108.8978
July | 27352.5099 | 44.4464 | 106.3013 | 0 | 0.0004 | 110514.5321 | 11391.0989
August | 26389.3299 | 42.7531 | 101.8642 | 0 | 0.0004 | 105900.6592 | 10977.4038
September | 23959.1391 | 38.5181 | 90.8711 | 0 | 0.0004 | 94469.6771 | 9937.2734
October | 23556.6701 | 37.3512 | 86.5309 | 0 | 0.0003 | 89953.6865 | 9719.3542
November | 23167.6442 | 35.8306 | 80.2102 | 0 | 0.0003 | 83375.7557 | 9470.192
December | 25422.6397 | 38.3272 | 82.6538 | 0 | 0.0003 | 85907.5766 | 10294.761
Annual Sum or Average | 292319.8935 | 459.5259 | 1052.2749 | 0 | 0.0042 | 1093866.523 | 120219.8442
Minimum of Months | 22345.28 | 34.0443 | 74.5787 | 0 | 0.0003 | 77517.766 | 9083.5772
Maximum of Months | 27352.5099 | 44.4464 | 106.3013 | 0 | 0.0004 | 110514.5321 | 11391.0989
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 68164500000 | 32833.088 | 27-JAN-11:20 | 3712.724 | 16310.475 | 7778.065 | 0 | 509.584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4522.239 | 0 | 0
February | 61457000000 | 32262.297 | 23-FEB-11:20 | 3712.724 | 16310.475 | 7778.065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4461.032 | 0 | 0
March | 68631300000 | 39258.592 | 26-MAR-13:00 | 2887.674 | 16310.475 | 7778.065 | 0 | 10210.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2072.254 | 0 | 0
April | 67395300000 | 40846.533 | 24-APR-11:20 | 3712.724 | 16310.475 | 7778.065 | 0 | 10181.326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2863.942 | 0 | 0
May | 73047900000 | 44610.197 | 23-MAY-11:20 | 3712.724 | 16310.475 | 7778.065 | 0 | 13938.636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2870.297 | 0 | 0
June | 76535000000 | 49987.338 | 28-JUN-11:00 | 3712.724 | 16310.475 | 7778.065 | 0 | 20103.217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2082.856 | 0 | 0
July | 87617300000 | 50885.273 | 17-JUL-11:20 | 3712.724 | 16310.475 | 7778.065 | 0 | 20197.008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2887.001 | 0 | 0
August | 83959300000 | 51302.677 | 30-AUG-12:00 | 3712.724 | 16310.475 | 7778.065 | 0 | 21371.955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2129.457 | 0 | 0
September | 74896700000 | 46636.936 | 02-SEP-14:00 | 3300.199 | 16310.475 | 7778.065 | 0 | 17167.983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2080.213 | 0 | 0
October | 71316400000 | 43395.092 | 05-OCT-11:20 | 3712.724 | 16310.475 | 7778.065 | 0 | 12730.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2862.928 | 0 | 0
November | 66101300000 | 36555.807 | 10-NOV-13:00 | 3712.724 | 16310.475 | 7778.065 | 0 | 6649.454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2105.088 | 0 | 0
December | 68108600000 | 32220.16 | 21-DEC-11:20 | 3712.724 | 16310.475 | 7778.065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4418.895 | 0 | 0
Annual Sum or Average | 867231000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 61457000000 | 32220.16 |  | 2887.674 | 16310.475 | 7778.065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2072.254 | 0 | 0
Maximum of Months | 87617300000 | 51302.677 |  | 3712.724 | 16310.475 | 7778.065 | 0 | 21371.955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4522.239 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 9088.4 | 8693.2 | 0 | 17781.6
Cost per Total Building Area ($/m2) | 39.12 | 37.42 | 0 | 76.53
Cost per Net Conditioned Building Area ($/m2) | 39.12 | 37.42 | 0 | 76.53
13-Minneapolis
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 2452.9 | 10557.25 | 10557.25
Net Site Energy | 2452.9 | 10557.25 | 10557.25
Total Source Energy | 4729.28 | 20354.74 | 20354.74
Net Source Energy | 4729.28 | 20354.74 | 20354.74
Area (m2)
Total Building Area | 232.34
Net Conditioned Building Area | 232.34
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 617.16 | 0 | 0 | 0 | 0
Cooling | 77.78 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 75.06 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 15.7 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 441.62 | 881.7 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 199.92 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 79.55 | 0 | 0 | 0 | 413.75
Refrigeration | 64.42 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 874.5 | 1578.4 | 0 | 0 | 0 | 413.75
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 874.5 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 874.5 | 100
Total On-Site and Utility Electric Sources | 874.5 | 100
Total Electricity End Uses | 874.5 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS | 0.22 | 0.505 | 0.55 | 46.47 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 116.17 | 0 | 180
KITCHEN_WALL_NORTH | EXT-WALLS | 0.22 | 0.505 | 0.55 | 46.47 | 0 | 90 | N
KITCHEN_WALL_EAST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 90 | 90 | E
KITCHEN_WALL_WEST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 116.17 | 0 | 180
WEST-ROOF | ROOFS | 0.22 | 0.154 | 0.16 | 27.38 | 270 | 45
EAST-ROOF | ROOFS | 0.22 | 0.154 | 0.16 | 27.38 | 90 | 45
NORTH-ROOF | ROOFS | 0.22 | 0.154 | 0.16 | 102.05 | 0 | 18.44
SOUTH-ROOF | ROOFS | 0.22 | 0.154 | 0.16 | 102.05 | 180 | 18.44
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
DINING_WALL_EAST_WINDOW | WINDOW_EAST | 6.51 | 3.24 | 0.39 | 0.495 | No | DINING_WALL_EAST
DINING_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 13.01 | 3.24 | 0.39 | 0.495 | No | DINING_WALL_SOUTH
DINING_WALL_WEST_WINDOW | WINDOW_WEST | 6.51 | 3.24 | 0.39 | 0.495 | No | DINING_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 37391.57 | 2.96
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 58597.96 | 2.78
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.83 | 0.01 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.01 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 1.51 | 2855.3 | 1 | Fan Energy
PSZ-AC_2:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.36 | 4474.66 | 1 | Fan Energy
Nominal Capacity [W]
PSZ-AC_1:1_HEATC | 35002.2
PSZ-AC_2:2_HEATC | 54853.48
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 27824.6114 | 38.7951 | 44.2121 | 0 | 0.0003 | 29018.4133 | 10924.2527
February | 23585.006 | 33.5779 | 39.7351 | 0 | 0.0003 | 26084.7704 | 9326.0668
March | 22776.0172 | 34.1511 | 43.9891 | 0 | 0.0003 | 28888.6695 | 9171.0624
April | 19722.6296 | 31.2102 | 43.4236 | 0 | 0.0003 | 28526.6758 | 8098.0938
May | 21200.7978 | 34.6159 | 50.151 | 0 | 0.0004 | 32951.5191 | 8806.9777
June | 22337.276 | 36.9889 | 54.524 | 0 | 0.0004 | 35827.1673 | 9328.5319
July | 24248.0496 | 40.3874 | 59.9513 | 0 | 0.0004 | 39394.4636 | 10148.9177
August | 23889.1357 | 39.7385 | 58.8977 | 0 | 0.0004 | 38701.9104 | 9993.8166
September | 19936.6387 | 32.5663 | 47.2076 | 0 | 0.0004 | 31017.6248 | 8283.2152
October | 20280.7111 | 32.1816 | 44.9395 | 0 | 0.0003 | 29522.9455 | 8335.6703
November | 21891.1693 | 32.9362 | 42.6442 | 0 | 0.0003 | 28006.112 | 8825.4558
December | 26233.7786 | 37.3106 | 44.0727 | 0 | 0.0003 | 28932.0663 | 10369.7884
Annual Sum or Average | 273925.8209 | 424.4598 | 573.7477 | 0 | 0.0044 | 376872.3379 | 111611.8494
Minimum of Months | 19722.6296 | 31.2102 | 39.7351 | 0 | 0.0003 | 26084.7704 | 8098.0938
Maximum of Months | 27824.6114 | 40.3874 | 59.9513 | 0 | 0.0004 | 39394.4636 | 10924.2527
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 67335000000 | 31748.474 | 30-JAN-11:20 | 3712.724 | 16310.475 | 7329.969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4395.306 | 0 | 0
February | 60527700000 | 31744.978 | 21-FEB-11:09 | 3712.724 | 16310.475 | 7329.969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4391.809 | 0 | 0
March | 67034000000 | 31924.473 | 25-MAR-18:30 | 3712.724 | 16310.475 | 7329.969 | 0 | 1369.98 | 1000.172 | 0 | 0 | 0 | 0 | 0 | 0 | 2201.153 | 0 | 0
April | 66194000000 | 39151.005 | 01-APR-17:10 | 3712.724 | 16310.475 | 7329.969 | 0 | 9711.398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2086.439 | 0 | 0
May | 76461500000 | 58151.745 | 27-MAY-14:00 | 3300.199 | 16310.475 | 7329.969 | 0 | 29071.939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2139.162 | 0 | 0
June | 83134200000 | 58317.702 | 29-JUN-11:20 | 3712.724 | 16310.475 | 7329.969 | 0 | 28032.811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2931.722 | 0 | 0
July | 91411900000 | 59730.642 | 15-JUL-14:00 | 3300.199 | 16310.475 | 7329.969 | 0 | 30647.164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2142.835 | 0 | 0
August | 89804900000 | 58965.955 | 27-AUG-14:00 | 2887.674 | 16310.475 | 7329.969 | 0 | 30317.844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2119.992 | 0 | 0
September | 71974100000 | 48480.683 | 14-SEP-12:00 | 3712.724 | 16310.475 | 7329.969 | 0 | 18968.892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2158.622 | 0 | 0
October | 68505800000 | 44451.305 | 08-OCT-14:00 | 2887.674 | 16310.475 | 7329.969 | 0 | 15824.962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2098.225 | 0 | 0
November | 64986100000 | 32681.444 | 02-NOV-14:00 | 3712.724 | 16310.475 | 7329.969 | 0 | 3188.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2140.275 | 0 | 0
December | 67134700000 | 31738.42 | 26-DEC-11:20 | 3712.724 | 16310.475 | 7329.969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4385.252 | 0 | 0
Annual Sum or Average | 874504000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 60527700000 | 31738.42 |  | 2887.674 | 16310.475 | 7329.969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2086.439 | 0 | 0
Maximum of Months | 91411900000 | 59730.642 |  | 3712.724 | 16310.475 | 7329.969 | 0 | 30647.164 | 1000.172 | 0 | 0 | 0 | 0 | 0 | 0 | 4395.306 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 12828.42 | 12576.58 | 0 | 25405
Cost per Total Building Area ($/m2) | 55.21 | 54.13 | 0 | 109.34
Cost per Net Conditioned Building Area ($/m2) | 55.21 | 54.13 | 0 | 109.34
14-Helena
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 2236.91 | 9627.6 | 9627.6
Net Site Energy | 2236.91 | 9627.6 | 9627.6
Total Source Energy | 4439.54 | 19107.71 | 19107.71
Net Source Energy | 4439.54 | 19107.71 | 19107.71
Area (m2)
Total Building Area | 232.34
Net Conditioned Building Area | 232.34
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 437.09 | 0 | 0 | 0 | 0
Cooling | 34.76 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 75.06 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 15.7 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 441.62 | 881.7 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 206.57 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 80.52 | 0 | 0 | 0 | 413.75
Refrigeration | 63.89 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 837.6 | 1399.3 | 0 | 0 | 0 | 413.75
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 837.6 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 837.6 | 100
Total On-Site and Utility Electric Sources | 837.6 | 100
Total Electricity End Uses | 837.6 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS | 0.22 | 0.505 | 0.55 | 46.47 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 116.17 | 0 | 180
KITCHEN_WALL_NORTH | EXT-WALLS | 0.22 | 0.505 | 0.55 | 46.47 | 0 | 90 | N
KITCHEN_WALL_EAST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 90 | 90 | E
KITCHEN_WALL_WEST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 116.17 | 0 | 180
WEST-ROOF | ROOFS | 0.22 | 0.154 | 0.16 | 27.38 | 270 | 45
EAST-ROOF | ROOFS | 0.22 | 0.154 | 0.16 | 27.38 | 90 | 45
NORTH-ROOF | ROOFS | 0.22 | 0.154 | 0.16 | 102.05 | 0 | 18.44
SOUTH-ROOF | ROOFS | 0.22 | 0.154 | 0.16 | 102.05 | 180 | 18.44
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
DINING_WALL_EAST_WINDOW | WINDOW_EAST | 6.51 | 3.24 | 0.39 | 0.495 | No | DINING_WALL_EAST
DINING_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 13.01 | 3.24 | 0.39 | 0.495 | No | DINING_WALL_SOUTH
DINING_WALL_WEST_WINDOW | WINDOW_WEST | 6.51 | 3.24 | 0.39 | 0.495 | No | DINING_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 27696.88 | 2.96
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 39062.08 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.83 | 0.01 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.01 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 1.67 | 3172.75 | 1 | Fan Energy
PSZ-AC_2:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.36 | 4474.66 | 1 | Fan Energy
Nominal Capacity [W]
PSZ-AC_1:1_HEATC | 35441.62
PSZ-AC_2:2_HEATC | 49984.81
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 26126.6224 | 37.6317 | 50.4477 | 0 | 0.0004 | 1195557.0747 | 10387.6789
February | 22684.7754 | 33.1333 | 45.4622 | 0 | 0.0003 | 1077511.2983 | 9063.6142
March | 22720.1392 | 34.5298 | 50.3967 | 0 | 0.0004 | 1194760.5497 | 9207.7399
April | 20748.0067 | 32.2265 | 48.5318 | 0 | 0.0003 | 1150689.3993 | 8475.578
May | 20933.5406 | 33.1402 | 51.2277 | 0 | 0.0004 | 1214727.639 | 8611.8267
June | 21627.3874 | 34.7453 | 54.758 | 0 | 0.0004 | 1298530.3628 | 8946.2432
July | 23488.3553 | 38.0171 | 60.4899 | 0 | 0.0004 | 1434505.798 | 9743.306
August | 22751.1367 | 36.701 | 58.1471 | 0 | 0.0004 | 1378924.3341 | 9425.622
September | 20890.4817 | 33.3911 | 52.2764 | 0 | 0.0004 | 1239651.45 | 8624.9584
October | 21239.6812 | 33.2806 | 50.7323 | 0 | 0.0004 | 1202916.3137 | 8704.5016
November | 22053.8402 | 33.4633 | 48.7237 | 0 | 0.0004 | 1155089.7806 | 8932.4993
December | 25397.3757 | 36.9658 | 50.4301 | 0 | 0.0004 | 1195227.6308 | 10134.9034
Annual Sum or Average | 270661.3424 | 417.2257 | 621.6237 | 0 | 0.0045 | 14738100 | 110258.4717
Minimum of Months | 20748.0067 | 32.2265 | 45.4622 | 0 | 0.0003 | 1077511.2983 | 8475.578
Maximum of Months | 26126.6224 | 38.0171 | 60.4899 | 0 | 0.0004 | 1434505.798 | 10387.6789
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 67946400000 | 32065.993 | 23-JAN-11:20 | 3712.724 | 16310.475 | 7647.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4395.374 | 0 | 0
February | 61237500000 | 32157.097 | 02-FEB-11:09 | 3712.724 | 16310.475 | 7647.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4486.478 | 0 | 0
March | 67901100000 | 34503.91 | 30-MAR-16:00 | 3712.724 | 16310.475 | 7647.42 | 0 | 4807.393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2025.898 | 0 | 0
April | 65396400000 | 32281.851 | 06-APR-16:00 | 3712.724 | 16310.475 | 7647.42 | 0 | 2586.214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2025.018 | 0 | 0
May | 69035900000 | 40413.56 | 16-MAY-17:10 | 3712.724 | 16310.475 | 7647.42 | 0 | 10708.097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2034.843 | 0 | 0
June | 73798600000 | 49885.597 | 30-JUN-12:00 | 3712.724 | 16310.475 | 7647.42 | 0 | 20057.664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2157.313 | 0 | 0
July | 81526400000 | 49083.471 | 21-JUL-17:10 | 3712.724 | 16310.475 | 7647.42 | 0 | 19373.291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2039.561 | 0 | 0
August | 78367600000 | 47761.033 | 09-AUG-16:00 | 3712.724 | 16310.475 | 7647.42 | 0 | 18044.434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2045.98 | 0 | 0
September | 70452400000 | 45303.936 | 01-SEP-16:00 | 3712.724 | 16310.475 | 7647.42 | 0 | 15587.014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2046.302 | 0 | 0
October | 68364600000 | 37862.09 | 06-OCT-16:00 | 3712.724 | 16310.475 | 7647.42 | 0 | 8158.576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2032.894 | 0 | 0
November | 65646500000 | 32154.355 | 21-NOV-11:20 | 3712.724 | 16310.475 | 7647.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4483.736 | 0 | 0
December | 67927600000 | 32063.732 | 01-DEC-11:20 | 3712.724 | 16310.475 | 7647.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4393.112 | 0 | 0
Annual Sum or Average | 837601000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 61237500000 | 32063.732 |  | 3712.724 | 16310.475 | 7647.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2025.018 | 0 | 0
Maximum of Months | 81526400000 | 49885.597 |  | 3712.724 | 16310.475 | 7647.42 | 0 | 20057.664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4486.478 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 15770.96 | 12115.41 | 0 | 27886.37
Cost per Total Building Area ($/m2) | 67.88 | 52.14 | 0 | 120.02
Cost per Net Conditioned Building Area ($/m2) | 67.88 | 52.14 | 0 | 120.02
15-Duluth
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 2563.54 | 11033.44 | 11033.44
Net Site Energy | 2563.54 | 11033.44 | 11033.44
Total Source Energy | 4734.8 | 20378.49 | 20378.49
Net Source Energy | 4734.8 | 20378.49 | 20378.49
Area (m2)
Total Building Area | 232.34
Net Conditioned Building Area | 232.34
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 768.12 | 0 | 0 | 0 | 0
Cooling | 30.75 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 75.06 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 15.69 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 441.62 | 881.7 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 199.02 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 88.39 | 0 | 0 | 0 | 413.75
Refrigeration | 63.2 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 825.33 | 1738.21 | 0 | 0 | 0 | 413.75
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 825.33 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 825.33 | 100
Total On-Site and Utility Electric Sources | 825.33 | 100
Total Electricity End Uses | 825.33 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS | 0.22 | 0.505 | 0.55 | 46.47 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 116.17 | 0 | 180
KITCHEN_WALL_NORTH | EXT-WALLS | 0.22 | 0.505 | 0.55 | 46.47 | 0 | 90 | N
KITCHEN_WALL_EAST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 90 | 90 | E
KITCHEN_WALL_WEST | EXT-WALLS | 0.22 | 0.505 | 0.55 | 23.24 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 116.17 | 0 | 180
WEST-ROOF | ROOFS | 0.22 | 0.154 | 0.16 | 27.38 | 270 | 45
EAST-ROOF | ROOFS | 0.22 | 0.154 | 0.16 | 27.38 | 90 | 45
NORTH-ROOF | ROOFS | 0.22 | 0.154 | 0.16 | 102.05 | 0 | 18.44
SOUTH-ROOF | ROOFS | 0.22 | 0.154 | 0.16 | 102.05 | 180 | 18.44
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
DINING_WALL_EAST_WINDOW | WINDOW_EAST | 6.51 | 3.24 | 0.49 | 0.49 | No | DINING_WALL_EAST
DINING_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 13.01 | 3.24 | 0.49 | 0.49 | No | DINING_WALL_SOUTH
DINING_WALL_WEST_WINDOW | WINDOW_WEST | 6.51 | 3.24 | 0.49 | 0.49 | No | DINING_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 35493.67 | 2.96
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 45796.63 | 2.78
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.83 | 0.01 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.01 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 1.54 | 2925.94 | 1 | Fan Energy
PSZ-AC_2:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.36 | 4474.66 | 1 | Fan Energy
Nominal Capacity [W]
PSZ-AC_1:1_HEATC | 36713.84
PSZ-AC_2:2_HEATC | 56146.71
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 28173.6261 | 39.1385 | 44.3003 | 0 | 0.0004 | 29075.3673 | 11047.5919
February | 24492.6467 | 34.4574 | 39.9203 | 0 | 0.0003 | 26203.6795 | 9645.5181
March | 24727.2846 | 35.936 | 44.0425 | 0 | 0.0003 | 28917.2395 | 9847.7037
April | 20821.7779 | 31.9115 | 42.4634 | 0 | 0.0003 | 27890.7074 | 8450.176
May | 19948.5814 | 31.7814 | 44.6165 | 0 | 0.0003 | 29311.3751 | 8211.2824
June | 19853.0566 | 32.3481 | 46.7437 | 0 | 0.0003 | 30712.4454 | 8240.6808
July | 22083.02 | 36.3565 | 53.215 | 0 | 0.0004 | 34966.09 | 9202.1418
August | 21270.6722 | 34.837 | 50.6647 | 0 | 0.0004 | 33289.5185 | 8846.2308
September | 19301.6626 | 31.0933 | 44.285 | 0 | 0.0003 | 29095.34 | 7977.7415
October | 20714.9009 | 32.3932 | 44.3473 | 0 | 0.0003 | 29131.5757 | 8468.5033
November | 22910.3542 | 33.8832 | 42.7202 | 0 | 0.0003 | 28052.6956 | 9180.2902
December | 27176.4622 | 38.2152 | 44.2365 | 0 | 0.0003 | 29036.6725 | 10700.731
Annual Sum or Average | 271474.0454 | 412.3512 | 541.5554 | 0 | 0.0041 | 355682.7065 | 109818.5914
Minimum of Months | 19301.6626 | 31.0933 | 39.9203 | 0 | 0.0003 | 26203.6795 | 7977.7415
Maximum of Months | 28173.6261 | 39.1385 | 53.215 | 0 | 0.0004 | 34966.09 | 11047.5919
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 67467200000 | 31806.521 | 13-JAN-11:20 | 3712.724 | 16310.475 | 7400.613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4382.708 | 0 | 0
February | 60803700000 | 31822.781 | 21-FEB-11:20 | 3712.724 | 16310.475 | 7400.613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4398.969 | 0 | 0
March | 67100300000 | 31826.152 | 30-MAR-10:20 | 3712.724 | 16310.475 | 7400.613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4402.34 | 0 | 0
April | 64718300000 | 31933.209 | 04-APR-10:20 | 3712.724 | 16310.475 | 7400.613 | 0 | 74.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4434.772 | 0 | 0
May | 68014800000 | 37941.519 | 31-MAY-16:10 | 3712.724 | 16310.475 | 7400.613 | 0 | 8481.385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2036.321 | 0 | 0
June | 71265900000 | 48356.842 | 14-JUN-15:09 | 3712.724 | 16310.475 | 7400.613 | 0 | 18770.806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2162.223 | 0 | 0
July | 81136200000 | 54485.49 | 08-JUL-11:20 | 3300.199 | 16310.475 | 7400.613 | 0 | 24560.574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2913.628 | 0 | 0
August | 77245800000 | 52085.37 | 12-AUG-11:20 | 3300.199 | 16310.475 | 7400.613 | 0 | 22160.465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2913.618 | 0 | 0
September | 67513500000 | 44038.235 | 07-SEP-14:00 | 3712.724 | 16310.475 | 7400.613 | 0 | 14453.157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2161.266 | 0 | 0
October | 67597600000 | 40432.632 | 07-OCT-14:00 | 3300.199 | 16310.475 | 7400.613 | 0 | 11306.519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2114.826 | 0 | 0
November | 65094200000 | 31987.643 | 09-NOV-11:09 | 3712.724 | 16310.475 | 7400.613 | 0 | 79.317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4484.513 | 0 | 0
December | 67377400000 | 31816.021 | 26-DEC-11:20 | 3712.724 | 16310.475 | 7400.613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4392.208 | 0 | 0
Annual Sum or Average | 825335000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 60803700000 | 31806.521 |  | 3300.199 | 16310.475 | 7400.613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2036.321 | 0 | 0
Maximum of Months | 81136200000 | 54485.49 |  | 3712.724 | 16310.475 | 7400.613 | 0 | 24560.574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4484.513 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 11780.49 | 13816.37 | 0 | 25596.86
Cost per Total Building Area ($/m2) | 50.7 | 59.47 | 0 | 110.17
Cost per Net Conditioned Building Area ($/m2) | 50.7 | 59.47 | 0 | 110.17
16-Fairbanks
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 3098.46 | 13335.73 | 13335.73
Net Site Energy | 3098.46 | 13335.73 | 13335.73
Total Source Energy | 5399.19 | 23238.02 | 23238.02
Net Source Energy | 5399.19 | 23238.02 | 23238.02
Area (m2)
Total Building Area | 232.34
Net Conditioned Building Area | 232.34
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 1304.9 | 0 | 0 | 0 | 0
Cooling | 19.41 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 75.06 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 15.59 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 441.62 | 881.7 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 199.18 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 99.1 | 0 | 0 | 0 | 413.75
Refrigeration | 61.91 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 812.77 | 2285.69 | 0 | 0 | 0 | 413.75
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 812.77 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 812.77 | 100
Total On-Site and Utility Electric Sources | 812.77 | 100
Total Electricity End Uses | 812.77 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS | 0.22 | 0.29 | 0.3 | 23.24 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS | 0.22 | 0.29 | 0.3 | 46.47 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS | 0.22 | 0.29 | 0.3 | 23.24 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 116.17 | 0 | 180
KITCHEN_WALL_NORTH | EXT-WALLS | 0.22 | 0.29 | 0.3 | 46.47 | 0 | 90 | N
KITCHEN_WALL_EAST | EXT-WALLS | 0.22 | 0.29 | 0.3 | 23.24 | 90 | 90 | E
KITCHEN_WALL_WEST | EXT-WALLS | 0.22 | 0.29 | 0.3 | 23.24 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 116.17 | 0 | 180
WEST-ROOF | ROOFS | 0.22 | 0.154 | 0.16 | 27.38 | 270 | 45
EAST-ROOF | ROOFS | 0.22 | 0.154 | 0.16 | 27.38 | 90 | 45
NORTH-ROOF | ROOFS | 0.22 | 0.154 | 0.16 | 102.05 | 0 | 18.44
SOUTH-ROOF | ROOFS | 0.22 | 0.154 | 0.16 | 102.05 | 180 | 18.44
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
DINING_WALL_EAST_WINDOW | WINDOW_EAST | 6.51 | 2.62 | 0.49 | 0.49 | No | DINING_WALL_EAST
DINING_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 13.01 | 2.62 | 0.49 | 0.49 | No | DINING_WALL_SOUTH
DINING_WALL_WEST_WINDOW | WINDOW_WEST | 6.51 | 2.62 | 0.49 | 0.49 | No | DINING_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 25074.87 | 2.96
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 39062.08 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.83 | 0.01 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.01 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 1.51 | 2872.39 | 1 | Fan Energy
PSZ-AC_2:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.36 | 4474.66 | 1 | Fan Energy
Nominal Capacity [W]
PSZ-AC_1:1_HEATC | 44632.24
PSZ-AC_2:2_HEATC | 69528.9
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 30610.4292 | 32.3929 | 96.4495 | 0 | 0.0004 | 19340.2913 | 11303.0839
February | 27282.2423 | 28.9003 | 86.5776 | 0 | 0.0003 | 17360.9463 | 10078.6528
March | 26444.8303 | 28.5386 | 94.9123 | 0 | 0.0003 | 19035.831 | 9850.1478
April | 21219.2056 | 23.6125 | 91.0789 | 0 | 0.0003 | 18271.3081 | 8013.4698
May | 18290.0247 | 21.1721 | 95.6436 | 0 | 0.0003 | 19191.1473 | 7033.3158
June | 18276.3443 | 21.393 | 100.5247 | 0 | 0.0003 | 20171.5227 | 7064.4842
July | 19322.6463 | 22.6899 | 107.7909 | 0 | 0.0004 | 21629.8672 | 7480.0352
August | 18523.4771 | 21.6403 | 101.0062 | 0 | 0.0004 | 20267.9828 | 7153.5537
September | 18269.259 | 20.9807 | 92.0332 | 0 | 0.0003 | 18466.0159 | 6999.5726
October | 22653.5101 | 25.0996 | 94.9561 | 0 | 0.0003 | 19048.5538 | 8538.3719
November | 27338.3665 | 29.2397 | 92.6131 | 0 | 0.0003 | 18573.1278 | 10142.471
December | 29994.549 | 31.826 | 96.2829 | 0 | 0.0004 | 19307.4514 | 11088.7144
Annual Sum or Average | 278224.8843 | 307.4857 | 1149.8689 | 0 | 0.0041 | 230664.0455 | 104745.8731
Minimum of Months | 18269.259 | 20.9807 | 86.5776 | 0 | 0.0003 | 17360.9463 | 6999.5726
Maximum of Months | 30610.4292 | 32.3929 | 107.7909 | 0 | 0.0004 | 21629.8672 | 11303.0839
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 68147600000 | 32560.701 | 03-JAN-11:09 | 3712.724 | 16310.475 | 7347.062 | 0 | 0 | 1000.172 | 0 | 0 | 0 | 0 | 0 | 0 | 4190.268 | 0 | 0
February | 61173200000 | 31742.487 | 27-FEB-11:20 | 3712.724 | 16310.475 | 7347.062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4372.225 | 0 | 0
March | 67074800000 | 31764.447 | 09-MAR-11:09 | 3712.724 | 16310.475 | 7347.062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4394.186 | 0 | 0
April | 64380900000 | 31760.978 | 14-APR-10:20 | 3712.724 | 16310.475 | 7347.062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4390.717 | 0 | 0
May | 67622100000 | 35602.398 | 30-MAY-11:20 | 3712.724 | 16310.475 | 7347.062 | 0 | 5360.667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2871.47 | 0 | 0
June | 71076500000 | 42124.152 | 20-JUN-17:00 | 3712.724 | 16310.475 | 7347.062 | 0 | 12706.603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2047.288 | 0 | 0
July | 76215200000 | 43875.811 | 29-JUL-18:10 | 3712.724 | 16310.475 | 7347.062 | 0 | 14235.106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2270.443 | 0 | 0
August | 71416400000 | 41146.635 | 15-AUG-17:10 | 3712.724 | 16310.475 | 7347.062 | 0 | 11711.735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2064.639 | 0 | 0
September | 65067000000 | 31820.106 | 01-SEP-10:09 | 3712.724 | 16310.475 | 7347.062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4449.844 | 0 | 0
October | 67119600000 | 31781.061 | 02-OCT-10:20 | 3712.724 | 16310.475 | 7347.062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4410.8 | 0 | 0
November | 65444400000 | 31758.695 | 13-NOV-11:20 | 3712.724 | 16310.475 | 7347.062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4388.434 | 0 | 0
December | 68031900000 | 32755.625 | 18-DEC-11:09 | 3712.724 | 16310.475 | 7347.062 | 0 | 0 | 1000.172 | 0 | 0 | 0 | 0 | 0 | 0 | 4385.192 | 0 | 0
Annual Sum or Average | 812770000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 61173200000 | 31742.487 |  | 3712.724 | 16310.475 | 7347.062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2047.288 | 0 | 0
Maximum of Months | 76215200000 | 43875.811 |  | 3712.724 | 16310.475 | 7347.062 | 0 | 14235.106 | 1000.172 | 0 | 0 | 0 | 0 | 0 | 0 | 4449.844 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 19585.92 | 9517.78 | 0 | 29103.71
Cost per Total Building Area ($/m2) | 84.3 | 40.96 | 0 | 125.26
Cost per Net Conditioned Building Area ($/m2) | 84.3 | 40.96 | 0 | 125.26

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago-O'Hare | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7A | 8A
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 57.6 | 407.6 | 89.8 | 463.5 | 433.8 | 69.3 | 19.9 | 812.2 | 25.7 | 92.6 | 817.7 | 206.2 | 229.9 | 3.5 | 32.3 | 2.09
Fabric
Exterior walls
| Construction Type | Wood-Framed and Other | Wood-Framed and Other | Wood-Framed and Other | Wood-Framed and Other | Wood-Framed and Other | Wood-Framed and Other | Wood-Framed and Other | Wood-Framed and Other | Wood-Framed and Other | Wood-Framed and Other | Wood-Framed and Other | Wood-Framed and Other | Wood-Framed and Other | Wood-Framed and Other | Wood-Framed and Other | Wood-Framed and Other
| R-value (m2·K / W) | 1.9802 | 1.9802 | 1.9802 | 1.9802 | 1.9802 | 1.9802 | 1.9802 | 1.9802 | 1.9802 | 1.9802 | 1.9802 | 1.9802 | 1.9802 | 1.9802 | 1.9802 | 3.4483
Roof
| Construction Type | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic
| R-value (m2·K / W) | 5.1546 | 5.1546 | 5.1546 | 5.1546 | 5.1546 | 5.1546 | 5.1546 | 5.1546 | 5.1546 | 5.1546 | 5.1546 | 5.1546 | 6.4935 | 6.4935 | 6.4935 | 6.4935
Window
| U-Factor (W / m2·K) | 6.88 | 6.88 | 6.88 | 3.24 | 3.24 | 3.24 | 6.88 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 2.62
| SHGC | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.49 | 0.49
| Visible transmittance | 0.25 | 0.25 | 0.25 | 0.318 | 0.318 | 0.318 | 0.39 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.49 | 0.49
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 10 cm slab-on-grade | 10 cm slab-on-grade | 10 cm slab-on-grade | 10 cm slab-on-grade | 10 cm slab-on-grade | 10 cm slab-on-grade | 10 cm slab-on-grade | 10 cm slab-on-grade | 10 cm slab-on-grade | 10 cm slab-on-grade | 10 cm slab-on-grade | 10 cm slab-on-grade | 10 cm slab-on-grade | 10 cm slab-on-grade | 10 cm slab-on-grade | 10 cm slab-on-grade
| R-value (m2·K / W) | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC_1:1_COOLC DXCOIL | 33.6066 | 34.3609 | 38.8646 | 35.1412 | 24.4601 | 34.603 | 24.1374 | 36.3221 | 28.488 | 28.2153 | 36.9435 | 28.8374 | 37.3916 | 27.6969 | 35.4937 | 25.0749
| PSZ-AC_2:2_COOLC DXCOIL | 58.598 | 58.598 | 44.7943 | 58.598 | 39.0621 | 39.0621 | 39.0621 | 58.598 | 39.0621 | 39.0621 | 58.598 | 39.0621 | 58.598 | 39.0621 | 45.7966 | 39.0621
Heating (kW)
| PSZ-AC_1:1_HEATC | 15.7187 | 21.2166 | 20.2466 | 23.407 | 16.216 | 22.0506 | 19.212 | 26.9318 | 25.1772 | 23.6987 | 32.0001 | 31.1498 | 35.0022 | 35.4416 | 36.7138 | 44.6322
| PSZ-AC_2:2_HEATC | 27.4079 | 36.1821 | 30.5267 | 39.0312 | 28.5053 | 33.0002 | 31.5078 | 43.4487 | 34.5224 | 37.5749 | 50.7571 | 42.1944 | 54.8535 | 49.9848 | 56.1467 | 69.5289
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC_1:1_COOLC DXCOIL | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96
| PSZ-AC_2:2_COOLC DXCOIL | 2.78 | 2.78 | 2.78 | 2.78 | 2.96 | 2.96 | 2.96 | 2.78 | 2.96 | 2.96 | 2.78 | 2.96 | 2.78 | 2.96 | 2.78 | 2.96
| Heating Efficiency (%) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
HVAC Control
| Economizer | None | None | Fixed Dry Bulb | None | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | None | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb
Fan Max Flow Rate (m3/s )
| DINING EXHAUST FAN | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83
| KITCHEN EXHAUST FAN | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
| PSZ-AC_1:1 FAN | 1.35 | 1.38 | 1.57 | 1.42 | 1.34 | 1.58 | 1.44 | 1.46 | 1.72 | 1.49 | 1.49 | 1.74 | 1.51 | 1.67 | 1.54 | 1.51
| PSZ-AC_2:2 FAN | 2.36 | 2.36 | 2.36 | 2.36 | 2.36 | 2.36 | 2.36 | 2.36 | 2.36 | 2.36 | 2.36 | 2.36 | 2.36 | 2.36 | 2.36 | 2.36
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.075825 | 0.10782 | 0.096454 | 0.10528 | 0.12548 | 0.093765 | 0.14625 | 0.066782 | 0.037701 | 0.072297 | 0.053127 | 0.037727 | 0.05281 | 0.067783 | 0.051385 | 0.086752
| Total Cost ($/m2) | 110.31 | 141.03 | 122.69 | 122.47 | 125.33 | 109.7 | 140.58 | 74.55 | 40.44 | 70.2 | 56.05 | 39.12 | 55.21 | 67.88 | 50.7 | 84.3
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011471 | 0.0082069 | 0.00863 | 0.010814 | 0.0083915 | 0.008205 | 0.0084051 | 0.01007 | 0.0072147 | 0.0082942 | 0.0088352 | 0.0071864 | 0.0079679 | 0.0086582 | 0.0079486 | 0.0041641
| Total Cost ($/m2) | 45.77 | 35.44 | 35.71 | 50.29 | 34.54 | 34.97 | 36.6 | 53.38 | 33.85 | 40.73 | 52.79 | 37.42 | 54.13 | 52.14 | 59.47 | 40.96
Total Utility Costs
| Cost Intensity ($/m2) | 156.08 | 176.47 | 158.41 | 172.76 | 159.86 | 144.67 | 177.18 | 127.92 | 74.29 | 110.93 | 108.84 | 76.53 | 109.34 | 120.02 | 110.17 | 125.26
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 114313.8889 | 81388.8889 | 70847.2222 | 48583.3333 | 10725 | 47947.2222 | 3183.3333 | 38077.7778 | 24075 | 5033.3333 | 24061.1111 | 16283.3333 | 21605.5556 | 9655.5556 | 8541.6667 | 5391.6667
| Interior Lighting | 20850 | 20850 | 20850 | 20850 | 20850 | 20850 | 20850 | 20850 | 20850 | 20850 | 20850 | 20850 | 20850 | 20850 | 20850 | 20850
| Exterior Lighting | 4372.2222 | 4369.4444 | 4369.4444 | 4369.4444 | 4363.8889 | 4363.8889 | 4366.6667 | 4363.8889 | 4366.6667 | 4355.5556 | 4363.8889 | 4361.1111 | 4361.1111 | 4361.1111 | 4358.3333 | 4330.5556
| Interior Equipment | 122672.2222 | 122672.2222 | 122672.2222 | 122672.2222 | 122672.2222 | 122672.2222 | 122672.2222 | 122672.2222 | 122672.2222 | 122672.2222 | 122672.2222 | 122672.2222 | 122672.2222 | 122672.2222 | 122672.2222 | 122672.2222
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 56411.1111 | 55605.5556 | 58061.1111 | 55219.4444 | 54566.6667 | 57541.6667 | 53925 | 55177.7778 | 59061.1111 | 54672.2222 | 55150 | 58736.1111 | 55533.3333 | 57380.5556 | 55283.3333 | 55327.7778
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 19388.8889 | 19000 | 18752.7778 | 18583.3333 | 18875 | 18455.5556 | 18336.1111 | 18219.4444 | 18205.5556 | 18008.3333 | 18013.8889 | 17994.4444 | 17894.4444 | 17747.2222 | 17555.5556 | 17197.2222
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 338011.1111 | 303886.1111 | 295550 | 270275 | 232055.5556 | 271830.5556 | 223336.1111 | 259361.1111 | 249227.7778 | 225591.6667 | 245111.1111 | 240897.2222 | 242916.6667 | 232666.6667 | 229258.3333 | 225769.4444
Gas (MJ)
| Heating | 2920 | 69800 | 33230 | 137830 | 15360 | 55590 | 63250 | 281820 | 141660 | 187590 | 432430 | 254120 | 617160 | 437090 | 768120 | 1304900
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 881700 | 881700 | 881700 | 881700 | 881700 | 881700 | 881700 | 881700 | 881700 | 881700 | 881700 | 881700 | 881700 | 881700 | 881700 | 881700
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 42580 | 51910 | 46540 | 60910 | 59160 | 53010 | 66860 | 67980 | 66640 | 71660 | 74180 | 73860 | 79550 | 80520 | 88390 | 99100
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 927200 | 1003410 | 961460 | 1080430 | 956220 | 990300 | 1011800 | 1231500 | 1090000 | 1140950 | 1388310 | 1209680 | 1578400 | 1399300 | 1738210 | 2285690
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 2144030 | 2097400 | 2025440 | 2053420 | 1791620 | 1968890 | 1815810 | 2165200 | 1987220 | 1953070 | 2270710 | 2076910 | 2452900 | 2236910 | 2563540 | 3098460
| On-Site Production (MJ) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 1771.2404 | 1261.0829 | 1097.7447 | 752.7761 | 166.1789 | 742.9199 | 49.3243 | 589.9974 | 373.0309 | 77.9892 | 372.8157 | 252.3027 | 334.768 | 149.6083 | 132.3491 | 83.5414
| Interior Lighting (elec) | 323.061 | 323.061 | 323.061 | 323.061 | 323.061 | 323.061 | 323.061 | 323.061 | 323.061 | 323.061 | 323.061 | 323.061 | 323.061 | 323.061 | 323.061 | 323.061
| Exterior Lighting (elec) | 67.7455 | 67.7025 | 67.7025 | 67.7025 | 67.6164 | 67.6164 | 67.6595 | 67.6164 | 67.6595 | 67.4873 | 67.6164 | 67.5734 | 67.5734 | 67.5734 | 67.5303 | 67.0999
| Interior Equipment (elec) | 1900.7489 | 1900.7489 | 1900.7489 | 1900.7489 | 1900.7489 | 1900.7489 | 1900.7489 | 1900.7489 | 1900.7489 | 1900.7489 | 1900.7489 | 1900.7489 | 1900.7489 | 1900.7489 | 1900.7489 | 1900.7489
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 874.0639 | 861.5822 | 899.6299 | 855.5996 | 845.4851 | 891.5813 | 835.5427 | 854.9539 | 915.1244 | 847.1206 | 854.5235 | 910.0887 | 860.4631 | 889.085 | 856.5895 | 857.2781
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 300.4218 | 294.3961 | 290.5656 | 287.9401 | 292.4593 | 285.9602 | 284.1095 | 282.3018 | 282.0866 | 279.0307 | 279.1168 | 278.8155 | 277.2661 | 274.9849 | 272.0152 | 266.4629
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 5237.3246 | 4708.5736 | 4579.4095 | 4187.7851 | 3595.5927 | 4211.8878 | 3460.4889 | 4018.6795 | 3861.6682 | 3495.4377 | 3797.8824 | 3732.5902 | 3763.8805 | 3605.0615 | 3552.251 | 3498.1923
| Gas (MJ/m2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heating (gas) | 12.5678 | 300.4218 | 143.0232 | 593.2254 | 66.11 | 239.2614 | 272.2304 | 1212.9638 | 609.7099 | 807.3943 | 1861.1948 | 1093.7419 | 2656.2796 | 1881.2516 | 3306.017 | 5616.3381
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 3794.8696 | 3794.8696 | 3794.8696 | 3794.8696 | 3794.8696 | 3794.8696 | 3794.8696 | 3794.8696 | 3794.8696 | 3794.8696 | 3794.8696 | 3794.8696 | 3794.8696 | 3794.8696 | 3794.8696 | 3794.8696
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 183.2659 | 223.4226 | 200.3099 | 262.1589 | 254.6268 | 228.157 | 287.7679 | 292.5884 | 286.821 | 308.4273 | 319.2735 | 317.8962 | 342.3862 | 346.5611 | 380.4338 | 426.5301
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 3990.7033 | 4318.714 | 4138.1596 | 4650.2109 | 4115.6064 | 4262.288 | 4354.8248 | 5300.4218 | 4691.4005 | 4910.6912 | 5975.3379 | 5206.5077 | 6793.4923 | 6022.6392 | 7481.3205 | 9837.6948
| Purchased Cooling (MJ/m2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Purchased Heating (MJ/m2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 9227.9848 | 9027.2876 | 8717.5691 | 8837.996 | 7711.1991 | 8474.1758 | 7815.3138 | 9319.1013 | 8553.0688 | 8406.0859 | 9773.2203 | 8939.0979 | 10557.3728 | 9627.7438 | 11033.5715 | 13335.8871
| On-Site Production (MJ/m2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 53.2967 | 51.1296 | 39.5871 | 32.9682 | 41.5853 | 32.001 | 31.7147 | 31.8639 | 32.2244 | 31.736 | 31.7264 | 32.8331 | 31.7485 | 32.066 | 31.8065 | 32.5607
| Feb | 53.9465 | 46.8397 | 41.5124 | 36.2288 | 41.9069 | 34.6419 | 34.2364 | 31.7059 | 34.7342 | 31.8037 | 31.8522 | 32.2623 | 31.745 | 32.1571 | 31.8228 | 31.7425
| Mar | 53.9506 | 50.1179 | 47.802 | 39.8162 | 40.9735 | 39.257 | 31.7359 | 42.9118 | 35.9981 | 31.8052 | 35.4261 | 39.2586 | 31.9245 | 34.5039 | 31.8262 | 31.7644
| Apr | 54.5691 | 54.3212 | 49.6078 | 46.8522 | 41.7669 | 47.3221 | 37.28 | 42.1051 | 43.4735 | 34.1125 | 36.2426 | 40.8465 | 39.151 | 32.2819 | 31.9332 | 31.761
| May | 59.3157 | 58.8013 | 58.1899 | 52.46 | 43.4672 | 51.9382 | 39.369 | 51.1907 | 45.7323 | 39.012 | 50.2029 | 44.6102 | 58.1517 | 40.4136 | 37.9415 | 35.6024
| Jun | 61.1015 | 58.6513 | 65.2821 | 56.0368 | 42.0293 | 58.916 | 42.0608 | 60.3973 | 50.3609 | 44.1154 | 60.817 | 49.9873 | 58.3177 | 49.8856 | 48.3568 | 42.1242
| Jul | 60.986 | 61.5838 | 64.6002 | 60.8328 | 44.5512 | 58.12 | 48.043 | 63.5444 | 51.418 | 44.9345 | 61.9329 | 50.8853 | 59.7306 | 49.0835 | 54.4855 | 43.8758
| Aug | 60.9698 | 62.228 | 64.9831 | 58.8304 | 48.0286 | 57.3217 | 44.5525 | 62.4368 | 50.4514 | 42.969 | 59.9454 | 51.3027 | 58.966 | 47.761 | 52.0854 | 41.1466
| Sep | 59.2901 | 61.1222 | 59.4129 | 53.9549 | 49.3162 | 55.7348 | 47.6248 | 53.4162 | 45.6977 | 51.0504 | 53.2191 | 46.6369 | 48.4807 | 45.3039 | 44.0382 | 31.8201
| Oct | 58.5709 | 56.4195 | 49.3453 | 48.9799 | 45.2873 | 48.4203 | 39.7056 | 50.5203 | 42.5222 | 35.2572 | 46.0055 | 43.3951 | 44.4513 | 37.8621 | 40.4326 | 31.7811
| Nov | 55.7582 | 53.1446 | 47.0287 | 40.0644 | 42.5035 | 36.7081 | 31.7583 | 47.2915 | 32.6899 | 31.8522 | 45.9696 | 36.5558 | 32.6814 | 32.1544 | 31.9876 | 31.7587
| Dec | 51.1758 | 52.8857 | 38.5354 | 37.2376 | 42.3836 | 36.4787 | 31.7158 | 31.6998 | 32.1955 | 31.7485 | 31.7627 | 32.2202 | 31.7384 | 32.0637 | 31.816 | 32.7556
Time of Peak Electrical Demand
| Jan | 06-JAN-12:20 | 03-JAN-12:20 | 28-JAN-14:00 | 23-JAN-13:00 | 26-JAN-12:00 | 19-JAN-11:09 | 05-JAN-11:09 | 09-JAN-11:09 | 27-JAN-11:20 | 27-JAN-11:20 | 17-JAN-11:20 | 27-JAN-11:20 | 30-JAN-11:20 | 23-JAN-11:20 | 13-JAN-11:20 | 03-JAN-11:09
| Feb | 23-FEB-12:09 | 21-FEB-12:20 | 28-FEB-13:00 | 18-FEB-13:00 | 12-FEB-12:20 | 08-FEB-13:00 | 14-FEB-12:00 | 13-FEB-11:09 | 14-FEB-15:00 | 22-FEB-11:20 | 28-FEB-11:20 | 23-FEB-11:20 | 21-FEB-11:09 | 02-FEB-11:09 | 21-FEB-11:20 | 27-FEB-11:20
| Mar | 13-MAR-11:20 | 25-MAR-11:00 | 17-MAR-16:10 | 28-MAR-12:00 | 04-MAR-12:20 | 31-MAR-12:00 | 01-MAR-11:20 | 09-MAR-13:00 | 02-MAR-14:00 | 29-MAR-10:20 | 31-MAR-14:00 | 26-MAR-13:00 | 25-MAR-18:30 | 30-MAR-16:00 | 30-MAR-10:20 | 09-MAR-11:09
| Apr | 04-APR-11:20 | 29-APR-11:20 | 01-APR-17:10 | 15-APR-11:20 | 11-APR-16:10 | 21-APR-17:10 | 29-APR-12:00 | 04-APR-16:10 | 22-APR-13:00 | 29-APR-14:00 | 07-APR-13:00 | 24-APR-11:20 | 01-APR-17:10 | 06-APR-16:00 | 04-APR-10:20 | 14-APR-10:20
| May | 23-MAY-11:20 | 18-MAY-11:20 | 28-MAY-16:00 | 31-MAY-17:30 | 30-MAY-11:09 | 31-MAY-16:10 | 17-MAY-13:00 | 15-MAY-12:00 | 31-MAY-17:10 | 06-MAY-12:00 | 30-MAY-16:10 | 23-MAY-11:20 | 27-MAY-14:00 | 16-MAY-17:10 | 31-MAY-16:10 | 30-MAY-11:20
| Jun | 26-JUN-10:20 | 28-JUN-11:20 | 28-JUN-16:30 | 19-JUN-11:09 | 28-JUN-11:20 | 27-JUN-15:00 | 16-JUN-11:20 | 30-JUN-16:00 | 29-JUN-13:00 | 18-JUN-11:20 | 08-JUN-12:00 | 28-JUN-11:00 | 29-JUN-11:20 | 30-JUN-12:00 | 14-JUN-15:09 | 20-JUN-17:00
| Jul | 11-JUL-11:20 | 18-JUL-12:00 | 19-JUL-17:10 | 03-JUL-11:00 | 29-JUL-10:09 | 24-JUL-16:10 | 02-JUL-12:00 | 25-JUL-10:20 | 31-JUL-14:00 | 31-JUL-11:20 | 14-JUL-11:20 | 17-JUL-11:20 | 15-JUL-14:00 | 21-JUL-17:10 | 08-JUL-11:20 | 29-JUL-18:10
| Aug | 21-AUG-13:00 | 31-AUG-11:20 | 01-AUG-16:00 | 17-AUG-11:20 | 08-AUG-10:09 | 04-AUG-16:10 | 15-AUG-11:20 | 17-AUG-11:20 | 01-AUG-13:00 | 18-AUG-17:19 | 04-AUG-11:20 | 30-AUG-12:00 | 27-AUG-14:00 | 09-AUG-16:00 | 12-AUG-11:20 | 15-AUG-17:10
| Sep | 01-SEP-11:20 | 16-SEP-10:20 | 12-SEP-17:10 | 11-SEP-11:20 | 24-SEP-10:00 | 01-SEP-14:00 | 28-SEP-14:00 | 05-SEP-11:20 | 03-SEP-13:00 | 02-SEP-16:10 | 06-SEP-11:09 | 02-SEP-14:00 | 14-SEP-12:00 | 01-SEP-16:00 | 07-SEP-14:00 | 01-SEP-10:09
| Oct | 06-OCT-11:20 | 31-OCT-12:09 | 24-OCT-13:00 | 12-OCT-15:00 | 19-OCT-10:00 | 06-OCT-11:09 | 31-OCT-12:00 | 03-OCT-11:20 | 03-OCT-11:20 | 17-OCT-12:00 | 31-OCT-12:20 | 05-OCT-11:20 | 08-OCT-14:00 | 06-OCT-16:00 | 07-OCT-14:00 | 02-OCT-10:20
| Nov | 01-NOV-12:09 | 26-NOV-11:00 | 12-NOV-13:00 | 22-NOV-12:20 | 20-NOV-12:20 | 10-NOV-12:20 | 08-NOV-11:09 | 04-NOV-12:20 | 08-NOV-14:00 | 03-NOV-11:09 | 02-NOV-12:09 | 10-NOV-13:00 | 02-NOV-14:00 | 21-NOV-11:20 | 09-NOV-11:09 | 13-NOV-11:20
| Dec | 15-DEC-12:20 | 02-DEC-12:20 | 09-DEC-14:00 | 31-DEC-12:20 | 19-DEC-12:20 | 05-DEC-13:00 | 04-DEC-11:20 | 08-DEC-11:09 | 13-DEC-11:20 | 28-DEC-11:09 | 12-DEC-11:09 | 21-DEC-11:20 | 26-DEC-11:20 | 01-DEC-11:20 | 26-DEC-11:20 | 18-DEC-11:09
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 413.75 | 413.75 | 413.75 | 413.75 | 413.75 | 413.75 | 413.75 | 413.75 | 413.75 | 413.75 | 413.75 | 413.75 | 413.75 | 413.75 | 413.75 | 413.75
| Total Building | 413.75 | 413.75 | 413.75 | 413.75 | 413.75 | 413.75 | 413.75 | 413.75 | 413.75 | 413.75 | 413.75 | 413.75 | 413.75 | 413.75 | 413.75 | 413.75
Emissions
| Carbon Equivalent (kg) | 109419.0833 | 119458.4927 | 106557.2531 | 102737.9051 | 44362.5885 | 109539.7605 | 44345.8003 | 92197.5554 | 121465.1163 | 37005.0728 | 155715.8459 | 120219.8442 | 111611.8494 | 110258.4717 | 109818.5914 | 104745.8731
| CO2 (kg) | 262956.9554 | 306629.7301 | 259909.4819 | 245245.5645 | 122223.1493 | 268744.4477 | 122398.1858 | 221116.6414 | 294014.9149 | 98474.1426 | 373847.1079 | 292319.8935 | 273925.8209 | 270661.3424 | 271474.0454 | 278224.8843
| NOX (kg) | 422.4143 | 381.7838 | 400.1024 | 415.9764 | 107.1908 | 402.9514 | 107.4914 | 372.0678 | 467.779 | 116.6792 | 614.6966 | 459.5259 | 424.4598 | 417.2257 | 412.3512 | 307.4857
| SO2 (kg) | 1447.0673 | 1449.8011 | 1188.7258 | 948.9567 | 675.5088 | 1495.5568 | 650.1501 | 947.1065 | 1088.6244 | 174.6695 | 1652.2257 | 1052.2749 | 573.7477 | 621.6237 | 541.5554 | 1149.8689
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0067 | 0.0042 | 0.0033 | 0.0036 | 0.0004 | 0.0029 | 0.0004 | 0.0039 | 0.0044 | 0.0008 | 0.0051 | 0.0042 | 0.0044 | 0.0045 | 0.0041 | 0.0041
| Water Environmental Factors (m3) | 179.0636 | 494.4568 | 8779.1532 | 1687.492 | 4074.3676 | 7457.4284 | 3921.267 | 58.885 | 1131.6978 | 2304.8177 | 380.2754 | 1093.8665 | 376.8723 | 14738.1 | 355.6827 | 230.664

## Picture
DOE Commercial Building Benchmark - Fast Food Restaurant

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 14.55 | 53.9 | 2810.5
|  |  | Sat | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 13.65
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | 11.15
BLDG_EQUIP_SCH | Fraction | Through 12/31 | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 6.25 | 25 | 1303.57
|  |  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 6.25
|  |  | SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 7.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 6.25
FF_GAS_EQUIP_SCH | Fraction | Through 12/31 | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.1 | 0.05 | 3.05 | 18.3 | 954.21
|  |  | SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.1 | 0.05 | 3.05
Rest_GAS_EQUIP_SCH | Fraction | Through 12/31 | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65 | 21.9 | 1141.93
|  |  | SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2 | 8.4 | 56.8 | 2961.71
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35 | 8.25
|  |  | Sun, Hol, Other | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2 | 6.55
INFIL_SCH | fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 35 | 1825
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
INFIL_HALF_ON_SCH | fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 14.5 | 101.5 | 5292.5
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 14.5
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 14.5
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | 7.75 | 52.65 | 2745.32
|  |  | Sat, WinterDesign | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3 | 7.45
|  |  | Sun, Hol, Other | 0.25 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2 | 6.45
Hours_of_operation | on/off | Through 12/31 | Weekday, SummerDesign | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 80 | 4171.43
|  |  | Sat, WinterDesign | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20
|  |  | Sun, Hol, Other | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | on/off | Through 12/31 | Weekday, SummerDesign | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 80 | 4171.43
|  |  | Sat, WinterDesign | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20
|  |  | Sun, Hol, Other | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Kitchen_Exhaust_SCH | on/off | Through 12/31 | Weekday, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 18 | 72 | 3754.29
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 18
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 18
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | WD, WinterDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 477 | 3339 | 174105
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 477
|  |  | Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 477
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 606 | 4248 | 221502.86
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 606
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 612
HTGSETP_KITCHEN_SCH | Temperature | Through 12/31 | WD, WinterDesign | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 442.4 | 3096.8 | 161476
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | Sat | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 442.4
|  |  | Sun, Hol, Other | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 442.4
CLGSETP_KITCHEN_SCH | Temperature | Through 12/31 | WD, SummerDesign | 26 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 640 | 4480 | 233600
|  |  | Sat | 26 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 640
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 26 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 640
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19 | 133 | 6935
|  |  | Sat | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
MinOA_SDKitch_Sched | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 1.08 | 7.56 | 394.2
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 1.08
|  |  | WinterDesign | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 1.44
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 1.08
MinOA_FFKitch_Sched | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 11.7 | 81.9 | 4270.5
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 11.7
|  |  | WinterDesign | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 15.6
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 11.7
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Kitchen Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Kitchen Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Kitchen Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Kitchen_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Kitchen_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Kitchen_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
SHWSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SHWSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SHWSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720