## BuildingSummary
Building Summary Medium Office new construction version 1.0_3.0
|  | Value | Data Source
Program
| Building Name | Benchmark Medium Office
| Available Fuel Types | gas, electricity
| Principal Building Activity | Office
Form
| Total Floor Area (m2) | 4982.2 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 1.5
| Number of Floors | 3
Window Fraction (Window to Wall Ratio)
| South | 0.33
| East | 0.33
| North | 0.33
| West | 0.33
| Total | 0.33
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | core zone with four perimeter zones on each floor
| Floor to Ceiling Height (m) | 2.74
| Floor to Floor Height (m) | 3.96
| Roof type | Insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel frame | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1977.67
| Net Dimensions - Total Area (m2) | 1324.84
| Wall to Skin Ratio | 0.544
Roof
| Construction Type | Insulation entirely above deck | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1661
| Net Dimensions - Total Area (m2) | 1661
| Roof to Skin Ratio | 0.456
Window Dimensions (m2)
| South | 195.85
| East | 130.57
| North | 195.85
| West | 130.57
| Total Area (m2) | 652.84
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab-on-grade
| Dimensions - Total Area (m2) | 1661
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 1423.65
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 9964.31
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.29 | See Benchmark Technical Report
HVAC
| System Type | MZ-VAV | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | PACU | 2003 CBECS
| Fan Control | Variable | 2003 CBECS
Service Water Heating
| SWH Type | gas water heater
| Fuel | gas
| Thermal Efficiency (%) | 80
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 174.77

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Perimeter_bot_ZN_3 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.92 | 65.28 | 18.5806 | 11.1589 | 10.76 | 8.0702 | 0 | 0 | 2.5 | 0.3 | 90.0993 | 0 | 0.262
Perimeter_bot_ZN_2 | Yes | 1 | 131.26 | 360.08 | 2.7433 | 91.28 | 43.52 | 18.5806 | 7.0643 | 10.76 | 8.0698 | 0 | 0 | 2.5 | 0.3 | 57.0389 | 0 | 0.2759
Perimeter_bot_ZN_1 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.92 | 65.28 | 18.5806 | 11.1589 | 10.76 | 8.0701 | 0 | 0 | 2.5 | 0.3 | 90.0993 | 0 | 0.262
Perimeter_bot_ZN_4 | Yes | 1 | 131.25 | 360.05 | 2.7432 | 91.28 | 43.52 | 18.5806 | 7.0638 | 10.76 | 8.0698 | 0 | 0 | 2.5 | 0.3 | 57.0345 | 0 | 0.27592
Core_bottom | Yes | 1 | 983.54 | 2698.04 | 2.7432 | 0 | 0 | 18.5806 | 52.9336 | 10.76 | 8.07 | 0 | 37.4755 | 2.5 | 0.3 | 427.3961 | 0 | 0
Perimeter_mid_ZN_3 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.92 | 65.28 | 18.5806 | 11.1589 | 10.76 | 8.0702 | 0 | 0 | 2.5 | 0.3 | 90.0993 | 0 | 0.262
Perimeter_mid_ZN_2 | Yes | 1 | 131.26 | 360.08 | 2.7433 | 91.28 | 43.52 | 18.5806 | 7.0643 | 10.76 | 8.0698 | 0 | 0 | 2.5 | 0.3 | 57.0389 | 0 | 0.2759
Perimeter_mid_ZN_1 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.92 | 65.28 | 18.5806 | 11.1589 | 10.76 | 8.0701 | 0 | 0 | 2.5 | 0.3 | 90.0993 | 0 | 0.262
Perimeter_mid_ZN_4 | Yes | 1 | 131.25 | 360.05 | 2.7432 | 91.28 | 43.52 | 18.5806 | 7.0638 | 10.76 | 8.0698 | 0 | 0 | 2.5 | 0.3 | 57.0345 | 0 | 0.27592
Core_mid | Yes | 1 | 983.54 | 2698.04 | 2.7432 | 0 | 0 | 18.5806 | 52.9336 | 10.76 | 8.07 | 0 | 37.4755 | 2.5 | 0.3 | 427.3961 | 0 | 0
Perimeter_top_ZN_3 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.92 | 65.28 | 18.5806 | 11.1589 | 10.76 | 8.0702 | 0 | 0 | 2.5 | 0.3 | 90.0993 | 0 | 0.65876
Perimeter_top_ZN_2 | Yes | 1 | 131.26 | 360.08 | 2.7433 | 91.28 | 43.52 | 18.5806 | 7.0643 | 10.76 | 8.0698 | 0 | 0 | 2.5 | 0.3 | 57.0389 | 0 | 0.67264
Perimeter_top_ZN_1 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.92 | 65.28 | 18.5806 | 11.1589 | 10.76 | 8.0701 | 0 | 0 | 2.5 | 0.3 | 90.0993 | 0 | 0.65876
Perimeter_top_ZN_4 | Yes | 1 | 131.25 | 360.05 | 2.7432 | 91.28 | 43.52 | 18.5806 | 7.0638 | 10.76 | 8.0698 | 0 | 0 | 2.5 | 0.3 | 57.0345 | 0 | 0.67267
Core_top | Yes | 1 | 983.54 | 2698.04 | 2.7432 | 0 | 0 | 18.5806 | 52.9336 | 10.76 | 8.07 | 0 | 37.4755 | 2.5 | 0.3 | 427.3961 | 0 | 0.39675
Firstfloor_plenum | No | 1 | 1660.73 | 2024.76 | 1.2192 | 202.84 | 0 | [10 empty] | 0.10903
Midfloor_plenum | No | 1 | 1660.73 | 2024.76 | 1.2192 | 202.84 | 0 | [10 empty] | 0.10903
Topfloor_plenum | No | 1 | 1660.73 | 2024.76 | 1.2192 | 202.84 | 0 | [10 empty] | 1.0017
Total Conditioned Zones |  |  | 4982.19 | 19741.41 |  | 1977.72 | 652.8 |  | 268.139
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report

## Query (hidden)
1-miami
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 2991.45 | 600.43 | 600.43
Net Site Energy | 2991.45 | 600.43 | 600.43
Total Source Energy | 9771.26 | 1961.24 | 1961.24
Net Source Energy | 9771.26 | 1961.24 | 1961.24
Area (m2)
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 40.28 | 0 | 0 | 0 | 0
Cooling | 1084.06 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 42.96 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 809.46 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 434.05 | 0 | 0 | 0 | 0 | 0
Pumps | 0.32 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 27.75 | 0 | 0 | 0 | 174.77
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2923.42 | 68.03 | 0 | 0 | 0 | 174.77
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 2923.42 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 2923.42 | 100
Total On-Site and Utility Electric Sources | 2923.42 | 100
Total Electricity End Uses | 2923.42 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 983.54 | 0 | 180
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1660.73 | 0 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 65.28 | 6.88 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 43.52 | 6.88 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_2_WALL_EAST
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 65.28 | 6.88 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_3_WALL_NORTH
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 43.52 | 6.88 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_4_WALL_WEST
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 65.28 | 6.88 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_1_WALL_SOUTH
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 43.52 | 6.88 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_2_WALL_EAST
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 65.28 | 6.88 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_3_WALL_NORTH
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 43.52 | 6.88 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_4_WALL_WEST
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 65.28 | 6.88 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 43.52 | 6.88 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_2_WALL_EAST
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 65.28 | 6.88 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_3_WALL_NORTH
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 43.52 | 6.88 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
HEATSYS1 BOILER | Boiler:HotWater | 1398626.16 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 129850.81 | 3
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 150036.43 | 3
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 167765.08 | 3
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
VAV_1 FAN | Fan:VariableVolume | 0.19 | 500 | 6.64 | 17834.77 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.19 | 500 | 7.53 | 20230.64 | 1 | Fan Energy
VAV_3 FAN | Fan:VariableVolume | 0.19 | 500 | 8.05 | 21634.52 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.45 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8228.59 | 0.85
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORE_BOTTOM VAV BOX REHEAT COIL | 0.004761 | 218931.68 | 7751.13
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | 0.001014 | 46615.54 | 1650.39
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | 0.001011 | 46494.04 | 1646.09
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | 0.001109 | 51007.6 | 1805.89
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | 0.001191 | 54777.05 | 1939.34
CORE_MID VAV BOX REHEAT COIL | 0.005243 | 241060.35 | 8534.58
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | 0.001226 | 56355.74 | 1995.24
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | 0.001203 | 55323.98 | 1958.71
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | 0.001272 | 58466.72 | 2069.97
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | 0.001365 | 62748.5 | 2221.57
CORE_TOP VAV BOX REHEAT COIL | 0.005404 | 248457.37 | 8796.47
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | 0.001277 | 58693.49 | 2078
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | 0.001224 | 56294.98 | 1993.09
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | 0.001601 | 73605.01 | 2605.94
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | 0.001518 | 69794.11 | 2471.01
Nominal Capacity [W]
VAV_1_HEATC | 4461.33
VAV_2_HEATC | 3297.83
VAV_3_HEATC | 2860.24
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 39922.2877 | 69.6115 | 262.828 | 0 | 0.0012 | 32527.9625 | 17161.1949
February | 36609.9312 | 64.1019 | 243.116 | 0 | 0.0011 | 30088.5787 | 15763.9979
March | 42774.8569 | 75.0284 | 285.0948 | 0 | 0.0013 | 35284.073 | 18431.8064
April | 40501.7828 | 71.3011 | 271.9887 | 0 | 0.0012 | 33662.2291 | 17478.3542
May | 46007.3984 | 81.0287 | 309.239 | 0 | 0.0014 | 38272.4689 | 19857.8085
June | 47219.5693 | 83.1804 | 317.519 | 0 | 0.0014 | 39297.2494 | 20382.6943
July | 47182.9485 | 83.1189 | 317.2968 | 0 | 0.0014 | 39269.743 | 20367.1919
August | 50562.0344 | 89.0717 | 340.0208 | 0 | 0.0015 | 42082.1474 | 21825.8262
September | 45517.7785 | 80.1788 | 306.0464 | 0 | 0.0014 | 37877.352 | 19647.7303
October | 43912.1151 | 77.3193 | 295.0051 | 0 | 0.0013 | 36510.8248 | 18951.5234
November | 40455.3862 | 71.202 | 271.5402 | 0 | 0.0012 | 33606.7085 | 17456.5889
December | 38568.9282 | 67.5498 | 256.2647 | 0 | 0.0012 | 31715.9116 | 16609.3068
Annual Sum or Average | 519235.0173 | 912.6926 | 3475.9596 | 0 | 0.0158 | 430195.2488 | 223934.0238
Minimum of Months | 36609.9312 | 64.1019 | 243.116 | 0 | 0.0011 | 30088.5787 | 15763.9979
Maximum of Months | 50562.0344 | 89.0717 | 340.0208 | 0 | 0.0015 | 42082.1474 | 21825.8262
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 221046000000 | 199515.597 | 23-JAN-16:15 | 48247.488 | 51263.506 | 26550.261 | 0 | 73445.893 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 204469000000 | 207614.103 | 21-FEB-13:00 | 48247.488 | 51919.067 | 27248.722 | 0 | 80190.377 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 239775000000 | 208870.647 | 27-MAR-15:30 | 48247.488 | 51263.506 | 27456.996 | 0 | 81894.208 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 228754000000 | 216628.506 | 03-APR-15:15 | 48247.488 | 51263.506 | 28158.096 | 0 | 88950.966 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 260083000000 | 226898.089 | 15-MAY-15:00 | 48247.488 | 51263.506 | 28305.318 | 0 | 99073.327 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 267047000000 | 240845.858 | 26-JUN-15:30 | 48247.488 | 51263.506 | 28576.753 | 0 | 112749.661 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 266860000000 | 235494.357 | 03-JUL-15:15 | 48247.488 | 51263.506 | 28714.39 | 0 | 107260.524 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 285972000000 | 247758.49 | 21-AUG-15:15 | 48247.488 | 51263.506 | 29640.517 | 0 | 118598.53 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 257398000000 | 236571.366 | 11-SEP-15:15 | 48247.488 | 51263.506 | 29503.843 | 0 | 107548.08 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 248111000000 | 225393.893 | 06-OCT-15:30 | 48247.488 | 51263.506 | 28121.927 | 0 | 97752.522 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 228376000000 | 207801.584 | 01-NOV-08:00 | 48247.488 | 58802.451 | 25818.197 | 0 | 74924.998 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 215527000000 | 195282.062 | 19-DEC-13:00 | 48247.488 | 51919.067 | 26320.235 | 0 | 68786.824 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2923420000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 204469000000 | 195282.062 |  | 48247.488 | 51263.506 | 25818.197 | 0 | 68786.824 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 285972000000 | 247758.49 |  | 48247.488 | 58802.451 | 29640.517 | 0 | 118598.53 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 71646.72 | 775.8 | 0 | 72422.52
Cost per Total Building Area ($/m2) | 14.38 | 0.16 | 0 | 14.54
Cost per Net Conditioned Building Area ($/m2) | 14.38 | 0.16 | 0 | 14.54
2-houston
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 3187.03 | 639.68 | 639.68
Net Site Energy | 3187.03 | 639.68 | 639.68
Total Source Energy | 457.94 | 91.91 | 91.91
Net Source Energy | 457.94 | 91.91 | 91.91
Area (m2)
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 387.66 | 0 | 0 | 0 | 0
Cooling | 906.41 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 42.88 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 809.46 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 455.46 | 0 | 0 | 0 | 0 | 0
Pumps | 0.89 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 31.69 | 0 | 0 | 0 | 174.77
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2767.67 | 419.35 | 0 | 0 | 0 | 174.77
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 2767.67 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 2767.67 | 100
Total On-Site and Utility Electric Sources | 2767.67 | 100
Total Electricity End Uses | 2767.67 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 983.54 | 0 | 180
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1660.73 | 0 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 65.28 | 6.88 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 43.52 | 6.88 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_2_WALL_EAST
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 65.28 | 6.88 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_3_WALL_NORTH
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 43.52 | 6.88 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_4_WALL_WEST
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 65.28 | 6.88 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_1_WALL_SOUTH
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 43.52 | 6.88 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_2_WALL_EAST
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 65.28 | 6.88 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_3_WALL_NORTH
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 43.52 | 6.88 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_4_WALL_WEST
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 65.28 | 6.88 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 43.52 | 6.88 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_2_WALL_EAST
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 65.28 | 6.88 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_3_WALL_NORTH
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 43.52 | 6.88 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
HEATSYS1 BOILER | Boiler:HotWater | 1430251.95 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 122957.31 | 3
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 147954.85 | 3
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 167308.39 | 3
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
VAV_1 FAN | Fan:VariableVolume | 0.19 | 500 | 6.34 | 17025.91 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.19 | 500 | 7.93 | 21303.93 | 1 | Fan Energy
VAV_3 FAN | Fan:VariableVolume | 0.19 | 500 | 8.54 | 22944.91 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.45 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8414.65 | 0.85
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORE_BOTTOM VAV BOX REHEAT COIL | 0.004252 | 195504.97 | 6921.72
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | 0.001179 | 54189.34 | 1918.54
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | 0.000954 | 43866.07 | 1553.05
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | 0.001066 | 49022.63 | 1735.61
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | 0.001192 | 54829.25 | 1941.19
CORE_MID VAV BOX REHEAT COIL | 0.005229 | 240432.53 | 8512.35
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | 0.001539 | 70781.08 | 2505.96
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | 0.001215 | 55855.32 | 1977.52
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | 0.001403 | 64511.03 | 2283.97
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | 0.001429 | 65688.22 | 2325.65
CORE_TOP VAV BOX REHEAT COIL | 0.005408 | 248646.62 | 8803.17
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | 0.001707 | 78488.92 | 2778.85
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | 0.001243 | 57133.51 | 2022.77
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | 0.001687 | 77553.55 | 2745.73
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | 0.001604 | 73748.91 | 2611.03
Nominal Capacity [W]
VAV_1_HEATC | 16073.3
VAV_2_HEATC | 13960.2
VAV_3_HEATC | 13171.01
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 52322.0634 | 66.6372 | 268.2719 | 0 | 0.0008 | 91502.2926 | 20576.1182
February | 46256.0105 | 58.8615 | 236.4693 | 0 | 0.0007 | 80654.8087 | 18184.1463
March | 54213.7459 | 70.2481 | 294.8015 | 0 | 0.0008 | 100556.7636 | 21474.9354
April | 50989.4682 | 66.6521 | 285.4183 | 0 | 0.0008 | 97358.8032 | 20272.7524
May | 58068.2238 | 76.2109 | 329.3231 | 0 | 0.0009 | 112336.4659 | 23126.5717
June | 61986.0476 | 81.4212 | 352.5006 | 0 | 0.001 | 120242.8955 | 24695.725
July | 62850.6762 | 82.5631 | 357.5032 | 0 | 0.001 | 121949.3871 | 25040.9882
August | 66393.3248 | 87.2087 | 377.54 | 0 | 0.0011 | 128784.1798 | 26451.3997
September | 56112.1529 | 73.688 | 318.8499 | 0 | 0.0009 | 108764.1047 | 22353.2448
October | 53968.5586 | 70.6545 | 303.6105 | 0 | 0.0009 | 103564.7749 | 21471.156
November | 50415.2489 | 65.5483 | 277.2574 | 0 | 0.0008 | 94573.4672 | 19998.9234
December | 51756.6059 | 65.9427 | 265.7322 | 0 | 0.0008 | 90636.1447 | 20357.0556
Annual Sum or Average | 665332.1267 | 865.636 | 3667.2778 | 0 | 0.0103 | 1250924.0879 | 264003.0166
Minimum of Months | 46256.0105 | 58.8615 | 236.4693 | 0 | 0.0007 | 80654.8087 | 18184.1463
Maximum of Months | 66393.3248 | 87.2087 | 377.54 | 0 | 0.0011 | 128784.1798 | 26451.3997
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 202449000000 | 189267.625 | 03-JAN-08:30 | 48247.488 | 58802.451 | 25617.985 | 0 | 56570.874 | 0 | 28.827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 178449000000 | 183786.433 | 23-FEB-13:00 | 48247.488 | 51919.067 | 26232.013 | 0 | 57379.416 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 222482000000 | 189560.899 | 29-MAR-07:00 | 48247.488 | 58802.451 | 25866.788 | 0 | 56635.227 | 0 | 8.945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 215407000000 | 194079.675 | 17-APR-15:00 | 48247.488 | 51263.506 | 26352.3 | 0 | 68207.931 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 248545000000 | 229491.07 | 18-MAY-15:30 | 48247.488 | 51263.506 | 28221.679 | 0 | 101749.948 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 266038000000 | 230820.479 | 12-JUN-15:15 | 48247.488 | 51263.506 | 28831.956 | 0 | 102469.08 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 269813000000 | 246835.01 | 05-JUL-15:00 | 48247.488 | 51263.506 | 29709.684 | 0 | 117605.882 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 284935000000 | 241973.075 | 31-AUG-15:00 | 48247.488 | 51263.506 | 29171.989 | 0 | 113281.643 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 240641000000 | 227439.061 | 15-SEP-15:15 | 48247.488 | 51263.506 | 27166.637 | 0 | 100752.98 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 229137000000 | 207119.725 | 30-OCT-08:00 | 48247.488 | 58802.451 | 25900.905 | 0 | 74160.432 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 209244000000 | 197124.8 | 27-NOV-08:45 | 48247.488 | 58802.451 | 25892.127 | 0 | 64174.285 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 200533000000 | 187650.624 | 20-DEC-08:45 | 48247.488 | 58802.451 | 25882.615 | 0 | 54701.106 | 0 | 16.964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2767670000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 178449000000 | 183786.433 |  | 48247.488 | 51263.506 | 25617.985 | 0 | 54701.106 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 284935000000 | 246835.01 |  | 48247.488 | 58802.451 | 29709.684 | 0 | 117605.882 | 0 | 28.827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 92098.93 | 3378.3 | 0 | 95477.23
Cost per Total Building Area ($/m2) | 18.49 | 0.68 | 0 | 19.16
Cost per Net Conditioned Building Area ($/m2) | 18.49 | 0.68 | 0 | 19.16
3-phoenix
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 3327.58 | 667.9 | 667.9
Net Site Energy | 3327.58 | 667.9 | 667.9
Total Source Energy | 9671.56 | 1941.23 | 1941.23
Net Source Energy | 9671.56 | 1941.23 | 1941.23
Area (m2)
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 382.75 | 0 | 0 | 0 | 0
Cooling | 962.03 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 42.87 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 809.46 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 547.68 | 0 | 0 | 0 | 0 | 0
Pumps | 0.8 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 29.42 | 0 | 0 | 0 | 174.77
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2915.42 | 412.16 | 0 | 0 | 0 | 174.77
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 2915.42 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 2915.42 | 100
Total On-Site and Utility Electric Sources | 2915.42 | 100
Total Electricity End Uses | 2915.42 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 983.54 | 0 | 180
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1660.73 | 0 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 65.28 | 6.88 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 43.52 | 6.88 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_2_WALL_EAST
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 65.28 | 6.88 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_3_WALL_NORTH
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 43.52 | 6.88 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_4_WALL_WEST
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 65.28 | 6.88 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_1_WALL_SOUTH
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 43.52 | 6.88 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_2_WALL_EAST
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 65.28 | 6.88 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_3_WALL_NORTH
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 43.52 | 6.88 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_4_WALL_WEST
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 65.28 | 6.88 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 43.52 | 6.88 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_2_WALL_EAST
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 65.28 | 6.88 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_3_WALL_NORTH
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 43.52 | 6.88 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
HEATSYS1 BOILER | Boiler:HotWater | 1629474.99 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 124042.02 | 3
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 156394.82 | 3
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 172579.34 | 3
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
VAV_1 FAN | Fan:VariableVolume | 0.19 | 500 | 7.23 | 19424.42 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.19 | 500 | 9.29 | 24969.07 | 1 | Fan Energy
VAV_3 FAN | Fan:VariableVolume | 0.19 | 500 | 10.43 | 28006.61 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.45 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 9586.75 | 0.85
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORE_BOTTOM VAV BOX REHEAT COIL | 0.004167 | 191583.11 | 6782.87
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | 0.001568 | 72089.84 | 2552.29
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | 0.001115 | 51248.83 | 1814.43
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | 0.001288 | 59209.87 | 2096.29
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | 0.001371 | 63044.53 | 2232.05
CORE_MID VAV BOX REHEAT COIL | 0.005375 | 247162.65 | 8750.63
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | 0.002027 | 93223.45 | 3300.51
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | 0.001435 | 66000.09 | 2336.69
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | 0.001717 | 78929.98 | 2794.46
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | 0.001667 | 76650.96 | 2713.78
CORE_TOP VAV BOX REHEAT COIL | 0.005921 | 272238.23 | 9638.41
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | 0.002289 | 105235.47 | 3725.79
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | 0.001513 | 69575.74 | 2463.28
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | 0.002088 | 96015.19 | 3399.35
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | 0.001898 | 87267.03 | 3089.63
Nominal Capacity [W]
VAV_1_HEATC | 8817.12
VAV_2_HEATC | 6348.74
VAV_3_HEATC | 4741.23
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 45816.3042 | 73.5496 | 231.3959 | 0 | 0.0006 | 1709120.9217 | 19089.1216
February | 41093.6381 | 66.3366 | 210.2087 | 0 | 0.0006 | 1552649.7599 | 17158.6969
March | 47958.854 | 79.3166 | 259.0545 | 0 | 0.0007 | 1913537.4253 | 20217.1697
April | 43887.9234 | 73.4212 | 243.1217 | 0 | 0.0007 | 1795890.994 | 18585.7249
May | 49284.3273 | 83.0368 | 277.2681 | 0 | 0.0008 | 2048152.7447 | 20930.4458
June | 57790.1673 | 97.5704 | 326.5857 | 0 | 0.0009 | 2412467.1291 | 24563.2458
July | 60208.6349 | 101.6838 | 340.4716 | 0 | 0.0009 | 2515042.6536 | 25594.2511
August | 61503.8171 | 103.8669 | 347.7646 | 0 | 0.0009 | 2568914.9772 | 26144.3884
September | 52419.9307 | 88.4776 | 296.0497 | 0 | 0.0008 | 2186897.8355 | 22278.0472
October | 46423.7345 | 77.8239 | 258.3301 | 0 | 0.0007 | 1908240.1136 | 19675.8229
November | 44012.9817 | 72.6788 | 236.9307 | 0 | 0.0006 | 1750111.8244 | 18542.4586
December | 45994.6316 | 73.4432 | 229.456 | 0 | 0.0006 | 1694771.1986 | 19123.7139
Annual Sum or Average | 596394.9447 | 991.2056 | 3256.6373 | 0 | 0.0089 | 24055800 | 251903.0867
Minimum of Months | 41093.6381 | 66.3366 | 210.2087 | 0 | 0.0006 | 1552649.7599 | 17158.6969
Maximum of Months | 61503.8171 | 103.8669 | 347.7646 | 0 | 0.0009 | 2568914.9772 | 26144.3884
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 207135000000 | 173719.034 | 30-JAN-13:00 | 48247.488 | 51919.067 | 30559.862 | 0 | 42982.112 | 0 | 10.505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 188172000000 | 177883.802 | 28-FEB-16:15 | 48247.488 | 51263.506 | 30562.383 | 0 | 47801.976 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 231910000000 | 195999.228 | 17-MAR-15:00 | 48247.488 | 51263.506 | 31296.344 | 0 | 65183.44 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 217652000000 | 198779.316 | 26-APR-15:45 | 48247.488 | 51263.506 | 31340.571 | 0 | 67919.302 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 248224000000 | 238593.267 | 30-MAY-15:30 | 48247.488 | 51263.506 | 34325.523 | 0 | 104748.301 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 292377000000 | 311442.612 | 28-JUN-15:00 | 48247.488 | 51263.506 | 49938.827 | 0 | 161984.342 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 304809000000 | 302736.705 | 11-JUL-15:00 | 48247.488 | 51263.506 | 43107.081 | 0 | 160110.181 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 311338000000 | 309475.198 | 01-AUG-15:45 | 48247.488 | 51263.506 | 48404.775 | 0 | 161550.98 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 265039000000 | 260800.575 | 11-SEP-15:45 | 48247.488 | 51263.506 | 35560.36 | 0 | 125720.772 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 231268000000 | 205367.081 | 13-OCT-15:45 | 48247.488 | 51263.506 | 31561.15 | 0 | 74286.488 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 212103000000 | 189142.041 | 13-NOV-13:00 | 48247.488 | 51919.067 | 31132.145 | 0 | 57834.891 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 205396000000 | 178231.934 | 13-DEC-13:15 | 48247.488 | 51919.067 | 30402.361 | 0 | 47648.304 | 0 | 14.714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2915420000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 188172000000 | 173719.034 |  | 48247.488 | 51263.506 | 30402.361 | 0 | 42982.112 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 311338000000 | 311442.612 |  | 48247.488 | 51919.067 | 49938.827 | 0 | 161984.342 | 0 | 14.714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 78924.99 | 3392.97 | 0 | 82317.95
Cost per Total Building Area ($/m2) | 15.84 | 0.68 | 0 | 16.52
Cost per Net Conditioned Building Area ($/m2) | 15.84 | 0.68 | 0 | 16.52
4-atlanta
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 3081.61 | 618.53 | 618.53
Net Site Energy | 3081.61 | 618.53 | 618.53
Total Source Energy | 9165.68 | 1839.69 | 1839.69
Net Source Energy | 9165.68 | 1839.69 | 1839.69
Area (m2)
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 493.05 | 0 | 0 | 0 | 0
Cooling | 685.55 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 42.94 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 809.46 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 461.48 | 0 | 0 | 0 | 0 | 0
Pumps | 1.06 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 35.5 | 0 | 0 | 0 | 174.77
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2553.07 | 528.55 | 0 | 0 | 0 | 174.77
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 2553.07 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 2553.07 | 100
Total On-Site and Utility Electric Sources | 2553.07 | 100
Total Electricity End Uses | 2553.07 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 983.54 | 0 | 180
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1660.73 | 0 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 65.28 | 3.24 | 0.25 | 0.318 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 43.52 | 3.24 | 0.25 | 0.318 | No | PERIMETER_BOT_ZN_2_WALL_EAST
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 65.28 | 3.24 | 0.25 | 0.318 | No | PERIMETER_BOT_ZN_3_WALL_NORTH
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 43.52 | 3.24 | 0.25 | 0.318 | No | PERIMETER_BOT_ZN_4_WALL_WEST
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 65.28 | 3.24 | 0.25 | 0.318 | No | PERIMETER_MID_ZN_1_WALL_SOUTH
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 43.52 | 3.24 | 0.25 | 0.318 | No | PERIMETER_MID_ZN_2_WALL_EAST
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 65.28 | 3.24 | 0.25 | 0.318 | No | PERIMETER_MID_ZN_3_WALL_NORTH
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 43.52 | 3.24 | 0.25 | 0.318 | No | PERIMETER_MID_ZN_4_WALL_WEST
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 65.28 | 3.24 | 0.25 | 0.318 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 43.52 | 3.24 | 0.25 | 0.318 | No | PERIMETER_TOP_ZN_2_WALL_EAST
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 65.28 | 3.24 | 0.25 | 0.318 | No | PERIMETER_TOP_ZN_3_WALL_NORTH
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 43.52 | 3.24 | 0.25 | 0.318 | No | PERIMETER_TOP_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
HEATSYS1 BOILER | Boiler:HotWater | 1397373.42 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 116289.78 | 3
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 145650.46 | 3
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 160270.24 | 3
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
VAV_1 FAN | Fan:VariableVolume | 0.19 | 500 | 6.28 | 16859.3 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.19 | 500 | 8.09 | 21726.5 | 1 | Fan Energy
VAV_3 FAN | Fan:VariableVolume | 0.19 | 500 | 8.68 | 23323.95 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.45 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8221.22 | 0.85
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORE_BOTTOM VAV BOX REHEAT COIL | 0.004097 | 188373.26 | 6669.23
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | 0.001184 | 54426.41 | 1926.93
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | 0.000954 | 43851.5 | 1552.53
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | 0.000922 | 42388.34 | 1500.73
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | 0.00112 | 51494.07 | 1823.11
CORE_MID VAV BOX REHEAT COIL | 0.005189 | 238570.59 | 8446.43
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | 0.001586 | 72935.87 | 2582.25
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | 0.001246 | 57277.6 | 2027.87
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | 0.001269 | 58340.78 | 2065.52
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | 0.001376 | 63266.94 | 2239.92
CORE_TOP VAV BOX REHEAT COIL | 0.005347 | 245852.6 | 8704.25
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | 0.00174 | 80013.01 | 2832.81
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | 0.001267 | 58244.91 | 2062.12
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | 0.001553 | 71408.88 | 2528.18
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | 0.001543 | 70928.66 | 2511.18
Nominal Capacity [W]
VAV_1_HEATC | 20736.58
VAV_2_HEATC | 18398.33
VAV_3_HEATC | 17666.98
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 43752.0095 | 76.9744 | 182.8432 | 0 | 0.0007 | 325174.8989 | 18583.7752
February | 37194.8375 | 66.8114 | 162.1724 | 0 | 0.0006 | 288427.8831 | 15925.43
March | 43266.9634 | 80.6353 | 202.9456 | 0 | 0.0007 | 360974.1267 | 18794.6585
April | 40658.5186 | 77.0885 | 197.1542 | 0 | 0.0007 | 350685.8385 | 17782.9773
May | 44466.1537 | 85.4448 | 221.191 | 0 | 0.0008 | 393451.5237 | 19553.3393
June | 47397.0645 | 91.3608 | 237.1631 | 0 | 0.0009 | 421865.0553 | 20868.4018
July | 47996.5201 | 92.5219 | 240.1901 | 0 | 0.0009 | 427249.5372 | 21132.8532
August | 51001.776 | 98.3186 | 255.2468 | 0 | 0.0009 | 454032.2912 | 22456.3938
September | 44990.2619 | 86.6381 | 224.711 | 0 | 0.0008 | 399714.5648 | 19801.007
October | 41649.1108 | 79.1928 | 203.0662 | 0 | 0.0007 | 361203.8325 | 18237.1219
November | 39805.9584 | 73.6564 | 184.1197 | 0 | 0.0007 | 327483.9162 | 17242.4084
December | 41163.3357 | 73.7566 | 178.577 | 0 | 0.0007 | 317602.0383 | 17607.6671
Annual Sum or Average | 523342.5101 | 982.3997 | 2489.3804 | 0 | 0.0091 | 4427865.5063 | 227986.0336
Minimum of Months | 37194.8375 | 66.8114 | 162.1724 | 0 | 0.0006 | 288427.8831 | 15925.43
Maximum of Months | 51001.776 | 98.3186 | 255.2468 | 0 | 0.0009 | 454032.2912 | 22456.3938
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 187493000000 | 166423.287 | 24-JAN-16:00 | 48247.488 | 51263.506 | 25920.294 | 0 | 40961.257 | 0 | 30.742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 166305000000 | 169319.926 | 22-FEB-08:15 | 48247.488 | 58802.451 | 25883.467 | 0 | 36337.446 | 0 | 49.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 208134000000 | 174130.089 | 29-MAR-15:15 | 48247.488 | 51263.506 | 26021.52 | 0 | 48589.126 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 202202000000 | 188726.039 | 20-APR-15:00 | 48247.488 | 51263.506 | 26960.875 | 0 | 62245.72 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 226860000000 | 209453.745 | 15-MAY-15:15 | 48247.488 | 51263.506 | 28374.066 | 0 | 81560.236 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 243243000000 | 222386.132 | 19-JUN-15:15 | 48247.488 | 51263.506 | 28923.78 | 0 | 93942.908 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 246348000000 | 246005.941 | 03-JUL-15:30 | 48247.488 | 51263.506 | 30377.842 | 0 | 116108.656 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 261791000000 | 224122.921 | 14-AUG-15:45 | 48247.488 | 51263.506 | 28786.737 | 0 | 95816.741 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 230472000000 | 214222.969 | 05-SEP-15:00 | 48247.488 | 51263.506 | 28729.439 | 0 | 85974.087 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 208267000000 | 192672.067 | 12-OCT-15:00 | 48247.488 | 51263.506 | 26940.55 | 0 | 66212.074 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 188824000000 | 171575.866 | 22-NOV-13:30 | 48247.488 | 51919.067 | 26152.255 | 0 | 45248.607 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 183126000000 | 171750.477 | 26-DEC-08:00 | 48247.488 | 58802.451 | 25883.467 | 0 | 38725.097 | 0 | 91.973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2553070000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 166305000000 | 166423.287 |  | 48247.488 | 51263.506 | 25883.467 | 0 | 36337.446 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 261791000000 | 246005.941 |  | 48247.488 | 58802.451 | 30377.842 | 0 | 116108.656 | 0 | 91.973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 70131.14 | 5091.46 | 0 | 75222.6
Cost per Total Building Area ($/m2) | 14.08 | 1.02 | 0 | 15.1
Cost per Net Conditioned Building Area ($/m2) | 14.08 | 1.02 | 0 | 15.1
5-losangeles
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 2627.91 | 527.46 | 527.46
Net Site Energy | 2627.91 | 527.46 | 527.46
Total Source Energy | 7700.5 | 1545.61 | 1545.61
Net Source Energy | 7700.5 | 1545.61 | 1545.61
Area (m2)
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 181.34 | 0 | 0 | 0 | 0
Cooling | 606.25 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 42.93 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 809.46 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 400.08 | 0 | 0 | 0 | 0 | 0
Pumps | 0.5 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 34.77 | 0 | 0 | 0 | 174.77
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2411.8 | 216.11 | 0 | 0 | 0 | 174.77
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 2411.8 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 2411.8 | 100
Total On-Site and Utility Electric Sources | 2411.8 | 100
Total Electricity End Uses | 2411.8 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 983.54 | 0 | 180
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1660.73 | 0 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 65.28 | 3.24 | 0.25 | 0.318 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 43.52 | 3.24 | 0.25 | 0.318 | No | PERIMETER_BOT_ZN_2_WALL_EAST
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 65.28 | 3.24 | 0.25 | 0.318 | No | PERIMETER_BOT_ZN_3_WALL_NORTH
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 43.52 | 3.24 | 0.25 | 0.318 | No | PERIMETER_BOT_ZN_4_WALL_WEST
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 65.28 | 3.24 | 0.25 | 0.318 | No | PERIMETER_MID_ZN_1_WALL_SOUTH
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 43.52 | 3.24 | 0.25 | 0.318 | No | PERIMETER_MID_ZN_2_WALL_EAST
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 65.28 | 3.24 | 0.25 | 0.318 | No | PERIMETER_MID_ZN_3_WALL_NORTH
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 43.52 | 3.24 | 0.25 | 0.318 | No | PERIMETER_MID_ZN_4_WALL_WEST
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 65.28 | 3.24 | 0.25 | 0.318 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 43.52 | 3.24 | 0.25 | 0.318 | No | PERIMETER_TOP_ZN_2_WALL_EAST
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 65.28 | 3.24 | 0.25 | 0.318 | No | PERIMETER_TOP_ZN_3_WALL_NORTH
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 43.52 | 3.24 | 0.25 | 0.318 | No | PERIMETER_TOP_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
HEATSYS1 BOILER | Boiler:HotWater | 1306445.02 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 93923.62 | 3
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 124912.04 | 3
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 126019.55 | 3
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
VAV_1 FAN | Fan:VariableVolume | 0.19 | 500 | 5.67 | 15242.16 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.19 | 500 | 7.55 | 20271.04 | 1 | Fan Energy
VAV_3 FAN | Fan:VariableVolume | 0.19 | 500 | 7.61 | 20450.77 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.45 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 7686.25 | 0.85
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORE_BOTTOM VAV BOX REHEAT COIL | 0.004001 | 183948.59 | 6512.58
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | 0.001218 | 56003.71 | 1982.77
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | 0.000876 | 40285.54 | 1426.28
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | 0.000616 | 28337.74 | 1003.28
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | 0.001027 | 47243.44 | 1672.62
CORE_MID VAV BOX REHEAT COIL | 0.005099 | 234443.42 | 8300.31
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | 0.001614 | 74208.25 | 2627.29
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | 0.001162 | 53413.33 | 1891.06
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | 0.001142 | 52495.23 | 1858.56
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | 0.001276 | 58654.94 | 2076.64
CORE_TOP VAV BOX REHEAT COIL | 0.005074 | 233298.52 | 8259.78
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | 0.001701 | 78204.25 | 2768.77
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | 0.00114 | 52430.35 | 1856.26
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | 0.001081 | 49681.63 | 1758.94
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | 0.001387 | 63796.09 | 2258.66
Nominal Capacity [W]
VAV_1_HEATC | 7321.29
VAV_2_HEATC | 4971.8
VAV_3_HEATC | 4939.34
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 18586.9641 | 16.0208 | 152.847 | 0 | 0.0001 | 922186.674 | 6899.3098
February | 16650.657 | 14.333 | 140.3019 | 0 | 0.0001 | 846509.8053 | 6190.876
March | 19293.2564 | 16.5865 | 166.3742 | 0 | 0.0001 | 1003830.8036 | 7185.0297
April | 17434.3551 | 14.9656 | 154.4075 | 0 | 0.0001 | 931643.1901 | 6505.1507
May | 18669.2625 | 16.0089 | 168.3526 | 0 | 0.0001 | 1015793.8398 | 6975.1002
June | 18619.2961 | 15.9541 | 170.0426 | 0 | 0.0001 | 1025998.1947 | 6962.9629
July | 18316.3212 | 15.6852 | 168.9322 | 0 | 0.0001 | 1019304.0525 | 6854.715
August | 20353.1046 | 17.4297 | 187.6573 | 0 | 0.0001 | 1132287.5086 | 7616.7788
September | 18192.3529 | 15.583 | 167.0734 | 0 | 0.0001 | 1008085.9963 | 6806.1383
October | 18249.6597 | 15.6446 | 165.3651 | 0 | 0.0001 | 997770.898 | 6820.7603
November | 17807.5845 | 15.2947 | 156.1522 | 0 | 0.0001 | 942165.0497 | 6639.6493
December | 18116.9161 | 15.5988 | 152.0061 | 0 | 0.0001 | 917124.5077 | 6734.0598
Annual Sum or Average | 220289.7302 | 189.105 | 1949.5122 | 0 | 0.0009 | 11762700 | 82190.5306
Minimum of Months | 16650.657 | 14.333 | 140.3019 | 0 | 0.0001 | 846509.8053 | 6190.876
Maximum of Months | 20353.1046 | 17.4297 | 187.6573 | 0 | 0.0001 | 1132287.5086 | 7616.7788
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 189083000000 | 165345.678 | 26-JAN-13:15 | 48247.488 | 51919.067 | 24030.408 | 0 | 41140.266 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 173566000000 | 166761.011 | 13-FEB-13:00 | 48247.488 | 51919.067 | 24153.038 | 0 | 42432.969 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 205823000000 | 165030.356 | 31-MAR-15:15 | 48247.488 | 51263.506 | 24362.142 | 0 | 41148.771 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 191022000000 | 173577.351 | 11-APR-15:15 | 48247.488 | 51263.506 | 24005.647 | 0 | 50052.261 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 208276000000 | 185656.383 | 30-MAY-15:15 | 48247.488 | 51263.506 | 24713.822 | 0 | 61423.118 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 210368000000 | 178027.615 | 30-JUN-15:00 | 48247.488 | 51263.506 | 24340.824 | 0 | 54167.348 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 208996000000 | 183738.122 | 24-JUL-15:15 | 48247.488 | 51263.506 | 24445.43 | 0 | 59773.248 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 232161000000 | 193075.739 | 08-AUG-15:15 | 48247.488 | 51263.506 | 24798.072 | 0 | 68758.224 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 206696000000 | 193507.019 | 25-SEP-15:15 | 48247.488 | 51263.506 | 25746.836 | 0 | 68240.74 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 204581000000 | 178142.678 | 05-OCT-15:15 | 48247.488 | 51263.506 | 24607.061 | 0 | 54016.174 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 193179000000 | 170624.525 | 10-NOV-13:15 | 48247.488 | 51919.067 | 24024.367 | 0 | 46425.154 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 188045000000 | 167234.515 | 19-DEC-13:15 | 48247.488 | 51919.067 | 24284.062 | 0 | 42775.449 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2411800000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 173566000000 | 165030.356 |  | 48247.488 | 51263.506 | 24005.647 | 0 | 41140.266 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 232161000000 | 193507.019 |  | 48247.488 | 51919.067 | 25746.836 | 0 | 68758.224 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 86644.76 | 1860.09 | 0 | 88504.85
Cost per Total Building Area ($/m2) | 17.39 | 0.37 | 0 | 17.76
Cost per Net Conditioned Building Area ($/m2) | 17.39 | 0.37 | 0 | 17.76
6-lasvegas
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 3120.34 | 626.3 | 626.3
Net Site Energy | 3120.34 | 626.3 | 626.3
Total Source Energy | 10200.55 | 2047.4 | 2047.4
Net Source Energy | 10200.55 | 2047.4 | 2047.4
Area (m2)
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 354.54 | 0 | 0 | 0 | 0
Cooling | 794.45 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 42.89 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 809.46 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 533.5 | 0 | 0 | 0 | 0 | 0
Pumps | 0.79 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 32.15 | 0 | 0 | 0 | 174.77
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2733.65 | 386.69 | 0 | 0 | 0 | 174.77
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 2733.65 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 2733.65 | 100
Total On-Site and Utility Electric Sources | 2733.65 | 100
Total Electricity End Uses | 2733.65 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 983.54 | 0 | 180
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1660.73 | 0 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 65.28 | 3.24 | 0.25 | 0.318 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 43.52 | 3.24 | 0.25 | 0.318 | No | PERIMETER_BOT_ZN_2_WALL_EAST
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 65.28 | 3.24 | 0.25 | 0.318 | No | PERIMETER_BOT_ZN_3_WALL_NORTH
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 43.52 | 3.24 | 0.25 | 0.318 | No | PERIMETER_BOT_ZN_4_WALL_WEST
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 65.28 | 3.24 | 0.25 | 0.318 | No | PERIMETER_MID_ZN_1_WALL_SOUTH
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 43.52 | 3.24 | 0.25 | 0.318 | No | PERIMETER_MID_ZN_2_WALL_EAST
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 65.28 | 3.24 | 0.25 | 0.318 | No | PERIMETER_MID_ZN_3_WALL_NORTH
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 43.52 | 3.24 | 0.25 | 0.318 | No | PERIMETER_MID_ZN_4_WALL_WEST
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 65.28 | 3.24 | 0.25 | 0.318 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 43.52 | 3.24 | 0.25 | 0.318 | No | PERIMETER_TOP_ZN_2_WALL_EAST
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 65.28 | 3.24 | 0.25 | 0.318 | No | PERIMETER_TOP_ZN_3_WALL_NORTH
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 43.52 | 3.24 | 0.25 | 0.318 | No | PERIMETER_TOP_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
HEATSYS1 BOILER | Boiler:HotWater | 1529507.48 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 116963.43 | 3
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 153051.24 | 3
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 165394.17 | 3
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
VAV_1 FAN | Fan:VariableVolume | 0.19 | 500 | 7.07 | 18981.12 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.19 | 500 | 9.25 | 24837.54 | 1 | Fan Energy
VAV_3 FAN | Fan:VariableVolume | 0.19 | 500 | 9.99 | 26840.59 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.45 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8998.61 | 0.85
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORE_BOTTOM VAV BOX REHEAT COIL | 0.004186 | 192479.41 | 6814.6
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | 0.001416 | 65085.02 | 2304.29
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | 0.001044 | 48025.16 | 1700.3
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | 0.001028 | 47263.96 | 1673.35
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | 0.001262 | 58016.48 | 2054.03
CORE_MID VAV BOX REHEAT COIL | 0.005408 | 248651.71 | 8803.35
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | 0.001867 | 85848.59 | 3039.41
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | 0.001376 | 63253.55 | 2239.45
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | 0.001494 | 68671.36 | 2431.26
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | 0.001549 | 71214.34 | 2521.3
CORE_TOP VAV BOX REHEAT COIL | 0.005484 | 252147.18 | 8927.1
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | 0.002093 | 96232.25 | 3407.04
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | 0.001434 | 65914 | 2333.64
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | 0.001862 | 85618.23 | 3031.26
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | 0.001764 | 81086.24 | 2870.8
Nominal Capacity [W]
VAV_1_HEATC | 13287.86
VAV_2_HEATC | 10538.97
VAV_3_HEATC | 9706.87
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 49084.7322 | 76.5878 | 301.268 | 0 | 0.0006 | 1502369.3455 | 20317.7199
February | 43502.4941 | 69.3359 | 280.7116 | 0 | 0.0005 | 1399915.5831 | 18158.6143
March | 50784.2836 | 81.2617 | 330.7055 | 0 | 0.0006 | 1649248.028 | 21231.3878
April | 47082.1006 | 76.6752 | 319.1686 | 0 | 0.0006 | 1591762.3736 | 19822.633
May | 52102.169 | 85.1947 | 356.4331 | 0 | 0.0007 | 1777620.8478 | 21971.9529
June | 59802.5234 | 97.9771 | 410.9085 | 0 | 0.0008 | 2049310.1065 | 25239.1326
July | 62268.7423 | 102.0371 | 428.0378 | 0 | 0.0008 | 2134738.9802 | 26282.0096
August | 64963.4792 | 106.4478 | 446.5136 | 0 | 0.0008 | 2226882.6772 | 27418.8579
September | 53657.9928 | 87.8895 | 368.4944 | 0 | 0.0007 | 1837778.9805 | 22643.7366
October | 49186.4954 | 80.0925 | 333.3417 | 0 | 0.0006 | 1662446.7361 | 20707.6085
November | 46720.7816 | 74.7982 | 304.6067 | 0 | 0.0006 | 1519093.5303 | 19536.5696
December | 47588.6144 | 74.7697 | 296.938 | 0 | 0.0006 | 1480796.4586 | 19752.0908
Annual Sum or Average | 626744.4086 | 1013.0672 | 4177.1275 | 0 | 0.0079 | 20832000 | 263082.3136
Minimum of Months | 43502.4941 | 69.3359 | 280.7116 | 0 | 0.0005 | 1399915.5831 | 18158.6143
Maximum of Months | 64963.4792 | 106.4478 | 446.5136 | 0 | 0.0008 | 2226882.6772 | 27418.8579
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 197147000000 | 166519.904 | 18-JAN-13:00 | 48247.488 | 51919.067 | 29698.71 | 0 | 36637.322 | 0 | 17.317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 183703000000 | 170165.681 | 27-FEB-13:00 | 48247.488 | 51919.067 | 30078.373 | 0 | 39912.119 | 0 | 8.634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 216421000000 | 175029.214 | 31-MAR-15:15 | 48247.488 | 51263.506 | 30004.176 | 0 | 45505.594 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 208877000000 | 197419.85 | 21-APR-15:30 | 48247.488 | 51263.506 | 30892.718 | 0 | 67007.688 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 233267000000 | 220116.122 | 31-MAY-15:00 | 48247.488 | 51263.506 | 32207.501 | 0 | 88389.177 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 268919000000 | 290573.483 | 27-JUN-15:45 | 48247.488 | 51263.506 | 47853.582 | 0 | 143200.457 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 280129000000 | 285508.397 | 24-JUL-15:00 | 48247.488 | 51263.506 | 47473.058 | 0 | 138515.896 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 292221000000 | 265088.677 | 04-AUG-15:00 | 48247.488 | 51263.506 | 38334.025 | 0 | 127235.208 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 241161000000 | 242833.867 | 01-SEP-15:15 | 48247.488 | 51263.506 | 33892.969 | 0 | 109421.455 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 218153000000 | 201064.535 | 06-OCT-12:00 | 48247.488 | 51919.067 | 30959.942 | 0 | 69929.588 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 199342000000 | 172562.26 | 09-NOV-16:45 | 48247.488 | 51263.506 | 29719.031 | 0 | 40594.623 | 2729.127 | 8.485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 194316000000 | 169234.076 | 05-DEC-13:00 | 48247.488 | 51919.067 | 29826.644 | 0 | 39227.183 | 0 | 13.694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2733650000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 183703000000 | 166519.904 |  | 48247.488 | 51263.506 | 29698.71 | 0 | 36637.322 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 292221000000 | 290573.483 |  | 48247.488 | 51919.067 | 47853.582 | 0 | 143200.457 | 2729.127 | 17.317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 75968.62 | 2976.23 | 0 | 78944.85
Cost per Total Building Area ($/m2) | 15.25 | 0.6 | 0 | 15.85
Cost per Net Conditioned Building Area ($/m2) | 15.25 | 0.6 | 0 | 15.85
7-sanfrancisco
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 2912.42 | 584.57 | 584.57
Net Site Energy | 2912.42 | 584.57 | 584.57
Total Source Energy | 7775.43 | 1560.65 | 1560.65
Net Source Energy | 7775.43 | 1560.65 | 1560.65
Area (m2)
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 580.3 | 0 | 0 | 0 | 0
Cooling | 479.25 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 42.85 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 809.46 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 408.76 | 0 | 0 | 0 | 0 | 0
Pumps | 1.2 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 38.02 | 0 | 0 | 0 | 174.77
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2294.09 | 618.33 | 0 | 0 | 0 | 174.77
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 2294.09 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 2294.09 | 100
Total On-Site and Utility Electric Sources | 2294.09 | 100
Total Electricity End Uses | 2294.09 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 983.54 | 0 | 180
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1660.73 | 0 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 65.28 | 6.88 | 0.34 | 0.34 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_EAST | 43.52 | 6.88 | 0.34 | 0.34 | No | PERIMETER_BOT_ZN_2_WALL_EAST
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_NORTH | 65.28 | 6.88 | 0.34 | 0.34 | No | PERIMETER_BOT_ZN_3_WALL_NORTH
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 43.52 | 6.88 | 0.34 | 0.34 | No | PERIMETER_BOT_ZN_4_WALL_WEST
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 65.28 | 6.88 | 0.34 | 0.34 | No | PERIMETER_MID_ZN_1_WALL_SOUTH
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_EAST | 43.52 | 6.88 | 0.34 | 0.34 | No | PERIMETER_MID_ZN_2_WALL_EAST
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_NORTH | 65.28 | 6.88 | 0.34 | 0.34 | No | PERIMETER_MID_ZN_3_WALL_NORTH
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 43.52 | 6.88 | 0.34 | 0.34 | No | PERIMETER_MID_ZN_4_WALL_WEST
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 65.28 | 6.88 | 0.34 | 0.34 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_EAST | 43.52 | 6.88 | 0.34 | 0.34 | No | PERIMETER_TOP_ZN_2_WALL_EAST
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_NORTH | 65.28 | 6.88 | 0.34 | 0.34 | No | PERIMETER_TOP_ZN_3_WALL_NORTH
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 43.52 | 6.88 | 0.34 | 0.34 | No | PERIMETER_TOP_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
HEATSYS1 BOILER | Boiler:HotWater | 1307227.56 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 98202.35 | 3
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 123945.94 | 3
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 116811.14 | 3
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
VAV_1 FAN | Fan:VariableVolume | 0.19 | 500 | 5.93 | 15936.53 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.19 | 500 | 7.49 | 20114.26 | 1 | Fan Energy
VAV_3 FAN | Fan:VariableVolume | 0.19 | 500 | 7.06 | 18956.41 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.45 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 7690.86 | 0.85
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORE_BOTTOM VAV BOX REHEAT COIL | 0.003923 | 180391.95 | 6386.66
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | 0.001629 | 74900.52 | 2651.8
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | 0.000859 | 39514.53 | 1398.99
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | 0.000744 | 34195.22 | 1210.66
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | 0.001128 | 51881.12 | 1836.82
CORE_MID VAV BOX REHEAT COIL | 0.004916 | 226054.43 | 8003.31
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | 0.002001 | 92020.84 | 3257.94
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | 0.001103 | 50709.01 | 1795.32
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | 0.000871 | 40026.21 | 1417.1
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | 0.001354 | 62250.84 | 2203.95
CORE_TOP VAV BOX REHEAT COIL | 0.004234 | 194677.44 | 6892.42
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | 0.002019 | 92846.52 | 3287.17
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | 0.001034 | 47554.86 | 1683.65
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | 0.001194 | 54910.39 | 1944.07
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | 0.00142 | 65293.7 | 2311.68
Nominal Capacity [W]
VAV_1_HEATC | 10594.97
VAV_2_HEATC | 8650.75
VAV_3_HEATC | 9359.01
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 21660.0574 | 18.8419 | 147.3017 | 0 | 0.0001 | 888613.301 | 7945.9941
February | 17800.0174 | 15.3968 | 136.669 | 0 | 0.0001 | 824541.2963 | 6577.5876
March | 20847.3986 | 18.0414 | 158.5159 | 0 | 0.0001 | 956340.4767 | 7698.9455
April | 18470.9882 | 15.945 | 147.5751 | 0 | 0.0001 | 890362.8014 | 6843.0859
May | 19119.7853 | 16.4592 | 160.9672 | 0 | 0.0001 | 971192.9126 | 7108.4943
June | 18784.4532 | 16.1517 | 161.5107 | 0 | 0.0001 | 974484.9051 | 6994.0937
July | 17947.3898 | 15.414 | 157.5284 | 0 | 0.0001 | 950468.817 | 6692.2347
August | 19694.0467 | 16.9176 | 172.2334 | 0 | 0.0001 | 1039190.8662 | 7341.6198
September | 18059.2731 | 15.5107 | 158.3969 | 0 | 0.0001 | 955708.6409 | 6733.6075
October | 18690.0029 | 16.083 | 158.4608 | 0 | 0.0001 | 956075.0479 | 6952.0992
November | 19030.2527 | 16.4434 | 149.2496 | 0 | 0.0001 | 900454.7958 | 7041.7572
December | 20940.0786 | 18.1951 | 146.0714 | 0 | 0.0001 | 881208.028 | 7693.0546
Annual Sum or Average | 231043.7438 | 199.3996 | 1854.4802 | 0 | 0.0009 | 11188600 | 85622.574
Minimum of Months | 17800.0174 | 15.3968 | 136.669 | 0 | 0.0001 | 824541.2963 | 6577.5876
Maximum of Months | 21660.0574 | 18.8419 | 172.2334 | 0 | 0.0001 | 1039190.8662 | 7945.9941
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 182199000000 | 154348.983 | 06-JAN-16:15 | 48247.488 | 51263.506 | 23127.2 | 0 | 31694.803 | 0 | 15.985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 169062000000 | 163594.02 | 15-FEB-16:15 | 48247.488 | 51263.506 | 23310.488 | 0 | 40764.089 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 196086000000 | 159073.272 | 01-MAR-13:15 | 48247.488 | 51919.067 | 23390.846 | 0 | 35505.417 | 0 | 10.454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 182558000000 | 160938.699 | 13-APR-15:15 | 48247.488 | 51263.506 | 23741.539 | 0 | 37677.717 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 199131000000 | 169424.876 | 25-MAY-15:00 | 48247.488 | 51263.506 | 23577.673 | 0 | 46327.76 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 199806000000 | 172402.318 | 16-JUN-15:00 | 48247.488 | 51263.506 | 24000.04 | 0 | 48882.834 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 194882000000 | 189532.109 | 03-JUL-12:00 | 48247.488 | 51919.067 | 25050.39 | 0 | 64306.716 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 213073000000 | 176470.799 | 15-AUG-12:15 | 48247.488 | 51919.067 | 23686.394 | 0 | 52609.402 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 195956000000 | 196980.769 | 28-SEP-15:30 | 48247.488 | 51263.506 | 26068.512 | 0 | 71392.813 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 196031000000 | 171123.063 | 31-OCT-13:15 | 48247.488 | 51919.067 | 23835.139 | 0 | 47112.921 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 184627000000 | 160837.55 | 16-NOV-16:00 | 48247.488 | 51263.506 | 23148.507 | 0 | 35420.485 | 2729.127 | 28.436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 180681000000 | 154864.232 | 14-DEC-16:00 | 48247.488 | 51263.506 | 23104.685 | 0 | 29473.805 | 2729.127 | 45.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2294090000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 169062000000 | 154348.983 |  | 48247.488 | 51263.506 | 23104.685 | 0 | 29473.805 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 213073000000 | 196980.769 |  | 48247.488 | 51919.067 | 26068.512 | 0 | 71392.813 | 2729.127 | 45.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 94890.49 | 5288.98 | 0 | 100179.46
Cost per Total Building Area ($/m2) | 19.05 | 1.06 | 0 | 20.11
Cost per Net Conditioned Building Area ($/m2) | 19.05 | 1.06 | 0 | 20.11
8-baltimore
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 3431.81 | 688.82 | 688.82
Net Site Energy | 3431.81 | 688.82 | 688.82
Total Source Energy | 10163.54 | 2039.98 | 2039.98
Net Source Energy | 10163.54 | 2039.98 | 2039.98
Area (m2)
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 810.39 | 0 | 0 | 0 | 0
Cooling | 652.71 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 42.89 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 809.46 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 523.76 | 0 | 0 | 0 | 0 | 0
Pumps | 1.54 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 38.48 | 0 | 0 | 0 | 174.77
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2582.93 | 848.87 | 0 | 0 | 0 | 174.77
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 2582.93 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 2582.93 | 100
Total On-Site and Utility Electric Sources | 2582.93 | 100
Total Electricity End Uses | 2582.93 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 983.54 | 0 | 180
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1660.73 | 0 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_2_WALL_EAST
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_3_WALL_NORTH
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_4_WALL_WEST
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_1_WALL_SOUTH
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_2_WALL_EAST
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_3_WALL_NORTH
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_4_WALL_WEST
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_2_WALL_EAST
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_3_WALL_NORTH
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
HEATSYS1 BOILER | Boiler:HotWater | 1571598.37 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 127260.37 | 3
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 157506.12 | 3
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 171474.89 | 3
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
VAV_1 FAN | Fan:VariableVolume | 0.19 | 500 | 6.97 | 18729.44 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.19 | 500 | 8.8 | 23634.26 | 1 | Fan Energy
VAV_3 FAN | Fan:VariableVolume | 0.19 | 500 | 9.34 | 25078.56 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.45 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 9246.24 | 0.85
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORE_BOTTOM VAV BOX REHEAT COIL | 0.004204 | 193292.82 | 6843.4
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | 0.001529 | 70312.93 | 2489.38
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | 0.00125 | 57454.19 | 2034.13
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | 0.001026 | 47169.33 | 1670
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | 0.001484 | 68220.49 | 2415.3
CORE_MID VAV BOX REHEAT COIL | 0.005294 | 243407.85 | 8617.69
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | 0.001953 | 89794.69 | 3179.12
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | 0.001563 | 71874.71 | 2544.68
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | 0.001411 | 64884.98 | 2297.21
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | 0.001757 | 80783.91 | 2860.1
CORE_TOP VAV BOX REHEAT COIL | 0.005477 | 251823.98 | 8915.66
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | 0.00209 | 96119.32 | 3403.04
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | 0.00157 | 72209.98 | 2556.55
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | 0.001653 | 75999.41 | 2690.71
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | 0.001919 | 88249.8 | 3124.42
Nominal Capacity [W]
VAV_1_HEATC | 24476.76
VAV_2_HEATC | 22072.83
VAV_3_HEATC | 21369.46
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 42231.8197 | 72.5283 | 188.9846 | 0 | 0.0008 | 11750.4586 | 17743.1537
February | 36177.4723 | 64.0348 | 172.4057 | 0 | 0.0007 | 10720.387 | 15373.6078
March | 39433.8885 | 73.4062 | 207.8429 | 0 | 0.0008 | 12925.2529 | 17087.2728
April | 35798.6884 | 68.4966 | 198.9384 | 0 | 0.0008 | 12372.1261 | 15681.918
May | 39006.2035 | 76.673 | 228.0225 | 0 | 0.0009 | 14181.5356 | 17273.4538
June | 42574.208 | 84.8126 | 255.0986 | 0 | 0.001 | 15865.8366 | 18956.4786
July | 43355.2346 | 86.4812 | 260.4009 | 0 | 0.001 | 16195.6429 | 19314.5442
August | 46660.2508 | 93.0271 | 279.9936 | 0 | 0.0011 | 17414.1974 | 20782.641
September | 38496.9769 | 76.1531 | 227.7022 | 0 | 0.0009 | 14161.7607 | 17091.9409
October | 37860.2478 | 73.301 | 215.1429 | 0 | 0.0009 | 13380.1673 | 16663.6298
November | 37257.1404 | 69.7286 | 198.4377 | 0 | 0.0008 | 12340.4867 | 16178.2965
December | 39565.3326 | 69.6332 | 186.3521 | 0 | 0.0008 | 11587.4388 | 16776.8678
Annual Sum or Average | 478417.4636 | 908.2757 | 2619.3222 | 0 | 0.0106 | 162895.2906 | 208923.805
Minimum of Months | 35798.6884 | 64.0348 | 172.4057 | 0 | 0.0007 | 10720.387 | 15373.6078
Maximum of Months | 46660.2508 | 93.0271 | 279.9936 | 0 | 0.0011 | 17414.1974 | 20782.641
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 186320000000 | 168259.405 | 09-JAN-08:00 | 48247.488 | 58802.451 | 28196.519 | 0 | 32919.167 | 0 | 93.779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 169987000000 | 161376.815 | 15-FEB-13:00 | 48247.488 | 51919.067 | 28216.965 | 0 | 32963.82 | 0 | 29.475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 204948000000 | 182790.838 | 09-MAR-16:15 | 48247.488 | 51263.506 | 28284.014 | 0 | 54986.488 | 0 | 9.342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 196177000000 | 183313.378 | 04-APR-15:00 | 48247.488 | 51263.506 | 28408.261 | 0 | 55385.674 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 224868000000 | 204148.638 | 31-MAY-15:45 | 48247.488 | 51263.506 | 28660.198 | 0 | 75968.996 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 251575000000 | 239339.755 | 30-JUN-15:30 | 48247.488 | 51263.506 | 30533.171 | 0 | 109287.14 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 256805000000 | 249025.329 | 25-JUL-12:00 | 48247.488 | 51919.067 | 30664.764 | 0 | 118185.561 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 276127000000 | 249021.984 | 17-AUG-15:15 | 48247.488 | 51263.506 | 30951.333 | 0 | 118551.208 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 224555000000 | 213747.442 | 08-SEP-15:15 | 48247.488 | 51263.506 | 30282.706 | 0 | 83945.293 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 212161000000 | 197960.811 | 12-OCT-15:15 | 48247.488 | 51263.506 | 29558.769 | 0 | 68882.599 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 195676000000 | 190751.079 | 03-NOV-13:00 | 48247.488 | 51919.067 | 28946.649 | 0 | 61629.426 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 183735000000 | 157436.344 | 08-DEC-08:00 | 48247.488 | 58802.451 | 28196.519 | 0 | 22111.691 | 0 | 78.194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2582930000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 169987000000 | 157436.344 |  | 48247.488 | 51263.506 | 28196.519 | 0 | 22111.691 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 276127000000 | 249025.329 |  | 48247.488 | 58802.451 | 30951.333 | 0 | 118551.208 | 0 | 93.779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 55632.48 | 8239.29 | 0 | 63871.77
Cost per Total Building Area ($/m2) | 11.17 | 1.65 | 0 | 12.82
Cost per Net Conditioned Building Area ($/m2) | 11.17 | 1.65 | 0 | 12.82
9-albuquerque
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 3246.55 | 651.63 | 651.63
Net Site Energy | 3246.55 | 651.63 | 651.63
Total Source Energy | 9500.1 | 1906.81 | 1906.81
Net Source Energy | 9500.1 | 1906.81 | 1906.81
Area (m2)
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 533.49 | 0 | 0 | 0 | 0
Cooling | 670.22 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 42.88 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 809.46 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 598.9 | 0 | 0 | 0 | 0 | 0
Pumps | 1.1 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 37.92 | 0 | 0 | 0 | 174.77
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2675.14 | 571.41 | 0 | 0 | 0 | 174.77
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 2675.14 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 2675.14 | 100
Total On-Site and Utility Electric Sources | 2675.14 | 100
Total Electricity End Uses | 2675.14 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 983.54 | 0 | 180
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1660.73 | 0 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_2_WALL_EAST
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_3_WALL_NORTH
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_4_WALL_WEST
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_1_WALL_SOUTH
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_2_WALL_EAST
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_3_WALL_NORTH
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_4_WALL_WEST
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_2_WALL_EAST
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_3_WALL_NORTH
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
HEATSYS1 BOILER | Boiler:HotWater | 1492528.12 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 132801.42 | 3
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 167560.27 | 3
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 176885.3 | 3
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
VAV_1 FAN | Fan:VariableVolume | 0.19 | 500 | 8.02 | 21551.35 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.19 | 500 | 10.12 | 27192.11 | 1 | Fan Energy
VAV_3 FAN | Fan:VariableVolume | 0.19 | 500 | 10.69 | 28705.4 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.45 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8781.04 | 0.85
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORE_BOTTOM VAV BOX REHEAT COIL | 0.004029 | 185252.32 | 6558.73
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | 0.001334 | 61335.33 | 2171.54
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | 0.001179 | 54218.09 | 1919.56
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | 0.00102 | 46884.25 | 1659.91
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | 0.001471 | 67629.25 | 2394.37
CORE_MID VAV BOX REHEAT COIL | 0.00509 | 234026.8 | 8285.56
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | 0.001762 | 81002.9 | 2867.85
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | 0.001501 | 69008.18 | 2443.19
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | 0.00129 | 59325.9 | 2100.39
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | 0.001754 | 80659.25 | 2855.69
CORE_TOP VAV BOX REHEAT COIL | 0.005099 | 234470.62 | 8301.27
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | 0.001878 | 86337.37 | 3056.72
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | 0.001484 | 68256.41 | 2416.57
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | 0.001657 | 76191.33 | 2697.5
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | 0.001912 | 87930.12 | 3113.11
Nominal Capacity [W]
VAV_1_HEATC | 17201.76
VAV_2_HEATC | 15009.03
VAV_3_HEATC | 14413.03
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 60438.4714 | 100.4878 | 247.2161 | 0 | 0.001 | 257031.5584 | 25393.4034
February | 53066.335 | 89.422 | 223.5104 | 0 | 0.0009 | 232393.0669 | 22412.8536
March | 61275.2263 | 104.4198 | 264.391 | 0 | 0.001 | 274906.3298 | 25994.1962
April | 56474.742 | 97.6664 | 251.4024 | 0 | 0.001 | 261410.7542 | 24097.7241
May | 62446.2762 | 109.1075 | 284.0149 | 0 | 0.0011 | 295328.8446 | 26755.0474
June | 66149.2405 | 115.8566 | 302.3676 | 0 | 0.0012 | 314414.4097 | 28368.9635
July | 68123.4477 | 119.3812 | 311.7534 | 0 | 0.0012 | 324174.5297 | 29222.1824
August | 71909.5106 | 125.9767 | 328.867 | 0 | 0.0013 | 341969.7748 | 30842.3976
September | 61451.6038 | 107.4723 | 280.0468 | 0 | 0.0011 | 291203.3406 | 26338.9541
October | 59567.6605 | 103.0673 | 265.4521 | 0 | 0.001 | 276020.1483 | 25422.5682
November | 57422.5549 | 97.4683 | 245.6772 | 0 | 0.001 | 255445.7017 | 24321.9345
December | 58752.9092 | 97.6999 | 240.4007 | 0 | 0.0009 | 249945.6793 | 24686.6447
Annual Sum or Average | 737077.9781 | 1268.0259 | 3245.0997 | 0 | 0.0127 | 3374244.1379 | 313856.8699
Minimum of Months | 53066.335 | 89.422 | 223.5104 | 0 | 0.0009 | 232393.0669 | 22412.8536
Maximum of Months | 71909.5106 | 125.9767 | 328.867 | 0 | 0.0013 | 341969.7748 | 30842.3976
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 203778000000 | 172993.208 | 27-JAN-13:00 | 48247.488 | 51919.067 | 33729.291 | 0 | 39084.414 | 0 | 12.948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 184244000000 | 177397.434 | 14-FEB-16:15 | 48247.488 | 51263.506 | 33454.261 | 0 | 44423.73 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 217949000000 | 178820.584 | 02-MAR-16:15 | 48247.488 | 51263.506 | 33584.907 | 0 | 45716.233 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 207250000000 | 191717.309 | 21-APR-15:30 | 48247.488 | 51263.506 | 34460.327 | 0 | 57737.538 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 234140000000 | 206248.601 | 31-MAY-15:00 | 48247.488 | 51263.506 | 35182.782 | 0 | 71546.376 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 249272000000 | 227697.394 | 29-JUN-15:30 | 48247.488 | 51263.506 | 37082.04 | 0 | 91095.911 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 257009000000 | 239449.769 | 03-JUL-15:30 | 48247.488 | 51263.506 | 38245.687 | 0 | 101684.639 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 271118000000 | 238903.411 | 01-AUG-15:15 | 48247.488 | 51263.506 | 37305.89 | 0 | 102078.078 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 230870000000 | 207121.003 | 05-SEP-12:00 | 48247.488 | 51919.067 | 34454.039 | 0 | 72491.959 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 218832000000 | 196028.079 | 11-OCT-15:00 | 48247.488 | 51263.506 | 34262.226 | 0 | 62246.41 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 202520000000 | 177964.248 | 10-NOV-13:00 | 48247.488 | 51919.067 | 33619.141 | 0 | 44169.477 | 0 | 9.076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 198160000000 | 171434.007 | 05-DEC-13:00 | 48247.488 | 51919.067 | 33401.208 | 0 | 37844.311 | 0 | 21.933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2675140000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 184244000000 | 171434.007 |  | 48247.488 | 51263.506 | 33401.208 | 0 | 37844.311 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 271118000000 | 239449.769 |  | 48247.488 | 51919.067 | 38245.687 | 0 | 102078.078 | 0 | 21.933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 27633.42 | 3944.2 | 0 | 31577.62
Cost per Total Building Area ($/m2) | 5.55 | 0.79 | 0 | 6.34
Cost per Net Conditioned Building Area ($/m2) | 5.55 | 0.79 | 0 | 6.34
10-seattle
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 3194.71 | 641.23 | 641.23
Net Site Energy | 3194.71 | 641.23 | 641.23
Total Source Energy | 5023.44 | 1008.28 | 1008.28
Net Source Energy | 5023.44 | 1008.28 | 1008.28
Area (m2)
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 793.4 | 0 | 0 | 0 | 0
Cooling | 479.84 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 42.82 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 809.46 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 475.12 | 0 | 0 | 0 | 0 | 0
Pumps | 1.45 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 40.05 | 0 | 0 | 0 | 174.77
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2361.26 | 833.45 | 0 | 0 | 0 | 174.77
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 2361.26 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 2361.26 | 100
Total On-Site and Utility Electric Sources | 2361.26 | 100
Total Electricity End Uses | 2361.26 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 983.54 | 0 | 180
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 91.28 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40.57 | 270 | 90 | W
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1660.73 | 0 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_2_WALL_EAST
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_3_WALL_NORTH
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_4_WALL_WEST
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_1_WALL_SOUTH
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_2_WALL_EAST
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_3_WALL_NORTH
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_4_WALL_WEST
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_2_WALL_EAST
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_3_WALL_NORTH
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
HEATSYS1 BOILER | Boiler:HotWater | 1458979.66 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 110611.26 | 3
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 138604.17 | 3
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 135861.98 | 3
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
VAV_1 FAN | Fan:VariableVolume | 0.19 | 500 | 6.68 | 17950.28 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.19 | 500 | 8.37 | 22493.04 | 1 | Fan Energy
VAV_3 FAN | Fan:VariableVolume | 0.19 | 500 | 8.21 | 22048.03 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.45 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8583.67 | 0.85
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORE_BOTTOM VAV BOX REHEAT COIL | 0.004058 | 186581.59 | 6605.8
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | 0.001829 | 84076.76 | 2976.68
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | 0.001094 | 50290.74 | 1780.51
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | 0.000774 | 35572.56 | 1259.42
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | 0.001352 | 62181.19 | 2201.48
CORE_MID VAV BOX REHEAT COIL | 0.005066 | 232950.63 | 8247.46
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | 0.002242 | 103100.93 | 3650.22
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | 0.001375 | 63212.75 | 2238.01
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | 0.001009 | 46409.41 | 1643.09
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | 0.001606 | 73829.72 | 2613.89
CORE_TOP VAV BOX REHEAT COIL | 0.004675 | 214949 | 7610.12
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | 0.002278 | 104736.19 | 3708.11
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | 0.001308 | 60126.72 | 2128.75
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | 0.001371 | 63017.16 | 2231.08
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | 0.001695 | 77944.29 | 2759.57
Nominal Capacity [W]
VAV_1_HEATC | 17669.63
VAV_2_HEATC | 15426.5
VAV_3_HEATC | 15705.75
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 16750.8696 | 21.4307 | 39.82 | 0 | 0.0002 | 525824.3049 | 6464.2732
February | 13307.9062 | 17.7455 | 36.2302 | 0 | 0.0002 | 478553.2806 | 5212.6855
March | 14676.473 | 20.0162 | 42.8018 | 0 | 0.0002 | 565426.0339 | 5796.4854
April | 12319.333 | 17.4104 | 39.816 | 0 | 0.0002 | 526073.4686 | 4930.7571
May | 11611.3957 | 17.503 | 44.5072 | 0 | 0.0002 | 588203.502 | 4764.4803
June | 11072.8694 | 17.1267 | 45.2233 | 0 | 0.0002 | 597716.9673 | 4590.1458
July | 10664.7853 | 16.7511 | 45.1887 | 0 | 0.0002 | 597286.2782 | 4448.3548
August | 11606.6763 | 18.2299 | 49.1757 | 0 | 0.0002 | 649985.4489 | 4841.1583
September | 11386.7513 | 17.1926 | 43.8264 | 0 | 0.0002 | 579209.0609 | 4675.3262
October | 12792.421 | 18.2313 | 42.317 | 0 | 0.0002 | 559138.3517 | 5136.4123
November | 14420.5932 | 19.2559 | 39.4293 | 0 | 0.0002 | 520813.7862 | 5651.3729
December | 16294.7329 | 20.8652 | 38.8506 | 0 | 0.0002 | 513027.6491 | 6290.176
Annual Sum or Average | 156904.807 | 221.7586 | 507.1861 | 0 | 0.0021 | 6701258.1321 | 62801.6278
Minimum of Months | 10664.7853 | 16.7511 | 36.2302 | 0 | 0.0002 | 478553.2806 | 4448.3548
Maximum of Months | 16750.8696 | 21.4307 | 49.1757 | 0 | 0.0002 | 649985.4489 | 6464.2732
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 185280000000 | 154291.515 | 27-JAN-16:00 | 48247.488 | 51263.506 | 26174.297 | 0 | 25820.44 | 2729.127 | 56.657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 168623000000 | 158360.355 | 22-FEB-08:00 | 48247.488 | 58802.451 | 26171.509 | 0 | 25081.485 | 0 | 57.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 199234000000 | 166014.731 | 29-MAR-12:00 | 48247.488 | 51919.067 | 26840.494 | 0 | 38999.219 | 0 | 8.463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 185368000000 | 165704.242 | 18-APR-15:45 | 48247.488 | 51263.506 | 26767.533 | 0 | 39417.265 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 207260000000 | 180050.706 | 04-MAY-15:15 | 48247.488 | 51263.506 | 27371.016 | 0 | 53160.247 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 210612000000 | 188509.956 | 28-JUN-15:15 | 48247.488 | 51263.506 | 27885.104 | 0 | 61105.409 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 210460000000 | 202226.615 | 24-JUL-15:15 | 48247.488 | 51263.506 | 28646.816 | 0 | 74060.355 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 229029000000 | 199484.531 | 07-AUG-15:15 | 48247.488 | 51263.506 | 28958.505 | 0 | 71006.582 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 204091000000 | 194193.372 | 01-SEP-15:45 | 48247.488 | 51263.506 | 27805.191 | 0 | 66868.737 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 197018000000 | 169832.523 | 10-OCT-07:45 | 48247.488 | 58802.451 | 26294.118 | 0 | 36444.462 | 0 | 44.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 183514000000 | 167260.769 | 03-NOV-08:00 | 48247.488 | 58802.451 | 26171.509 | 0 | 33984.462 | 0 | 54.859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 180771000000 | 155125.451 | 05-DEC-08:00 | 48247.488 | 58802.451 | 26171.509 | 0 | 21800.552 | 0 | 103.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2361260000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 168623000000 | 154291.515 |  | 48247.488 | 51263.506 | 26171.509 | 0 | 21800.552 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 229029000000 | 202226.615 |  | 48247.488 | 58802.451 | 28958.505 | 0 | 74060.355 | 2729.127 | 103.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 50043.83 | 7011.93 | 0 | 57055.76
Cost per Total Building Area ($/m2) | 10.04 | 1.41 | 0 | 11.45
Cost per Net Conditioned Building Area ($/m2) | 10.04 | 1.41 | 0 | 11.45
11-chicago
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 3597.35 | 722.04 | 722.04
Net Site Energy | 3597.35 | 722.04 | 722.04
Total Source Energy | 10041.23 | 2015.43 | 2015.43
Net Source Energy | 10041.23 | 2015.43 | 2015.43
Area (m2)
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 1065.24 | 0 | 0 | 0 | 0
Cooling | 552.27 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 42.83 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 809.46 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 531.89 | 0 | 0 | 0 | 0 | 0
Pumps | 1.98 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 41.11 | 0 | 0 | 0 | 174.77
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2491 | 1106.35 | 0 | 0 | 0 | 174.77
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 2491 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 2491 | 100
Total On-Site and Utility Electric Sources | 2491 | 100
Total Electricity End Uses | 2491 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 983.54 | 0 | 180
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 270 | 90 | W
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1660.73 | 0 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_2_WALL_EAST
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_3_WALL_NORTH
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_4_WALL_WEST
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_1_WALL_SOUTH
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_2_WALL_EAST
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_3_WALL_NORTH
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_4_WALL_WEST
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_2_WALL_EAST
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_3_WALL_NORTH
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
HEATSYS1 BOILER | Boiler:HotWater | 1560033.88 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 124989.91 | 3
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 155878.23 | 3
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 168718.33 | 3
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
VAV_1 FAN | Fan:VariableVolume | 0.19 | 500 | 6.91 | 18550.69 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.19 | 500 | 8.79 | 23620.38 | 1 | Fan Energy
VAV_3 FAN | Fan:VariableVolume | 0.19 | 500 | 9.14 | 24564.35 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.45 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 9178.2 | 0.85
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORE_BOTTOM VAV BOX REHEAT COIL | 0.004176 | 192025.18 | 6798.52
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | 0.001522 | 69979.43 | 2477.57
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | 0.001171 | 53825.48 | 1905.65
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | 0.001089 | 50056.88 | 1772.23
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | 0.001408 | 64737.98 | 2292
CORE_MID VAV BOX REHEAT COIL | 0.005268 | 242243.88 | 8576.48
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | 0.00195 | 89671.39 | 3174.76
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | 0.00149 | 68516.51 | 2425.78
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | 0.001378 | 63373.35 | 2243.69
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | 0.001682 | 77339.67 | 2738.16
CORE_TOP VAV BOX REHEAT COIL | 0.005481 | 252025.03 | 8922.78
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | 0.002067 | 95041.92 | 3364.9
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | 0.001483 | 68176.44 | 2413.74
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | 0.001934 | 88907.54 | 3147.71
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | 0.001829 | 84113.21 | 2977.97
Nominal Capacity [W]
VAV_1_HEATC | 34234.58
VAV_2_HEATC | 31916.4
VAV_3_HEATC | 31446.55
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 76577.1294 | 126.8005 | 343.7628 | 0 | 0.0011 | 79121.6893 | 31981.1042
February | 65370.2839 | 110.5937 | 307.5425 | 0 | 0.0009 | 70788.8267 | 27525.4589
March | 73748.7597 | 127.8413 | 365.3811 | 0 | 0.0011 | 84106.4948 | 31347.1809
April | 69321.6898 | 123.0077 | 360.4757 | 0 | 0.0011 | 82981.4202 | 29737.0227
May | 76714.1681 | 138.3599 | 412.3135 | 0 | 0.0012 | 94917.5129 | 33121.8478
June | 83077.0428 | 151.004 | 453.5146 | 0 | 0.0014 | 104403.8493 | 35980.7486
July | 84305.2017 | 153.3163 | 460.6984 | 0 | 0.0014 | 106057.747 | 36520.3107
August | 88121.5769 | 160.1809 | 481.0992 | 0 | 0.0014 | 110754.1243 | 38166.2855
September | 76000.2817 | 137.5491 | 411.3343 | 0 | 0.0012 | 94692.7296 | 32859.2009
October | 72676.6624 | 129.7017 | 382.3628 | 0 | 0.0012 | 88020.8299 | 31247.0411
November | 69276.5507 | 120.4823 | 345.5823 | 0 | 0.0011 | 79549.6232 | 29483.8666
December | 73626.6724 | 123.3938 | 339.3831 | 0 | 0.001 | 78115.9803 | 30890.2893
Annual Sum or Average | 908816.0196 | 1602.2313 | 4663.4504 | 0 | 0.0142 | 1073510.8276 | 388860.3573
Minimum of Months | 65370.2839 | 110.5937 | 307.5425 | 0 | 0.0009 | 70788.8267 | 27525.4589
Maximum of Months | 88121.5769 | 160.1809 | 481.0992 | 0 | 0.0014 | 110754.1243 | 38166.2855
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 183596000000 | 156696.323 | 18-JAN-08:00 | 48247.488 | 58802.451 | 27991.524 | 0 | 21554.469 | 0 | 100.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 164260000000 | 156749.421 | 28-FEB-08:00 | 48247.488 | 58802.451 | 27991.524 | 0 | 21634.169 | 0 | 73.788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 195163000000 | 169267.289 | 31-MAR-15:15 | 48247.488 | 51263.506 | 28139.459 | 0 | 41608.387 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 192552000000 | 178115.535 | 10-APR-07:00 | 48247.488 | 58802.451 | 27991.524 | 0 | 43023.613 | 0 | 50.458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 220249000000 | 204527.421 | 30-MAY-15:00 | 48247.488 | 51263.506 | 28836.461 | 0 | 76171.517 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 242261000000 | 230580.652 | 08-JUN-12:00 | 48247.488 | 51919.067 | 29487.613 | 0 | 100918.035 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 246099000000 | 240125.49 | 03-JUL-15:15 | 48247.488 | 51263.506 | 31628.318 | 0 | 108977.728 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 256997000000 | 235610.51 | 04-AUG-15:30 | 48247.488 | 51263.506 | 30221.535 | 0 | 105869.531 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 219727000000 | 205935.459 | 05-SEP-15:15 | 48247.488 | 51263.506 | 30078.295 | 0 | 76337.72 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 204246000000 | 187354.956 | 31-OCT-08:45 | 48247.488 | 58802.451 | 28248.539 | 0 | 52037.078 | 0 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 184589000000 | 187558.049 | 02-NOV-08:45 | 48247.488 | 58802.451 | 28183.065 | 0 | 52292.571 | 0 | 32.473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 181262000000 | 160475.819 | 12-DEC-08:00 | 48247.488 | 58802.451 | 27991.524 | 0 | 25346.519 | 0 | 87.835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2491000000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 164260000000 | 156696.323 |  | 48247.488 | 51263.506 | 27991.524 | 0 | 21554.469 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 256997000000 | 240125.49 |  | 48247.488 | 58802.451 | 31628.318 | 0 | 108977.728 | 0 | 100.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 61659.17 | 9231.57 | 0 | 70890.75
Cost per Total Building Area ($/m2) | 12.38 | 1.85 | 0 | 14.23
Cost per Net Conditioned Building Area ($/m2) | 12.38 | 1.85 | 0 | 14.23
12-boulder
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 3383.5 | 679.12 | 679.12
Net Site Energy | 3383.5 | 679.12 | 679.12
Total Source Energy | 9381.14 | 1882.94 | 1882.94
Net Source Energy | 9381.14 | 1882.94 | 1882.94
Area (m2)
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 788.01 | 0 | 0 | 0 | 0
Cooling | 554.74 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 42.84 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 809.46 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 593.32 | 0 | 0 | 0 | 0 | 0
Pumps | 1.59 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 40.97 | 0 | 0 | 0 | 174.77
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2554.52 | 828.98 | 0 | 0 | 0 | 174.77
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 2554.52 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 2554.52 | 100
Total On-Site and Utility Electric Sources | 2554.52 | 100
Total Electricity End Uses | 2554.52 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 983.54 | 0 | 180
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 270 | 90 | W
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1660.73 | 0 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_2_WALL_EAST
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_3_WALL_NORTH
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_4_WALL_WEST
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_1_WALL_SOUTH
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_2_WALL_EAST
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_3_WALL_NORTH
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_4_WALL_WEST
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_2_WALL_EAST
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_3_WALL_NORTH
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
HEATSYS1 BOILER | Boiler:HotWater | 1473082.67 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 129918.91 | 3
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 164389.43 | 3
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 171319.79 | 3
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
VAV_1 FAN | Fan:VariableVolume | 0.19 | 500 | 7.85 | 21083.57 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.19 | 500 | 9.93 | 26677.53 | 1 | Fan Energy
VAV_3 FAN | Fan:VariableVolume | 0.19 | 500 | 10.35 | 27802.21 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.45 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8666.64 | 0.85
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORE_BOTTOM VAV BOX REHEAT COIL | 0.003998 | 183814.04 | 6507.81
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | 0.001418 | 65185.63 | 2307.85
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | 0.001083 | 49816.64 | 1763.72
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | 0.001014 | 46640.53 | 1651.28
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | 0.001392 | 63985.04 | 2265.35
CORE_MID VAV BOX REHEAT COIL | 0.00504 | 231739.3 | 8204.57
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | 0.001843 | 84737.1 | 3000.06
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | 0.001397 | 64236.75 | 2274.26
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | 0.00121 | 55629.37 | 1969.52
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | 0.001671 | 76815.9 | 2719.62
CORE_TOP VAV BOX REHEAT COIL | 0.005082 | 233688.36 | 8273.58
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | 0.001934 | 88942.7 | 3148.96
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | 0.001354 | 62253.25 | 2204.03
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | 0.001791 | 82363.26 | 2916.02
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | 0.00181 | 83234.81 | 2946.87
Nominal Capacity [W]
VAV_1_HEATC | 27166.66
VAV_2_HEATC | 25032.82
VAV_3_HEATC | 24564.8
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 61895.0913 | 100.7753 | 241.6222 | 0 | 0.001 | 251200.4303 | 25796.0522
February | 53164.7037 | 88.0141 | 215.4069 | 0 | 0.0009 | 223956.654 | 22300.0333
March | 60935.9399 | 102.7594 | 257.0695 | 0 | 0.001 | 267286.3712 | 25744.1094
April | 55374.3239 | 94.9846 | 242.2883 | 0 | 0.0009 | 251928.7341 | 23551.7802
May | 59922.2204 | 103.8298 | 267.839 | 0 | 0.001 | 278503.0184 | 25588.5112
June | 62050.8015 | 108.2834 | 281.4953 | 0 | 0.0011 | 292707.9945 | 26572.541
July | 64309.6674 | 112.6217 | 293.8886 | 0 | 0.0011 | 305597.5215 | 27578.7643
August | 67249.8841 | 117.6962 | 306.9215 | 0 | 0.0012 | 319149.1448 | 28832.3412
September | 58493.612 | 101.7773 | 263.7422 | 0 | 0.001 | 274245.8078 | 25019.9323
October | 58450.7144 | 100.4541 | 256.791 | 0 | 0.001 | 267009.8089 | 24879.115
November | 56939.6339 | 95.4784 | 237.2775 | 0 | 0.0009 | 246704.058 | 24002.6061
December | 59818.1307 | 97.5781 | 234.5123 | 0 | 0.0009 | 243810.0427 | 24948.5227
Annual Sum or Average | 718604.7232 | 1224.2522 | 3098.8542 | 0 | 0.0122 | 3222099.5861 | 304814.3089
Minimum of Months | 53164.7037 | 88.0141 | 215.4069 | 0 | 0.0009 | 223956.654 | 22300.0333
Maximum of Months | 67249.8841 | 117.6962 | 306.9215 | 0 | 0.0012 | 319149.1448 | 28832.3412
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 199155000000 | 168012.005 | 27-JAN-13:00 | 48247.488 | 51919.067 | 31770.953 | 0 | 36059.33 | 0 | 15.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 177556000000 | 167268.694 | 07-FEB-13:00 | 48247.488 | 51919.067 | 32332.269 | 0 | 34748.697 | 0 | 21.173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 211908000000 | 176927.857 | 27-MAR-12:00 | 48247.488 | 51919.067 | 32797.335 | 0 | 43955.518 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 199732000000 | 184191.225 | 26-APR-15:45 | 48247.488 | 51263.506 | 33125.735 | 0 | 51546.047 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 220801000000 | 197645.402 | 24-MAY-15:30 | 48247.488 | 51263.506 | 33496.157 | 0 | 64629.802 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 232062000000 | 210059.539 | 27-JUN-15:15 | 48247.488 | 51263.506 | 34593.384 | 0 | 75946.711 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 242281000000 | 224484.799 | 17-JUL-15:15 | 48247.488 | 51263.506 | 36309.529 | 0 | 88655.827 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 253025000000 | 221536.128 | 30-AUG-13:00 | 48247.488 | 48313.484 | 35302.74 | 0 | 89663.967 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 217425000000 | 200077.315 | 01-SEP-15:45 | 48247.488 | 51263.506 | 33960.996 | 0 | 66596.875 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 211689000000 | 191164.605 | 05-OCT-15:15 | 48247.488 | 51263.506 | 33903.752 | 0 | 57741.41 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 195590000000 | 173878.979 | 10-NOV-13:45 | 48247.488 | 51919.067 | 32554.918 | 0 | 41144.128 | 0 | 13.379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 193296000000 | 167667.959 | 21-DEC-13:00 | 48247.488 | 51919.067 | 32166.327 | 0 | 35310.98 | 0 | 24.098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2554520000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 177556000000 | 167268.694 |  | 48247.488 | 48313.484 | 31770.953 | 0 | 34748.697 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 253025000000 | 224484.799 |  | 48247.488 | 51919.067 | 36309.529 | 0 | 89663.967 | 0 | 24.098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 26396.11 | 5741.94 | 0 | 32138.05
Cost per Total Building Area ($/m2) | 5.3 | 1.15 | 0 | 6.45
Cost per Net Conditioned Building Area ($/m2) | 5.3 | 1.15 | 0 | 6.45
13-minneapolis
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 3992.54 | 801.36 | 801.36
Net Site Energy | 3992.54 | 801.36 | 801.36
Total Source Energy | 10184.37 | 2044.16 | 2044.16
Net Source Energy | 10184.37 | 2044.16 | 2044.16
Area (m2)
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 1465.36 | 0 | 0 | 0 | 0
Cooling | 507.99 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 42.87 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 809.46 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 568.2 | 0 | 0 | 0 | 0 | 0
Pumps | 2.71 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 43.38 | 0 | 0 | 0 | 174.77
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2483.8 | 1508.74 | 0 | 0 | 0 | 174.77
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 2483.8 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 2483.8 | 100
Total On-Site and Utility Electric Sources | 2483.8 | 100
Total Electricity End Uses | 2483.8 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 983.54 | 0 | 180
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 270 | 90 | W
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1660.73 | 0 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_2_WALL_EAST
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_3_WALL_NORTH
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_4_WALL_WEST
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_1_WALL_SOUTH
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_2_WALL_EAST
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_3_WALL_NORTH
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_4_WALL_WEST
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_2_WALL_EAST
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_3_WALL_NORTH
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
HEATSYS1 BOILER | Boiler:HotWater | 1599794.27 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 121802.1 | 3
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 153585.58 | 3
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 173851.56 | 3
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
VAV_1 FAN | Fan:VariableVolume | 0.19 | 500 | 6.92 | 18588.38 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.19 | 500 | 8.89 | 23885.83 | 1 | Fan Energy
VAV_3 FAN | Fan:VariableVolume | 0.19 | 500 | 9.76 | 26219.45 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.45 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 9412.13 | 0.85
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORE_BOTTOM VAV BOX REHEAT COIL | 0.004118 | 189342.27 | 6703.54
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | 0.001594 | 73301.02 | 2595.17
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | 0.001158 | 53266.43 | 1885.86
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | 0.001197 | 55034.44 | 1948.46
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | 0.00139 | 63911.34 | 2262.74
CORE_MID VAV BOX REHEAT COIL | 0.005248 | 241296.14 | 8542.93
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | 0.002031 | 93389.68 | 3306.4
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | 0.001476 | 67846.14 | 2402.05
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | 0.001387 | 63776.76 | 2257.97
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | 0.001668 | 76695.47 | 2715.35
CORE_TOP VAV BOX REHEAT COIL | 0.005974 | 274695.9 | 9725.42
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | 0.002149 | 98824.31 | 3498.81
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | 0.001468 | 67516.22 | 2390.37
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | 0.002125 | 97687.35 | 3458.56
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | 0.00181 | 83210.8 | 2946.02
Nominal Capacity [W]
VAV_1_HEATC | 39639.09
VAV_2_HEATC | 37256.21
VAV_3_HEATC | 36102.55
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 60723.0764 | 91.884 | 119.9938 | 0 | 0.0009 | 78807.606 | 24530.6374
February | 49197.9676 | 77.5655 | 107.3815 | 0 | 0.0008 | 70541.674 | 20173.093
March | 51400.0066 | 86.1588 | 128.8643 | 0 | 0.001 | 84680.1939 | 21565.5669
April | 45935.3708 | 80.3891 | 126.2036 | 0 | 0.0009 | 82946.6569 | 19596.8786
May | 51291.6944 | 92.2364 | 148.9735 | 0 | 0.0011 | 97922.0356 | 22118.4133
June | 53355.3639 | 96.9723 | 158.3045 | 0 | 0.0012 | 104059.2937 | 23106.2906
July | 53575.5973 | 97.5518 | 159.5416 | 0 | 0.0012 | 104873.1092 | 23218.7979
August | 57243.8081 | 104.1202 | 170.1043 | 0 | 0.0012 | 111816.0307 | 24797.9521
September | 48172.1288 | 86.6945 | 140.134 | 0 | 0.001 | 92111.9674 | 20779.6586
October | 48040.4125 | 83.8277 | 131.1881 | 0 | 0.001 | 86221.7412 | 20471.4768
November | 48702.6782 | 81.1123 | 120.392 | 0 | 0.0009 | 79110.5206 | 20383.6729
December | 55416.3093 | 86.3711 | 117.7033 | 0 | 0.0009 | 77317.287 | 22627.4331
Annual Sum or Average | 623054.414 | 1064.8838 | 1628.7845 | 0 | 0.012 | 1070408.116 | 263369.8713
Minimum of Months | 45935.3708 | 77.5655 | 107.3815 | 0 | 0.0008 | 70541.674 | 19596.8786
Maximum of Months | 60723.0764 | 104.1202 | 170.1043 | 0 | 0.0012 | 111816.0307 | 24797.9521
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 182867000000 | 147152.867 | 19-JAN-08:00 | 48247.488 | 58802.451 | 28831.541 | 0 | 11130.817 | 0 | 140.569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 163687000000 | 148208.703 | 21-FEB-08:00 | 48247.488 | 58802.451 | 28831.541 | 0 | 12136.873 | 0 | 190.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 196494000000 | 166983.809 | 23-MAR-15:30 | 48247.488 | 51263.506 | 29052.219 | 0 | 38407.851 | 0 | 12.745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 192471000000 | 172869.465 | 26-APR-12:00 | 48247.488 | 51919.067 | 29345.592 | 0 | 43347.463 | 0 | 9.855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 227221000000 | 202130.229 | 31-MAY-12:15 | 48247.488 | 51919.067 | 29755.602 | 0 | 72199.623 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 241462000000 | 230499.573 | 30-JUN-15:15 | 48247.488 | 51263.506 | 31788.926 | 0 | 99191.203 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 243350000000 | 226607.502 | 13-JUL-15:30 | 48247.488 | 51263.506 | 30165.287 | 0 | 96922.771 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 259461000000 | 224295.437 | 25-AUG-15:00 | 48247.488 | 51263.506 | 30319.885 | 0 | 94456.108 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 213739000000 | 204328.882 | 14-SEP-15:15 | 48247.488 | 51263.506 | 30300.501 | 0 | 74508.937 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 200071000000 | 176541.588 | 06-OCT-15:15 | 48247.488 | 51263.506 | 29454.285 | 0 | 47567.159 | 0 | 9.151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 183570000000 | 169849.932 | 02-NOV-13:00 | 48247.488 | 51919.067 | 29389.868 | 0 | 40274.748 | 0 | 18.761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 179409000000 | 148480.144 | 01-DEC-16:30 | 48247.488 | 51263.506 | 28841.41 | 0 | 17328.932 | 2729.127 | 69.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2483800000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 163687000000 | 147152.867 |  | 48247.488 | 51263.506 | 28831.541 | 0 | 11130.817 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 259461000000 | 230499.573 |  | 48247.488 | 58802.451 | 31788.926 | 0 | 99191.203 | 2729.127 | 190.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 42517.98 | 11892.79 | 0 | 54410.77
Cost per Total Building Area ($/m2) | 8.53 | 2.39 | 0 | 10.92
Cost per Net Conditioned Building Area ($/m2) | 8.53 | 2.39 | 0 | 10.92
14-helena
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 3785.39 | 759.79 | 759.79
Net Site Energy | 3785.39 | 759.79 | 759.79
Total Source Energy | 10061.16 | 2019.43 | 2019.43
Net Source Energy | 10061.16 | 2019.43 | 2019.43
Area (m2)
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 1255.23 | 0 | 0 | 0 | 0
Cooling | 475.8 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 42.81 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 809.46 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 603.34 | 0 | 0 | 0 | 0 | 0
Pumps | 2.38 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 43.79 | 0 | 0 | 0 | 174.77
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2486.37 | 1299.02 | 0 | 0 | 0 | 174.77
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 2486.37 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 2486.37 | 100
Total On-Site and Utility Electric Sources | 2486.37 | 100
Total Electricity End Uses | 2486.37 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 983.54 | 0 | 180
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 91.28 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40.57 | 270 | 90 | W
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1660.73 | 0 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_2_WALL_EAST
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_3_WALL_NORTH
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_4_WALL_WEST
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_1_WALL_SOUTH
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_2_WALL_EAST
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_3_WALL_NORTH
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_4_WALL_WEST
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_2_WALL_EAST
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 65.28 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_3_WALL_NORTH
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 43.52 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
HEATSYS1 BOILER | Boiler:HotWater | 1546993.73 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 123306.91 | 3
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 157124.37 | 3
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 177139.82 | 3
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
VAV_1 FAN | Fan:VariableVolume | 0.19 | 500 | 7.45 | 20010.56 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.19 | 500 | 9.49 | 25498.54 | 1 | Fan Energy
VAV_3 FAN | Fan:VariableVolume | 0.19 | 500 | 10.7 | 28746.7 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.45 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 9101.48 | 0.85
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORE_BOTTOM VAV BOX REHEAT COIL | 0.003969 | 182511.15 | 6461.68
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | 0.001579 | 72583.76 | 2569.78
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | 0.001077 | 49515.51 | 1753.06
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | 0.001179 | 54223.26 | 1919.74
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | 0.001355 | 62290.45 | 2205.35
CORE_MID VAV BOX REHEAT COIL | 0.005028 | 231207.09 | 8185.73
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | 0.002005 | 92184.69 | 3263.74
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | 0.00138 | 63459.14 | 2246.73
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | 0.001353 | 62216.67 | 2202.74
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | 0.001626 | 74763.49 | 2646.95
CORE_TOP VAV BOX REHEAT COIL | 0.005837 | 268373.57 | 9501.59
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | 0.00208 | 95620.24 | 3385.37
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | 0.001346 | 61902.47 | 2191.62
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | 0.002084 | 95834.97 | 3392.97
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | 0.001747 | 80307.27 | 2843.22
Nominal Capacity [W]
VAV_1_HEATC | 36030.68
VAV_2_HEATC | 33844.6
VAV_3_HEATC | 32416.45
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 60997.5378 | 94.8931 | 143.2209 | 0 | 0.001 | 3395794.8069 | 24932.0066
February | 52800.431 | 84.2621 | 131.6454 | 0 | 0.0009 | 3121736.548 | 21786.576
March | 56022.1154 | 93.6046 | 154.8713 | 0 | 0.0011 | 3673241.7867 | 23522.0076
April | 49483.0155 | 84.1902 | 142.2602 | 0 | 0.001 | 3374374.5928 | 20922.5362
May | 53221.4957 | 92.4768 | 159.9733 | 0 | 0.0011 | 3794819.0477 | 22689.4185
June | 55523.7596 | 97.4928 | 170.5666 | 0 | 0.0012 | 4046258.2586 | 23769.0989
July | 54851.5611 | 97.1041 | 171.3643 | 0 | 0.0012 | 4065295.4756 | 23557.853
August | 58407.5833 | 103.12 | 181.4636 | 0 | 0.0013 | 4304844.7044 | 25058.1067
September | 51715.6636 | 90.307 | 157.0629 | 0 | 0.0011 | 3725845.1417 | 22090.6398
October | 52182.5417 | 89.1202 | 151.2401 | 0 | 0.0011 | 3587426.4641 | 22096.5366
November | 52237.1799 | 86.543 | 141.7407 | 0 | 0.001 | 3361692.4784 | 21861.5351
December | 57268.4953 | 90.3682 | 139.081 | 0 | 0.001 | 3297876.362 | 23531.1784
Annual Sum or Average | 654711.3798 | 1103.4821 | 1844.4902 | 0 | 0.0129 | 43749200 | 275817.4933
Minimum of Months | 49483.0155 | 84.1902 | 131.6454 | 0 | 0.0009 | 3121736.548 | 20922.5362
Maximum of Months | 60997.5378 | 103.12 | 181.4636 | 0 | 0.0013 | 4304844.7044 | 25058.1067
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 192991000000 | 159708.168 | 10-JAN-08:15 | 48247.488 | 58802.451 | 31170.869 | 0 | 18611.42 | 2729.127 | 146.813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 177416000000 | 168413.77 | 02-FEB-16:15 | 48247.488 | 51263.506 | 31200.56 | 0 | 37679.951 | 0 | 22.265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 208759000000 | 175611.052 | 28-MAR-15:00 | 48247.488 | 51263.506 | 32213.908 | 0 | 43876.84 | 0 | 9.309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 191774000000 | 170121.915 | 06-APR-15:00 | 48247.488 | 51263.506 | 31380.487 | 0 | 39221.468 | 0 | 8.965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 215669000000 | 183206.445 | 17-MAY-15:45 | 48247.488 | 51263.506 | 32329.741 | 0 | 51357.261 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 229959000000 | 221552.13 | 26-JUN-15:15 | 48247.488 | 51263.506 | 34660.8 | 0 | 87371.886 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 231040000000 | 216250.742 | 21-JUL-15:45 | 48247.488 | 51263.506 | 34321.034 | 0 | 82410.264 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 244655000000 | 206495.222 | 09-AUG-15:00 | 48247.488 | 51263.506 | 33283.951 | 0 | 73691.828 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 211749000000 | 197184.804 | 01-SEP-15:00 | 48247.488 | 51263.506 | 33214.46 | 0 | 64450.901 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 203882000000 | 182785.07 | 06-OCT-15:15 | 48247.488 | 51263.506 | 32455.679 | 0 | 50809.947 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 191053000000 | 166448.512 | 21-NOV-08:00 | 48247.488 | 58802.451 | 31170.869 | 0 | 28158.661 | 0 | 69.043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 187426000000 | 160302.915 | 29-DEC-08:15 | 48247.488 | 58802.451 | 31170.869 | 0 | 19217.298 | 2729.127 | 135.682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2486370000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 177416000000 | 159708.168 |  | 48247.488 | 51263.506 | 31170.869 | 0 | 18611.42 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 244655000000 | 221552.13 |  | 48247.488 | 58802.451 | 34660.8 | 0 | 87371.886 | 2729.127 | 146.813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 53501.17 | 10564.17 | 0 | 64065.33
Cost per Total Building Area ($/m2) | 10.74 | 2.12 | 0 | 12.86
Cost per Net Conditioned Building Area ($/m2) | 10.74 | 2.12 | 0 | 12.86
15-duluth
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 4247.11 | 852.46 | 852.46
Net Site Energy | 4247.11 | 852.46 | 852.46
Total Source Energy | 10347.11 | 2076.82 | 2076.82
Net Source Energy | 10347.11 | 2076.82 | 2076.82
Area (m2)
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 1765.34 | 0 | 0 | 0 | 0
Cooling | 418.89 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 42.8 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 809.46 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 607.73 | 0 | 0 | 0 | 0 | 0
Pumps | 3.2 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 47.12 | 0 | 0 | 0 | 174.77
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2434.65 | 1812.46 | 0 | 0 | 0 | 174.77
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 2434.65 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 2434.65 | 100
Total On-Site and Utility Electric Sources | 2434.65 | 100
Total Electricity End Uses | 2434.65 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 983.54 | 0 | 180
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 91.28 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 40.57 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 40.57 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 40.57 | 270 | 90 | W
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1660.73 | 0 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 65.28 | 3.24 | 0.49 | 0.49 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 43.52 | 3.24 | 0.49 | 0.49 | No | PERIMETER_BOT_ZN_2_WALL_EAST
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_NORTH | 65.28 | 3.24 | 0.49 | 0.49 | No | PERIMETER_BOT_ZN_3_WALL_NORTH
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 43.52 | 3.24 | 0.49 | 0.49 | No | PERIMETER_BOT_ZN_4_WALL_WEST
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 65.28 | 3.24 | 0.49 | 0.49 | No | PERIMETER_MID_ZN_1_WALL_SOUTH
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 43.52 | 3.24 | 0.49 | 0.49 | No | PERIMETER_MID_ZN_2_WALL_EAST
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_NORTH | 65.28 | 3.24 | 0.49 | 0.49 | No | PERIMETER_MID_ZN_3_WALL_NORTH
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 43.52 | 3.24 | 0.49 | 0.49 | No | PERIMETER_MID_ZN_4_WALL_WEST
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 65.28 | 3.24 | 0.49 | 0.49 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 43.52 | 3.24 | 0.49 | 0.49 | No | PERIMETER_TOP_ZN_2_WALL_EAST
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_NORTH | 65.28 | 3.24 | 0.49 | 0.49 | No | PERIMETER_TOP_ZN_3_WALL_NORTH
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 43.52 | 3.24 | 0.49 | 0.49 | No | PERIMETER_TOP_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
HEATSYS1 BOILER | Boiler:HotWater | 1644352.22 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 120137.91 | 3
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 151307.96 | 3
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 170880.77 | 3
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
VAV_1 FAN | Fan:VariableVolume | 0.19 | 500 | 7.26 | 19496.28 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.19 | 500 | 9.14 | 24554.64 | 1 | Fan Energy
VAV_3 FAN | Fan:VariableVolume | 0.19 | 500 | 10.26 | 27562.91 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.45 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 9674.28 | 0.85
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORE_BOTTOM VAV BOX REHEAT COIL | 0.004064 | 186853.55 | 6615.42
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | 0.001691 | 77766.88 | 2753.28
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | 0.001259 | 57867.52 | 2048.76
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | 0.00122 | 56089.08 | 1985.8
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | 0.001536 | 70629.15 | 2500.58
CORE_MID VAV BOX REHEAT COIL | 0.005146 | 236628.18 | 8377.66
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | 0.002126 | 97745.43 | 3460.61
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | 0.001578 | 72546.91 | 2568.47
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | 0.001395 | 64161.85 | 2271.61
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | 0.001814 | 83429.32 | 2953.76
CORE_TOP VAV BOX REHEAT COIL | 0.006145 | 282549.83 | 10003.49
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | 0.002176 | 100053.44 | 3542.32
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | 0.00151 | 69416.99 | 2457.66
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | 0.002189 | 100644.56 | 3563.25
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | 0.001913 | 87969.54 | 3114.5
Nominal Capacity [W]
VAV_1_HEATC | 41461.54
VAV_2_HEATC | 39246.83
VAV_3_HEATC | 37813.82
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 60789.0469 | 92.2624 | 121.0313 | 0 | 0.0009 | 79490.5044 | 24583.9152
February | 52882.2444 | 82.0937 | 111.2537 | 0 | 0.0008 | 73078.9493 | 21561.3997
March | 53964.8994 | 88.5828 | 129.1881 | 0 | 0.001 | 84884.7175 | 22462.4388
April | 46451.6654 | 79.8708 | 122.9924 | 0 | 0.0009 | 80830.4029 | 19681.2324
May | 49272.1086 | 87.0009 | 137.8858 | 0 | 0.001 | 90627.852 | 21094.2173
June | 50678.207 | 91.6248 | 148.7924 | 0 | 0.0011 | 97804.8248 | 21900.8493
July | 52469.5382 | 95.1898 | 155.1145 | 0 | 0.0011 | 101961.761 | 22706.1807
August | 54840.9294 | 99.0562 | 160.7062 | 0 | 0.0012 | 105635.7216 | 23690.7494
September | 47893.991 | 84.9769 | 135.3623 | 0 | 0.001 | 88970.8638 | 20543.3566
October | 48619.6812 | 84.0231 | 130.1149 | 0 | 0.001 | 85513.1024 | 20640.3799
November | 52416.7212 | 85.7085 | 124.3976 | 0 | 0.0009 | 81735.5377 | 21786.1937
December | 57826.4048 | 89.2012 | 119.8062 | 0 | 0.0009 | 78693.8727 | 23522.9786
Annual Sum or Average | 628105.4374 | 1059.5912 | 1596.6454 | 0 | 0.0118 | 1049228.1101 | 264173.8916
Minimum of Months | 46451.6654 | 79.8708 | 111.2537 | 0 | 0.0008 | 73078.9493 | 19681.2324
Maximum of Months | 60789.0469 | 99.0562 | 160.7062 | 0 | 0.0012 | 105635.7216 | 24583.9152
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 184452000000 | 150180.921 | 13-JAN-16:45 | 48247.488 | 51263.506 | 30091.349 | 0 | 17761.967 | 2729.127 | 87.484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 169574000000 | 156445.067 | 28-FEB-13:45 | 48247.488 | 51919.067 | 30253.823 | 0 | 25982.348 | 0 | 42.341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 196969000000 | 156480.431 | 30-MAR-07:00 | 48247.488 | 58802.451 | 30091.349 | 0 | 19227.149 | 0 | 111.993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 187561000000 | 169540.325 | 04-APR-15:15 | 48247.488 | 51263.506 | 30377.759 | 0 | 39639.3 | 0 | 12.271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 210295000000 | 182143.578 | 31-MAY-15:00 | 48247.488 | 51263.506 | 30968.656 | 0 | 51655.478 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 226949000000 | 211556.678 | 14-JUN-15:15 | 48247.488 | 51263.506 | 31382.976 | 0 | 80654.259 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 236595000000 | 225687.676 | 06-JUL-15:30 | 48247.488 | 51263.506 | 32801.293 | 0 | 93366.94 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 245120000000 | 215650.352 | 11-AUG-15:30 | 48247.488 | 51263.506 | 31838.103 | 0 | 84292.806 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 206450000000 | 203879.549 | 07-SEP-15:15 | 48247.488 | 51263.506 | 31479.509 | 0 | 72880.596 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 198427000000 | 173694.821 | 06-OCT-15:15 | 48247.488 | 51263.506 | 30725.968 | 0 | 43447.752 | 0 | 10.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 189661000000 | 171592.214 | 09-NOV-08:00 | 48247.488 | 58802.451 | 30091.349 | 0 | 34367.837 | 0 | 83.088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 182603000000 | 147427.239 | 01-DEC-16:30 | 48247.488 | 51263.506 | 30091.349 | 0 | 15007.98 | 2729.127 | 87.789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2434650000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 169574000000 | 147427.239 |  | 48247.488 | 51263.506 | 30091.349 | 0 | 15007.98 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 245120000000 | 225687.676 |  | 48247.488 | 58802.451 | 32801.293 | 0 | 93366.94 | 2729.127 | 111.993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 41581.58 | 14276.07 | 0 | 55857.65
Cost per Total Building Area ($/m2) | 8.35 | 2.87 | 0 | 11.21
Cost per Net Conditioned Building Area ($/m2) | 8.35 | 2.87 | 0 | 11.21
16-fairbanks
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 5525.58 | 1109.07 | 1109.07
Net Site Energy | 5525.58 | 1109.07 | 1109.07
Total Source Energy | 12057.4 | 2420.1 | 2420.1
Net Source Energy | 12057.4 | 2420.1 | 2420.1
Area (m2)
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 3045.12 | 0 | 0 | 0 | 0
Cooling | 332.72 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 42.55 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 809.46 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 686.21 | 0 | 0 | 0 | 0 | 0
Pumps | 5.3 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 51.64 | 0 | 0 | 0 | 174.77
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2428.82 | 3096.76 | 0 | 0 | 0 | 174.77
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 2428.82 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 2428.82 | 100
Total On-Site and Utility Electric Sources | 2428.82 | 100
Total Electricity End Uses | 2428.82 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 983.54 | 0 | 180
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 91.28 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 40.57 | 270 | 90 | W
PERIMETER_BOT_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 40.57 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 40.57 | 270 | 90 | W
BUILDING_ROOF | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 1660.73 | 0 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 65.28 | 2.62 | 0.49 | 0.49 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 43.52 | 2.62 | 0.49 | 0.49 | No | PERIMETER_BOT_ZN_2_WALL_EAST
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_NORTH | 65.28 | 2.62 | 0.49 | 0.49 | No | PERIMETER_BOT_ZN_3_WALL_NORTH
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 43.52 | 2.62 | 0.49 | 0.49 | No | PERIMETER_BOT_ZN_4_WALL_WEST
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 65.28 | 2.62 | 0.49 | 0.49 | No | PERIMETER_MID_ZN_1_WALL_SOUTH
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 43.52 | 2.62 | 0.49 | 0.49 | No | PERIMETER_MID_ZN_2_WALL_EAST
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_NORTH | 65.28 | 2.62 | 0.49 | 0.49 | No | PERIMETER_MID_ZN_3_WALL_NORTH
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 43.52 | 2.62 | 0.49 | 0.49 | No | PERIMETER_MID_ZN_4_WALL_WEST
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 65.28 | 2.62 | 0.49 | 0.49 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 43.52 | 2.62 | 0.49 | 0.49 | No | PERIMETER_TOP_ZN_2_WALL_EAST
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_NORTH | 65.28 | 2.62 | 0.49 | 0.49 | No | PERIMETER_TOP_ZN_3_WALL_NORTH
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 43.52 | 2.62 | 0.49 | 0.49 | No | PERIMETER_TOP_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
HEATSYS1 BOILER | Boiler:HotWater | 1805934.83 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 122661.38 | 3
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 157344.81 | 3
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 192740.98 | 3
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
VAV_1 FAN | Fan:VariableVolume | 0.19 | 500 | 7.41 | 19905.8 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.19 | 500 | 9.51 | 25534.31 | 1 | Fan Energy
VAV_3 FAN | Fan:VariableVolume | 0.19 | 500 | 11.64 | 31278.5 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.45 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 10624.92 | 0.85
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORE_BOTTOM VAV BOX REHEAT COIL | 0.004147 | 190678.08 | 6750.83
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | 0.002173 | 99904.15 | 3537.04
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | 0.001298 | 59659.78 | 2112.21
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | 0.00136 | 62514.79 | 2213.29
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | 0.00148 | 68046.57 | 2409.14
CORE_MID VAV BOX REHEAT COIL | 0.005363 | 246602.35 | 8730.79
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | 0.002638 | 121293.07 | 4294.3
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | 0.001622 | 74570.4 | 2640.11
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | 0.001554 | 71432.74 | 2529.03
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | 0.001759 | 80872.01 | 2863.22
CORE_TOP VAV BOX REHEAT COIL | 0.007307 | 335970.34 | 11894.8
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | 0.002607 | 119858.44 | 4243.51
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | 0.001648 | 75772.78 | 2682.68
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | 0.00254 | 116804.41 | 4135.38
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | 0.001782 | 81954.92 | 2901.56
Nominal Capacity [W]
VAV_1_HEATC | 57129.5
VAV_2_HEATC | 54621.27
VAV_3_HEATC | 51788.66
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 73033.2781 | 79.4266 | 274.9014 | 0 | 0.001 | 55138.5737 | 27297.378
February | 60495.2545 | 66.6386 | 245.4403 | 0 | 0.0009 | 49234.244 | 22741.5211
March | 56961.5575 | 65.2507 | 283.5019 | 0 | 0.001 | 56882.5817 | 21798.5454
April | 44058.0692 | 52.5837 | 263.5128 | 0 | 0.0009 | 52881.1029 | 17185.8812
May | 45033.2183 | 55.4355 | 304.6593 | 0 | 0.001 | 61144.3779 | 17826.0159
June | 45770.6998 | 56.9937 | 323.2538 | 0 | 0.0011 | 64878.3364 | 18218.0165
July | 44997.1192 | 56.068 | 318.5772 | 0 | 0.0011 | 63939.8235 | 17915.8965
August | 48252.4955 | 59.7052 | 332.857 | 0 | 0.0011 | 66804.5632 | 19147.5516
September | 43737.7006 | 53.1243 | 280.9065 | 0 | 0.001 | 56374.9564 | 17202.9484
October | 49299.0427 | 57.8577 | 274.3326 | 0 | 0.001 | 55048.8517 | 19079.2608
November | 59284.1939 | 66.4642 | 264.7875 | 0 | 0.0009 | 53121.3978 | 22464.7078
December | 65980.8762 | 72.7172 | 268.446 | 0 | 0.001 | 53849.2755 | 24809.2023
Annual Sum or Average | 636903.5055 | 742.2655 | 3435.1763 | 0 | 0.0119 | 689298.0848 | 245686.9256
Minimum of Months | 43737.7006 | 52.5837 | 245.4403 | 0 | 0.0009 | 49234.244 | 17185.8812
Maximum of Months | 73033.2781 | 79.4266 | 332.857 | 0 | 0.0011 | 66804.5632 | 27297.378
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 194287000000 | 159040.65 | 19-JAN-08:00 | 48247.488 | 58802.451 | 32182.675 | 0 | 16933.542 | 2729.127 | 145.366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 173482000000 | 151556.412 | 28-FEB-16:30 | 48247.488 | 51263.506 | 32225.06 | 0 | 19765.996 | 0 | 54.361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 200432000000 | 161777.724 | 31-MAR-15:30 | 48247.488 | 51263.506 | 32258.917 | 0 | 29974.084 | 0 | 33.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 186332000000 | 167117.34 | 25-APR-15:45 | 48247.488 | 51263.506 | 32568.033 | 0 | 35023.388 | 0 | 14.924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 215449000000 | 182557.583 | 24-MAY-15:15 | 48247.488 | 51263.506 | 33231.747 | 0 | 49806.393 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 228606000000 | 202508.112 | 21-JUN-15:00 | 48247.488 | 51263.506 | 33694.397 | 0 | 69294.271 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 225299000000 | 202108.609 | 11-JUL-15:00 | 48247.488 | 51263.506 | 33907.638 | 0 | 68681.528 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 235393000000 | 197197.71 | 15-AUG-12:00 | 48247.488 | 51919.067 | 33574.521 | 0 | 63448.185 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 198643000000 | 174253.099 | 01-SEP-15:00 | 48247.488 | 51263.506 | 32301.698 | 0 | 42422.641 | 0 | 17.766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 193971000000 | 167194.473 | 03-OCT-15:15 | 48247.488 | 51263.506 | 32349.955 | 0 | 35301.377 | 0 | 32.147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 187179000000 | 156900.486 | 14-NOV-08:00 | 48247.488 | 58802.451 | 32182.675 | 0 | 14776.956 | 2729.127 | 161.788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 189744000000 | 154979.327 | 18-DEC-08:00 | 48247.488 | 58802.451 | 32182.675 | 0 | 12804.332 | 2729.127 | 213.253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2428820000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 173482000000 | 151556.412 |  | 48247.488 | 51263.506 | 32182.675 | 0 | 12804.332 | 0 | 8.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 235393000000 | 202508.112 |  | 48247.488 | 58802.451 | 33907.638 | 0 | 69294.271 | 2729.127 | 213.253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 67227.83 | 12767.28 | 0 | 79995.11
Cost per Total Building Area ($/m2) | 13.49 | 2.56 | 0 | 16.06
Cost per Net Conditioned Building Area ($/m2) | 13.49 | 2.56 | 0 | 16.06

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago-O'Hare | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7A | 8A
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 42.2 | 369 | 83.3 | 414.1 | 472 | 52.6 | 21.6 | 938.7 | 23.5 | 118 | 832.4 | 187.6 | 236.8 | 28.1 | 32.3 | 1.67
Fabric
Exterior walls
| Construction Type | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall
| R-value (m2·K / W) | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 2.0964 | 2.0964 | 2.0964 | 2.0964 | 2.7473 | 2.7473
Roof
| Construction Type | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck
| R-value (m2·K / W) | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 3.663
Window
| U-Factor (W / m2·K) | 6.88 | 6.88 | 6.88 | 3.24 | 3.24 | 3.24 | 6.88 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 2.62
| SHGC | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.34 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.49 | 0.49
| Visible transmittance | 0.25 | 0.25 | 0.25 | 0.318 | 0.318 | 0.318 | 0.34 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.49 | 0.49
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade
| R-value (m2·K / W) | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463
HVAC
HVAC Sizing
Air Conditioning (kW)
| VAV_1_COOLC DXCOIL | 129.8508 | 122.9573 | 124.042 | 116.2898 | 93.9236 | 116.9634 | 98.2023 | 127.2604 | 132.8014 | 110.6113 | 124.9899 | 129.9189 | 121.8021 | 123.3069 | 120.1379 | 122.6614
| VAV_2_COOLC DXCOIL | 150.0364 | 147.9548 | 156.3948 | 145.6505 | 124.912 | 153.0512 | 123.9459 | 157.5061 | 167.5603 | 138.6042 | 155.8782 | 164.3894 | 153.5856 | 157.1244 | 151.308 | 157.3448
| VAV_3_COOLC DXCOIL | 167.7651 | 167.3084 | 172.5793 | 160.2702 | 126.0195 | 165.3942 | 116.8111 | 171.4749 | 176.8853 | 135.862 | 168.7183 | 171.3198 | 173.8516 | 177.1398 | 170.8808 | 192.741
Heating (kW)
| HEATSYS1 BOILER | 1398.6262 | 1430.252 | 1629.475 | 1397.3734 | 1306.445 | 1529.5075 | 1307.2276 | 1571.5984 | 1492.5281 | 1458.9797 | 1560.0339 | 1473.0827 | 1599.7943 | 1546.9937 | 1644.3522 | 1805.9348
HVAC Efficiency
Air Conditioning (COP)
| VAV_1_COOLC DXCOIL | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| VAV_2_COOLC DXCOIL | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| VAV_3_COOLC DXCOIL | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Heating Efficiency (%) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
HVAC Control
| Economizer | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
Fan Max Flow Rate (m3/s )
| VAV_1 FAN | 6.64 | 6.34 | 7.23 | 6.28 | 5.67 | 7.07 | 5.93 | 6.97 | 8.02 | 6.68 | 6.91 | 7.85 | 6.92 | 7.45 | 7.26 | 7.41
| VAV_2 FAN | 7.53 | 7.93 | 9.29 | 8.09 | 7.55 | 9.25 | 7.49 | 8.8 | 10.12 | 8.37 | 8.79 | 9.93 | 8.89 | 9.49 | 9.14 | 9.51
| VAV_3 FAN | 8.05 | 8.54 | 10.43 | 8.68 | 7.61 | 9.99 | 7.06 | 9.34 | 10.69 | 8.21 | 9.14 | 10.35 | 9.76 | 10.7 | 10.26 | 11.64
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.088228 | 0.1198 | 0.097458 | 0.09889 | 0.12933 | 0.10004 | 0.14891 | 0.077539 | 0.037187 | 0.076297 | 0.08911 | 0.037199 | 0.061625 | 0.077464 | 0.061485 | 0.099645
| Total Cost ($/m2) | 14.38 | 18.49 | 15.84 | 14.08 | 17.39 | 15.25 | 19.05 | 11.17 | 5.55 | 10.04 | 12.38 | 5.3 | 8.53 | 10.74 | 8.35 | 13.49
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011404 | 0.008056 | 0.0082322 | 0.0096329 | 0.0086071 | 0.0076967 | 0.0085537 | 0.0097062 | 0.0069026 | 0.0084131 | 0.0083442 | 0.0069265 | 0.0078826 | 0.0081324 | 0.0078766 | 0.0041228
| Total Cost ($/m2) | 0.16 | 0.68 | 0.68 | 1.02 | 0.37 | 0.6 | 1.06 | 1.65 | 0.79 | 1.41 | 1.85 | 1.15 | 2.39 | 2.12 | 2.87 | 2.56
Total Utility Costs
| Cost Intensity ($/m2) | 14.54 | 19.16 | 16.52 | 15.1 | 17.76 | 15.85 | 20.11 | 12.82 | 6.34 | 11.45 | 14.23 | 6.45 | 10.92 | 12.86 | 11.21 | 16.06
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 301127.7778 | 251780.5556 | 267230.5556 | 190430.5556 | 168402.7778 | 220680.5556 | 133125 | 181308.3333 | 186172.2222 | 133288.8889 | 153408.3333 | 154094.4444 | 141108.3333 | 132166.6667 | 116358.3333 | 92422.2222
| Interior Lighting | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667
| Exterior Lighting | 11933.3333 | 11911.1111 | 11908.3333 | 11927.7778 | 11925 | 11913.8889 | 11902.7778 | 11913.8889 | 11911.1111 | 11894.4444 | 11897.2222 | 11900 | 11908.3333 | 11891.6667 | 11888.8889 | 11819.4444
| Interior Equipment | 224850 | 224850 | 224850 | 224850 | 224850 | 224850 | 224850 | 224850 | 224850 | 224850 | 224850 | 224850 | 224850 | 224850 | 224850 | 224850
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 120569.4444 | 126516.6667 | 152133.3333 | 128188.8889 | 111133.3333 | 148194.4444 | 113544.4444 | 145488.8889 | 166361.1111 | 131977.7778 | 147747.2222 | 164811.1111 | 157833.3333 | 167594.4444 | 168813.8889 | 190613.8889
| Pumps | 88.8889 | 247.2222 | 222.2222 | 294.4444 | 138.8889 | 219.4444 | 333.3333 | 427.7778 | 305.5556 | 402.7778 | 550 | 441.6667 | 752.7778 | 661.1111 | 888.8889 | 1472.2222
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 812061.1111 | 768797.2222 | 809838.8889 | 709186.1111 | 669944.4444 | 759347.2222 | 637247.2222 | 717480.5556 | 743094.4445 | 655905.5556 | 691944.4444 | 709588.8889 | 689944.4444 | 690658.3333 | 676291.6667 | 674672.2222
Gas (MJ)
| Heating | 40280 | 387660 | 382750 | 493050 | 181340 | 354540 | 580300 | 810390 | 533490 | 793400 | 1065240 | 788010 | 1465360 | 1255230 | 1765340 | 3045120
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 27750 | 31690 | 29420 | 35500 | 34770 | 32150 | 38020 | 38480 | 37920 | 40050 | 41110 | 40970 | 43380 | 43790 | 47120 | 51640
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 68030 | 419350 | 412160 | 528550 | 216110 | 386690 | 618330 | 848870 | 571410 | 833450 | 1106350 | 828980 | 1508740 | 1299020 | 1812460 | 3096760
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 2991450 | 3187030 | 3327580 | 3081610 | 2627910 | 3120340 | 2912420 | 3431810 | 3246550 | 3194710 | 3597350 | 3383500 | 3992540 | 3785390 | 4247110 | 5525580
| On-Site Production (MJ) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 217.587 | 181.93 | 193.0938 | 137.6001 | 121.6834 | 159.458 | 96.1926 | 131.0087 | 134.5232 | 96.3111 | 110.8488 | 111.3446 | 101.9612 | 95.5002 | 84.0775 | 66.7819
| Interior Lighting (elec) | 110.9091 | 110.9091 | 110.9091 | 110.9091 | 110.9091 | 110.9091 | 110.9091 | 110.9091 | 110.9091 | 110.9091 | 110.9091 | 110.9091 | 110.9091 | 110.9091 | 110.9091 | 110.9091
| Exterior Lighting (elec) | 8.6227 | 8.6067 | 8.6046 | 8.6187 | 8.6167 | 8.6087 | 8.6006 | 8.6087 | 8.6067 | 8.5946 | 8.5966 | 8.5986 | 8.6046 | 8.5926 | 8.5906 | 8.5404
| Interior Equipment (elec) | 162.4707 | 162.4707 | 162.4707 | 162.4707 | 162.4707 | 162.4707 | 162.4707 | 162.4707 | 162.4707 | 162.4707 | 162.4707 | 162.4707 | 162.4707 | 162.4707 | 162.4707 | 162.4707
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 87.1203 | 91.4176 | 109.9276 | 92.6259 | 80.302 | 107.0814 | 82.0442 | 105.1265 | 120.2082 | 95.3637 | 106.7583 | 119.0882 | 114.0462 | 121.0994 | 121.9805 | 137.7326
| Pumps (elec) | 0.064229 | 0.17864 | 0.16057 | 0.21276 | 0.10036 | 0.15856 | 0.24086 | 0.3091 | 0.22079 | 0.29104 | 0.39742 | 0.31914 | 0.54394 | 0.4777 | 0.64229 | 1.0638
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 586.7741 | 555.5127 | 585.1684 | 512.4393 | 484.0843 | 548.6844 | 460.4582 | 518.4327 | 536.9406 | 473.9402 | 499.9809 | 512.7303 | 498.5358 | 499.0516 | 488.6706 | 487.5005
Gas (MJ/m2)
| Heating (gas) | 8.0848 | 77.8092 | 76.8236 | 98.9625 | 36.3976 | 71.1615 | 116.4749 | 162.6574 | 107.0794 | 159.2472 | 213.8096 | 158.1654 | 294.1197 | 251.9434 | 354.3301 | 611.2011
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 5.5698 | 6.3607 | 5.905 | 7.1254 | 6.9789 | 6.453 | 7.6312 | 7.7235 | 7.6111 | 8.0386 | 8.2514 | 8.2233 | 8.707 | 8.7893 | 9.4577 | 10.3649
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 13.6546 | 84.1698 | 82.7267 | 106.0879 | 43.3765 | 77.6145 | 124.1081 | 170.3809 | 114.6905 | 167.2859 | 222.061 | 166.3887 | 302.8267 | 260.7327 | 363.7878 | 621.566
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 600.4287 | 639.6846 | 667.895 | 618.5252 | 527.4608 | 626.2989 | 584.5662 | 688.8156 | 651.6311 | 641.226 | 722.0419 | 679.119 | 801.3625 | 759.7844 | 852.4585 | 1109.0665
| On-Site Production (MJ/m2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 199.5156 | 189.2676 | 173.719 | 166.4233 | 165.3457 | 166.5199 | 154.349 | 168.2594 | 172.9932 | 154.2915 | 156.6963 | 168.012 | 147.1529 | 159.7082 | 150.1809 | 159.0406
| Feb | 207.6141 | 183.7864 | 177.8838 | 169.3199 | 166.761 | 170.1657 | 163.594 | 161.3768 | 177.3974 | 158.3604 | 156.7494 | 167.2687 | 148.2087 | 168.4138 | 156.4451 | 151.5564
| Mar | 208.8706 | 189.5609 | 195.9992 | 174.1301 | 165.0304 | 175.0292 | 159.0733 | 182.7908 | 178.8206 | 166.0147 | 169.2673 | 176.9279 | 166.9838 | 175.6111 | 156.4804 | 161.7777
| Apr | 216.6285 | 194.0797 | 198.7793 | 188.726 | 173.5774 | 197.4198 | 160.9387 | 183.3134 | 191.7173 | 165.7042 | 178.1155 | 184.1912 | 172.8695 | 170.1219 | 169.5403 | 167.1173
| May | 226.8981 | 229.4911 | 238.5933 | 209.4537 | 185.6564 | 220.1161 | 169.4249 | 204.1486 | 206.2486 | 180.0507 | 204.5274 | 197.6454 | 202.1302 | 183.2064 | 182.1436 | 182.5576
| Jun | 240.8459 | 230.8205 | 311.4426 | 222.3861 | 178.0276 | 290.5735 | 172.4023 | 239.3398 | 227.6974 | 188.51 | 230.5807 | 210.0595 | 230.4996 | 221.5521 | 211.5567 | 202.5081
| Jul | 235.4944 | 246.835 | 302.7367 | 246.0059 | 183.7381 | 285.5084 | 189.5321 | 249.0253 | 239.4498 | 202.2266 | 240.1255 | 224.4848 | 226.6075 | 216.2507 | 225.6877 | 202.1086
| Aug | 247.7585 | 241.9731 | 309.4752 | 224.1229 | 193.0757 | 265.0887 | 176.4708 | 249.022 | 238.9034 | 199.4845 | 235.6105 | 221.5361 | 224.2954 | 206.4952 | 215.6504 | 197.1977
| Sep | 236.5714 | 227.4391 | 260.8006 | 214.223 | 193.507 | 242.8339 | 196.9808 | 213.7474 | 207.121 | 194.1934 | 205.9355 | 200.0773 | 204.3289 | 197.1848 | 203.8795 | 174.2531
| Oct | 225.3939 | 207.1197 | 205.3671 | 192.6721 | 178.1427 | 201.0645 | 171.1231 | 197.9608 | 196.0281 | 169.8325 | 187.355 | 191.1646 | 176.5416 | 182.7851 | 173.6948 | 167.1945
| Nov | 207.8016 | 197.1248 | 189.142 | 171.5759 | 170.6245 | 172.5623 | 160.8375 | 190.7511 | 177.9642 | 167.2608 | 187.558 | 173.879 | 169.8499 | 166.4485 | 171.5922 | 156.9005
| Dec | 195.2821 | 187.6506 | 178.2319 | 171.7505 | 167.2345 | 169.2341 | 154.8642 | 157.4363 | 171.434 | 155.1255 | 160.4758 | 167.668 | 148.4801 | 160.3029 | 147.4272 | 154.9793
Time of Peak Electrical Demand
| Jan | 23-JAN-16:15 | 03-JAN-08:30 | 30-JAN-13:00 | 24-JAN-16:00 | 26-JAN-13:15 | 18-JAN-13:00 | 06-JAN-16:15 | 09-JAN-08:00 | 27-JAN-13:00 | 27-JAN-16:00 | 18-JAN-08:00 | 27-JAN-13:00 | 19-JAN-08:00 | 10-JAN-08:15 | 13-JAN-16:45 | 19-JAN-08:00
| Feb | 21-FEB-13:00 | 23-FEB-13:00 | 28-FEB-16:15 | 22-FEB-08:15 | 13-FEB-13:00 | 27-FEB-13:00 | 15-FEB-16:15 | 15-FEB-13:00 | 14-FEB-16:15 | 22-FEB-08:00 | 28-FEB-08:00 | 07-FEB-13:00 | 21-FEB-08:00 | 02-FEB-16:15 | 28-FEB-13:45 | 28-FEB-16:30
| Mar | 27-MAR-15:30 | 29-MAR-07:00 | 17-MAR-15:00 | 29-MAR-15:15 | 31-MAR-15:15 | 31-MAR-15:15 | 01-MAR-13:15 | 09-MAR-16:15 | 02-MAR-16:15 | 29-MAR-12:00 | 31-MAR-15:15 | 27-MAR-12:00 | 23-MAR-15:30 | 28-MAR-15:00 | 30-MAR-07:00 | 31-MAR-15:30
| Apr | 03-APR-15:15 | 17-APR-15:00 | 26-APR-15:45 | 20-APR-15:00 | 11-APR-15:15 | 21-APR-15:30 | 13-APR-15:15 | 04-APR-15:00 | 21-APR-15:30 | 18-APR-15:45 | 10-APR-07:00 | 26-APR-15:45 | 26-APR-12:00 | 06-APR-15:00 | 04-APR-15:15 | 25-APR-15:45
| May | 15-MAY-15:00 | 18-MAY-15:30 | 30-MAY-15:30 | 15-MAY-15:15 | 30-MAY-15:15 | 31-MAY-15:00 | 25-MAY-15:00 | 31-MAY-15:45 | 31-MAY-15:00 | 04-MAY-15:15 | 30-MAY-15:00 | 24-MAY-15:30 | 31-MAY-12:15 | 17-MAY-15:45 | 31-MAY-15:00 | 24-MAY-15:15
| Jun | 26-JUN-15:30 | 12-JUN-15:15 | 28-JUN-15:00 | 19-JUN-15:15 | 30-JUN-15:00 | 27-JUN-15:45 | 16-JUN-15:00 | 30-JUN-15:30 | 29-JUN-15:30 | 28-JUN-15:15 | 08-JUN-12:00 | 27-JUN-15:15 | 30-JUN-15:15 | 26-JUN-15:15 | 14-JUN-15:15 | 21-JUN-15:00
| Jul | 03-JUL-15:15 | 05-JUL-15:00 | 11-JUL-15:00 | 03-JUL-15:30 | 24-JUL-15:15 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 03-JUL-15:30 | 24-JUL-15:15 | 03-JUL-15:15 | 17-JUL-15:15 | 13-JUL-15:30 | 21-JUL-15:45 | 06-JUL-15:30 | 11-JUL-15:00
| Aug | 21-AUG-15:15 | 31-AUG-15:00 | 01-AUG-15:45 | 14-AUG-15:45 | 08-AUG-15:15 | 04-AUG-15:00 | 15-AUG-12:15 | 17-AUG-15:15 | 01-AUG-15:15 | 07-AUG-15:15 | 04-AUG-15:30 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-15:30 | 15-AUG-12:00
| Sep | 11-SEP-15:15 | 15-SEP-15:15 | 11-SEP-15:45 | 05-SEP-15:00 | 25-SEP-15:15 | 01-SEP-15:15 | 28-SEP-15:30 | 08-SEP-15:15 | 05-SEP-12:00 | 01-SEP-15:45 | 05-SEP-15:15 | 01-SEP-15:45 | 14-SEP-15:15 | 01-SEP-15:00 | 07-SEP-15:15 | 01-SEP-15:00
| Oct | 06-OCT-15:30 | 30-OCT-08:00 | 13-OCT-15:45 | 12-OCT-15:00 | 05-OCT-15:15 | 06-OCT-12:00 | 31-OCT-13:15 | 12-OCT-15:15 | 11-OCT-15:00 | 10-OCT-07:45 | 31-OCT-08:45 | 05-OCT-15:15 | 06-OCT-15:15 | 06-OCT-15:15 | 06-OCT-15:15 | 03-OCT-15:15
| Nov | 01-NOV-08:00 | 27-NOV-08:45 | 13-NOV-13:00 | 22-NOV-13:30 | 10-NOV-13:15 | 09-NOV-16:45 | 16-NOV-16:00 | 03-NOV-13:00 | 10-NOV-13:00 | 03-NOV-08:00 | 02-NOV-08:45 | 10-NOV-13:45 | 02-NOV-13:00 | 21-NOV-08:00 | 09-NOV-08:00 | 14-NOV-08:00
| Dec | 19-DEC-13:00 | 20-DEC-08:45 | 13-DEC-13:15 | 26-DEC-08:00 | 19-DEC-13:15 | 05-DEC-13:00 | 14-DEC-16:00 | 08-DEC-08:00 | 05-DEC-13:00 | 05-DEC-08:00 | 12-DEC-08:00 | 21-DEC-13:00 | 01-DEC-16:30 | 29-DEC-08:15 | 01-DEC-16:30 | 18-DEC-08:00
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77
| Total Building | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77 | 174.77
Emissions
| Carbon Equivalent (kg) | 223934.0238 | 264003.0166 | 251903.0867 | 227986.0336 | 82190.5306 | 263082.3136 | 85622.574 | 208923.805 | 313856.8699 | 62801.6278 | 388860.3573 | 304814.3089 | 263369.8713 | 275817.4933 | 264173.8916 | 245686.9256
| CO2 (kg) | 519235.0173 | 665332.1267 | 596394.9447 | 523342.5101 | 220289.7302 | 626744.4086 | 231043.7438 | 478417.4636 | 737077.9781 | 156904.807 | 908816.0196 | 718604.7232 | 623054.414 | 654711.3798 | 628105.4374 | 636903.5055
| NOX (kg) | 912.6926 | 865.636 | 991.2056 | 982.3997 | 189.105 | 1013.0672 | 199.3996 | 908.2757 | 1268.0259 | 221.7586 | 1602.2313 | 1224.2522 | 1064.8838 | 1103.4821 | 1059.5912 | 742.2655
| SO2 (kg) | 3475.9596 | 3667.2778 | 3256.6373 | 2489.3804 | 1949.5122 | 4177.1275 | 1854.4802 | 2619.3222 | 3245.0997 | 507.1861 | 4663.4504 | 3098.8542 | 1628.7845 | 1844.4902 | 1596.6454 | 3435.1763
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0158 | 0.0103 | 0.0089 | 0.0091 | 0.0009 | 0.0079 | 0.0009 | 0.0106 | 0.0127 | 0.0021 | 0.0142 | 0.0122 | 0.012 | 0.0129 | 0.0118 | 0.0119
| Water Environmental Factors (m3) | 430.1952 | 1250.9241 | 24055.8 | 24055.8 | 11762.7 | 20832 | 11188.6 | 162.8953 | 3374.2441 | 6701.2581 | 1073.5108 | 3222.0996 | 1070.4081 | 43749.2 | 1049.2281 | 689.2981

## Picture
DOE Commercial Building Benchmark - Medium Office

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | 11.15 | 70.85 | 3694.32
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | 9.85
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 5.25
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | 7.2 | 46.3 | 2414.21
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | 7.5
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 2.8
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | 13.7 | 89.4 | 4661.57
|  |  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15 | 12.15
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 8.75
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.22 | 0.64 | 0.74 | 0.68 | 0.68 | 0.71 | 0.72 | 0.72 | 0.73 | 0.68 | 0.68 | 0.58 | 0.54 | 0 | 0 | 0 | 8.44 | 52.69 | 2747.41
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.21 | 0.56 | 0.66 | 0.68 | 0.68 | 0.69 | 0.7 | 0.69 | 0.66 | 0.58 | 0.47 | 0.43 | 0.43 | 0.08 | 0 | 0 | 7.61
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.13 | 0.35 | 0.37 | 0.37 | 0.39 | 0.41 | 0.38 | 0.34 | 0.03 | 0 | 0 | 0 | 0 | 0 | 2.88
INFIL_SCH | fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 9 | 68 | 3545.71
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 15
INFIL_HALF_ON_SCH | fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 16.5 | 118 | 6152.86
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19.5
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0.23 | 0.13 | 0.08 | 6.62 | 44.59 | 2325.05
|  |  | Sat, WinterDesign | 0.11 | 0.1 | 0.08 | 0.06 | 0.06 | 0.06 | 0.07 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0.16 | 0.13 | 6.9
|  |  | Sun, Hol, Other | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07 | 0.1 | 0.12 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.1 | 0.06 | 4.59
Hours_of_operation | on/off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 100 | 5214.29
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | on/off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 100 | 5214.29
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | WD, WinterDesign | 13 | 13 | 13 | 13 | 13 | 13 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 13 | 13 | 13 | 432 | 2992 | 156011.43
|  |  | SummerDesign | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312
|  |  | Sat | 13 | 13 | 13 | 13 | 13 | 13 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 13 | 13 | 440
|  |  | Sun, Hol, Other | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 13 | 13 | 13 | 13 | 13 | 13 | 392
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 33 | 33 | 33 | 33 | 33 | 33 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 33 | 33 | 33 | 657 | 4644 | 242151.43
|  |  | Sat | 33 | 33 | 33 | 33 | 33 | 33 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 33 | 33 | 648
|  |  | WinterDesign | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 792
|  |  | Sun, Hol, Other | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 711
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 100 | 5214.29
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 126984
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Temperature Schedules (oF)
HTGSETP_SCH | Temperature | Through 12/31 | WD, WinterDesign | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 55.4 | 55.4 | 55.4
|  |  | SummerDesign | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4
|  |  | Sat | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 55.4 | 55.4
|  |  | Sun, Hol, Other | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 91.4 | 91.4 | 91.4
|  |  | Sat | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 91.4 | 91.4
|  |  | WinterDesign | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4
|  |  | Sun, Hol, Other | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4