## BuildingSummary
Building Summary Outpatient Health Care new construction version 1.0_3.0
|  | Value | Data Source
Program
| Building Name | Outpatient Health Care
| Available Fuel Types | gas, electricity
| Principal Building Activity | Health care, outpatient
Form
| Total Floor Area (m2) | 929.5 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 1.5
| Number of Floors | 2
Window Fraction (Window to Wall Ratio)
| South | 0.15
| East | 0.15
| North | 0.15
| West | 0.15
| Total | 0.15
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | single zone per floor
| Floor to Ceiling Height (m) | 3.05
| Floor to Floor Height (m) | 3.05
| Roof type | Attic | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel frame | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 536.66
| Net Dimensions - Total Area (m2) | 456.22
| Wall to Skin Ratio | 0.51348
Roof
| Construction Type | Insulation entirely above deck | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 508.48
| Net Dimensions - Total Area (m2) | 508.48
| Roof to Skin Ratio | 0.48652
Window Dimensions (m2)
| South | 24.14
| East | 16.08
| North | 24.14
| West | 16.08
| Total Area (m2) | 80.44
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 10 cm slab-on-grade with carpet
| Dimensions - Total Area (m2) | 464.75
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
Dimensions - Total Area (m2)
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 1859.01
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.3 | See Benchmark Technical Report
HVAC
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | PACU | 2003 CBECS
| Fan Control | CAV | 2003 CBECS
Service Water Heating
| SWH Type | gas water heater
| Fuel | gas
| Thermal Efficiency (%) | 80
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 10.03

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
First_floor | Yes | 1 | 464.75 | 1416.93 | 3.0488 | 268.33 | 40.22 | 18.5806 | 25.0126 | 10.76 | 8.0699 | 0 | 23.6707 | 2.5 | 0.3 | 201.9565 | 0 | 0.3
Second_floor | Yes | 1 | 464.75 | 1416.93 | 3.0488 | 268.33 | 40.22 | 18.5806 | 25.0126 | 10.76 | 8.0699 | 0 | 23.6707 | 2.5 | 0.3 | 201.9565 | 0 | 0.3
Attic | No | 1 | 2293.99 | 631.22 | 0.27516
Total Conditioned Zones |  |  | 929.5 | 2833.86 |  | 536.66 | 80.44 |  | 50.0252
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report

## Query (hidden)
1-miami
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 612.58 | 659.05 | 659.05
Net Site Energy | 612.58 | 659.05 | 659.05
Total Source Energy | 2010.12 | 2162.57 | 2162.57
Net Source Energy | 2010.12 | 2162.57 | 2162.57
Area (m2)
Total Building Area | 929.5
Net Conditioned Building Area | 929.5
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 0.25 | 0 | 0 | 0 | 0
Cooling | 218.89 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 109.85 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 134.31 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 139.72 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 9.56 | 0 | 0 | 0 | 10.03
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 602.78 | 9.81 | 0 | 0 | 0 | 10.03
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 602.78 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 602.78 | 100
Total On-Site and Utility Electric Sources | 602.78 | 100
Total Electricity End Uses | 602.78 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
FIRST_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 0 | 90 | N
FIRST_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 90 | 90 | E
FIRST_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 180 | 90 | S
FIRST_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 270 | 90 | W
FIRST_FLOOR_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 464.75 | 0 | 180
SECOND_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 0 | 90 | N
SECOND_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 90 | 90 | E
SECOND_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 180 | 90 | S
SECOND_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 270 | 90 | W
WEST-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 36.51 | 270 | 45
EAST-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 36.51 | 90 | 45
SOUTH-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 217.73 | 180 | 18.43
NORTH-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 217.73 | 0 | 18.44
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
FIRST_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 6.88 | 0.25 | 0.25 | No | FIRST_FLOOR_WALL_NORTH
FIRST_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 6.88 | 0.25 | 0.25 | No | FIRST_FLOOR_WALL_EAST
FIRST_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 6.88 | 0.25 | 0.25 | No | FIRST_FLOOR_WALL_SOUTH
FIRST_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 6.88 | 0.25 | 0.25 | No | FIRST_FLOOR_WALL_WEST
SECOND_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 6.88 | 0.25 | 0.25 | No | SECOND_FLOOR_WALL_NORTH
SECOND_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 6.88 | 0.25 | 0.25 | No | SECOND_FLOOR_WALL_EAST
SECOND_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 6.88 | 0.25 | 0.25 | No | SECOND_FLOOR_WALL_SOUTH
SECOND_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 6.88 | 0.25 | 0.25 | No | SECOND_FLOOR_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_2:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 28504.83 | 2.96
PSZ-AC_1:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 34920.92 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC_2:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.33 | 1903.12 | 1 | General
PSZ-AC_1:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.77 | 2527.49 | 1 | General
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
Nominal Capacity [W]
PSZ-AC_2:1_UNITARY_PACKAGE_HEATCOIL | 9691.49
PSZ-AC_1:2_UNITARY_PACKAGE_HEATCOIL | 14555.89
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 7491.4282 | 13.1645 | 50.1219 | 0 | 0.0002 | 6203.2318 | 3230.5147
February | 7026.0536 | 12.3576 | 47.0938 | 0 | 0.0002 | 5828.4778 | 3030.9213
March | 8279.7231 | 14.5658 | 55.5218 | 0 | 0.0003 | 6871.5516 | 3572.0507
April | 8605.576 | 15.1414 | 57.7261 | 0 | 0.0003 | 7144.3659 | 3712.8754
May | 9696.0059 | 17.064 | 65.0717 | 0 | 0.0003 | 8053.4862 | 4183.7364
June | 9975.805 | 17.5589 | 66.9693 | 0 | 0.0003 | 8288.3361 | 4304.7189
July | 10411.2856 | 18.3255 | 69.893 | 0 | 0.0003 | 8650.1814 | 4492.6386
August | 10663.8807 | 18.7709 | 71.5955 | 0 | 0.0003 | 8860.8991 | 4601.7249
September | 9724.3864 | 17.1155 | 65.2746 | 0 | 0.0003 | 8078.5997 | 4196.1407
October | 9310.143 | 16.3835 | 62.4709 | 0 | 0.0003 | 7731.5947 | 4017.0968
November | 8180.9709 | 14.3926 | 54.8641 | 0 | 0.0003 | 6790.1551 | 3529.5045
December | 7475.4846 | 13.1474 | 50.1009 | 0 | 0.0002 | 6200.6462 | 3224.7306
Annual Sum or Average | 106840.743 | 187.9876 | 716.7035 | 0 | 0.0033 | 88701.5257 | 46096.6535
Minimum of Months | 7026.0536 | 12.3576 | 47.0938 | 0 | 0.0002 | 5828.4778 | 3030.9213
Maximum of Months | 10663.8807 | 18.7709 | 71.5955 | 0 | 0.0003 | 8860.8991 | 4601.7249
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 42154400000 | 31496.126 | 06-JAN-13:00 | 9001.312 | 6750.984 | 4430.615 | 0 | 11313.214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 39607700000 | 32527.182 | 22-FEB-15:00 | 9001.312 | 6750.984 | 4430.615 | 0 | 12344.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 46696000000 | 32821.398 | 13-MAR-14:00 | 9001.312 | 6750.984 | 4430.615 | 0 | 12638.486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 48549900000 | 33721.512 | 03-APR-14:39 | 9001.312 | 6750.984 | 4430.615 | 0 | 13538.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 54727900000 | 35855.233 | 24-MAY-14:00 | 9001.312 | 6750.984 | 4430.615 | 0 | 15672.321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 56323800000 | 37108.18 | 28-JUN-14:00 | 9001.312 | 6750.984 | 4430.615 | 0 | 16925.268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 58782800000 | 36456.468 | 13-JUL-14:00 | 9001.312 | 6750.984 | 4430.615 | 0 | 16273.556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 60214700000 | 37114.296 | 21-AUG-14:00 | 9001.312 | 6750.984 | 4430.615 | 0 | 16931.384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 54898600000 | 36176.551 | 01-SEP-14:00 | 9001.312 | 6750.984 | 4430.615 | 0 | 15993.639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 52540500000 | 35537.179 | 06-OCT-14:00 | 9001.312 | 6750.984 | 4430.615 | 0 | 15354.267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 46142900000 | 33366.69 | 07-NOV-14:00 | 9001.312 | 6750.984 | 4430.615 | 0 | 13183.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 42136800000 | 31375.536 | 19-DEC-14:30 | 9001.312 | 6750.984 | 4430.615 | 0 | 11192.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 602776000000 | [7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 39607700000 | 31375.536 |  | 9001.312 | 6750.984 | 4430.615 | 0 | 11192.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 60214700000 | 37114.296 |  | 9001.312 | 6750.984 | 4430.615 | 0 | 16931.384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 13053.78 | 112.49 | 0 | 13166.27
Cost per Total Building Area ($/m2) | 14.04 | 0.12 | 0 | 14.16
Cost per Net Conditioned Building Area ($/m2) | 14.04 | 0.12 | 0 | 14.16
2-houston
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 585.99 | 630.44 | 630.44
Net Site Energy | 585.99 | 630.44 | 630.44
Total Source Energy | 60.91 | 65.53 | 65.53
Net Source Energy | 60.91 | 65.53 | 65.53
Area (m2)
Total Building Area | 929.5
Net Conditioned Building Area | 929.5
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 45.99 | 0 | 0 | 0 | 0
Cooling | 143.56 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 109.85 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 134.31 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 142.49 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 9.79 | 0 | 0 | 0 | 10.03
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 530.21 | 55.78 | 0 | 0 | 0 | 10.03
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 530.21 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 530.21 | 100
Total On-Site and Utility Electric Sources | 530.21 | 100
Total Electricity End Uses | 530.21 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
FIRST_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 0 | 90 | N
FIRST_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 90 | 90 | E
FIRST_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 180 | 90 | S
FIRST_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 270 | 90 | W
FIRST_FLOOR_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 464.75 | 0 | 180
SECOND_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 0 | 90 | N
SECOND_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 90 | 90 | E
SECOND_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 180 | 90 | S
SECOND_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 270 | 90 | W
WEST-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 36.51 | 270 | 45
EAST-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 36.51 | 90 | 45
SOUTH-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 217.73 | 180 | 18.43
NORTH-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 217.73 | 0 | 18.44
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
FIRST_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 6.88 | 0.25 | 0.25 | No | FIRST_FLOOR_WALL_NORTH
FIRST_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 6.88 | 0.25 | 0.25 | No | FIRST_FLOOR_WALL_EAST
FIRST_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 6.88 | 0.25 | 0.25 | No | FIRST_FLOOR_WALL_SOUTH
FIRST_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 6.88 | 0.25 | 0.25 | No | FIRST_FLOOR_WALL_WEST
SECOND_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 6.88 | 0.25 | 0.25 | No | SECOND_FLOOR_WALL_NORTH
SECOND_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 6.88 | 0.25 | 0.25 | No | SECOND_FLOOR_WALL_EAST
SECOND_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 6.88 | 0.25 | 0.25 | No | SECOND_FLOOR_WALL_SOUTH
SECOND_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 6.88 | 0.25 | 0.25 | No | SECOND_FLOOR_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_2:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27500.82 | 2.96
PSZ-AC_1:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 35779.21 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC_2:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.3 | 1853.48 | 1 | General
PSZ-AC_1:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.87 | 2664.86 | 1 | General
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
Nominal Capacity [W]
PSZ-AC_2:1_UNITARY_PACKAGE_HEATCOIL | 19219.71
PSZ-AC_1:2_UNITARY_PACKAGE_HEATCOIL | 26005.87
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 9022.9199 | 11.5035 | 46.4304 | 0 | 0.0001 | 15836.5396 | 3549.8804
February | 7890.6268 | 10.0851 | 40.9568 | 0 | 0.0001 | 13969.7299 | 3107.6522
March | 9051.0129 | 11.8309 | 50.6594 | 0 | 0.0001 | 17280.3712 | 3598.5239
April | 9607.7249 | 12.6109 | 54.5081 | 0 | 0.0002 | 18593.4276 | 3826.6064
May | 11606.6684 | 15.2384 | 65.9002 | 0 | 0.0002 | 22479.4447 | 4623.2273
June | 12659.6278 | 16.6231 | 71.9107 | 0 | 0.0002 | 24529.7357 | 5042.9426
July | 13504.6465 | 17.7335 | 76.7228 | 0 | 0.0002 | 26171.2077 | 5379.6659
August | 13530.0305 | 17.7669 | 76.8675 | 0 | 0.0002 | 26220.5536 | 5389.7819
September | 11723.8969 | 15.3932 | 66.5781 | 0 | 0.0002 | 22710.687 | 4670.0355
October | 10199.482 | 13.3878 | 57.867 | 0 | 0.0002 | 19739.2195 | 4062.3099
November | 8779.2988 | 11.4865 | 49.2884 | 0 | 0.0001 | 16812.7748 | 3491.8743
December | 8604.8828 | 11.0119 | 44.8584 | 0 | 0.0001 | 15300.5665 | 3390.7427
Annual Sum or Average | 126180.8183 | 164.6717 | 702.5477 | 0 | 0.002 | 239644.2578 | 50133.2429
Minimum of Months | 7890.6268 | 10.0851 | 40.9568 | 0 | 0.0001 | 13969.7299 | 3107.6522
Maximum of Months | 13530.0305 | 17.7669 | 76.8675 | 0 | 0.0002 | 26220.5536 | 5389.7819
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 35038400000 | 29446.103 | 03-JAN-13:00 | 9001.312 | 6750.984 | 4518.344 | 0 | 9175.463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 30908100000 | 29989.467 | 23-FEB-14:00 | 9001.312 | 6750.984 | 4518.344 | 0 | 9718.827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 38232900000 | 30116.552 | 29-MAR-11:00 | 9001.312 | 6750.984 | 4518.344 | 0 | 9845.912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 41138000000 | 31709.705 | 21-APR-14:00 | 9001.312 | 6750.984 | 4518.344 | 0 | 11439.065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 49735800000 | 35970.187 | 18-MAY-14:00 | 9001.312 | 6750.984 | 4518.344 | 0 | 15699.547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 54272100000 | 36148.682 | 13-JUN-14:00 | 9001.312 | 6750.984 | 4518.344 | 0 | 15878.042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 57903800000 | 37310.272 | 18-JUL-12:00 | 9001.312 | 6750.984 | 4518.344 | 0 | 17039.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 58013000000 | 37353.34 | 31-AUG-13:00 | 9001.312 | 6750.984 | 4518.344 | 0 | 17082.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 50247400000 | 36248.786 | 15-SEP-14:00 | 9001.312 | 6750.984 | 4518.344 | 0 | 15978.146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 43673100000 | 32874.134 | 13-OCT-14:00 | 9001.312 | 6750.984 | 4518.344 | 0 | 12603.494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 37198300000 | 30755.644 | 03-NOV-14:39 | 9001.312 | 6750.984 | 4518.344 | 0 | 10485.004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 33852500000 | 29154.263 | 19-DEC-15:20 | 9001.312 | 6750.984 | 4518.344 | 0 | 8883.623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 530213000000 | [7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 30908100000 | 29154.263 |  | 9001.312 | 6750.984 | 4518.344 | 0 | 8883.623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 58013000000 | 37353.34 |  | 9001.312 | 6750.984 | 4518.344 | 0 | 17082.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 17002.27 | 451.17 | 0 | 17453.44
Cost per Total Building Area ($/m2) | 18.29 | 0.49 | 0 | 18.78
Cost per Net Conditioned Building Area ($/m2) | 18.29 | 0.49 | 0 | 18.78
3-phoenix
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 613.23 | 659.74 | 659.74
Net Site Energy | 613.23 | 659.74 | 659.74
Total Source Energy | 1872.11 | 2014.1 | 2014.1
Net Source Energy | 1872.11 | 2014.1 | 2014.1
Area (m2)
Total Building Area | 929.5
Net Conditioned Building Area | 929.5
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 22.94 | 0 | 0 | 0 | 0
Cooling | 159.71 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 109.85 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 134.31 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 176.75 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 9.66 | 0 | 0 | 0 | 10.03
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 580.62 | 32.61 | 0 | 0 | 0 | 10.03
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 580.62 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 580.62 | 100
Total On-Site and Utility Electric Sources | 580.62 | 100
Total Electricity End Uses | 580.62 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
FIRST_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 0 | 90 | N
FIRST_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 90 | 90 | E
FIRST_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 180 | 90 | S
FIRST_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 270 | 90 | W
FIRST_FLOOR_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 464.75 | 0 | 180
SECOND_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 0 | 90 | N
SECOND_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 90 | 90 | E
SECOND_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 180 | 90 | S
SECOND_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 270 | 90 | W
WEST-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 36.51 | 270 | 45
EAST-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 36.51 | 90 | 45
SOUTH-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 217.73 | 180 | 18.43
NORTH-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 217.73 | 0 | 18.44
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
FIRST_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 6.88 | 0.25 | 0.25 | No | FIRST_FLOOR_WALL_NORTH
FIRST_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 6.88 | 0.25 | 0.25 | No | FIRST_FLOOR_WALL_EAST
FIRST_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 6.88 | 0.25 | 0.25 | No | FIRST_FLOOR_WALL_SOUTH
FIRST_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 6.88 | 0.25 | 0.25 | No | FIRST_FLOOR_WALL_WEST
SECOND_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 6.88 | 0.25 | 0.25 | No | SECOND_FLOOR_WALL_NORTH
SECOND_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 6.88 | 0.25 | 0.25 | No | SECOND_FLOOR_WALL_EAST
SECOND_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 6.88 | 0.25 | 0.25 | No | SECOND_FLOOR_WALL_SOUTH
SECOND_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 6.88 | 0.25 | 0.25 | No | SECOND_FLOOR_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_2:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 29157.5 | 2.96
PSZ-AC_1:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 39630.2 | 2.78
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC_2:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.57 | 2246.74 | 1 | General
PSZ-AC_1:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 2.35 | 3358.06 | 1 | General
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
Nominal Capacity [W]
PSZ-AC_2:1_UNITARY_PACKAGE_HEATCOIL | 15037.94
PSZ-AC_1:2_UNITARY_PACKAGE_HEATCOIL | 19941.45
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 7487.0246 | 12.3407 | 40.1403 | 0 | 0.0001 | 296499.186 | 3151.9573
February | 6735.833 | 11.1561 | 36.5004 | 0 | 0.0001 | 269615.6395 | 2841.1302
March | 8265.8791 | 13.8999 | 46.3086 | 0 | 0.0001 | 342075.5962 | 3507.7002
April | 8608.4884 | 14.5174 | 48.527 | 0 | 0.0001 | 358464.5894 | 3657.2686
May | 10295.9389 | 17.3689 | 58.0816 | 0 | 0.0002 | 429044.1763 | 4374.7639
June | 12469.6309 | 21.0442 | 70.4038 | 0 | 0.0002 | 520067.71 | 5299.2077
July | 13415.5323 | 22.6424 | 75.7581 | 0 | 0.0002 | 559619.4711 | 5701.378
August | 13328.9555 | 22.4957 | 75.2646 | 0 | 0.0002 | 555974.1399 | 5664.5204
September | 11428.3848 | 19.2843 | 64.5059 | 0 | 0.0002 | 476499.9941 | 4856.4442
October | 9054.6901 | 15.2706 | 51.0477 | 0 | 0.0001 | 377085.1818 | 3846.9113
November | 7511.2571 | 12.6489 | 42.2109 | 0 | 0.0001 | 311807.4988 | 3189.2869
December | 7595.7075 | 12.3942 | 39.814 | 0 | 0.0001 | 294082.0798 | 3185.0045
Annual Sum or Average | 116197.3221 | 195.0634 | 648.5627 | 0 | 0.0018 | 4790835.2629 | 49275.5734
Minimum of Months | 6735.833 | 11.1561 | 36.5004 | 0 | 0.0001 | 269615.6395 | 2841.1302
Maximum of Months | 13415.5323 | 22.6424 | 75.7581 | 0 | 0.0002 | 559619.4711 | 5701.378
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 35934000000 | 27386.034 | 27-JAN-14:00 | 9001.312 | 6750.984 | 5604.8 | 0 | 6028.937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 32675800000 | 29040.897 | 28-FEB-15:00 | 9001.312 | 6750.984 | 5604.8 | 0 | 7683.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 41457600000 | 33723.599 | 17-MAR-14:00 | 9001.312 | 6750.984 | 5604.8 | 0 | 12366.503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 43443800000 | 34185.747 | 26-APR-14:00 | 9001.312 | 6750.984 | 5604.8 | 0 | 12828.651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 51997700000 | 38222.862 | 30-MAY-14:00 | 9001.312 | 6750.984 | 5604.8 | 0 | 16865.765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 63029200000 | 45017.357 | 28-JUN-14:00 | 9001.312 | 6750.984 | 5604.8 | 0 | 23660.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 67822600000 | 43903.738 | 19-JUL-14:00 | 9001.312 | 6750.984 | 5604.8 | 0 | 22546.641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 67380800000 | 44309.07 | 01-AUG-14:00 | 9001.312 | 6750.984 | 5604.8 | 0 | 22951.973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 57749000000 | 40682.901 | 08-SEP-14:30 | 9001.312 | 6750.984 | 5604.8 | 0 | 19325.805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 45700500000 | 34388.306 | 13-OCT-14:00 | 9001.312 | 6750.984 | 5604.8 | 0 | 13031.209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 37789300000 | 31222.817 | 13-NOV-15:00 | 9001.312 | 6750.984 | 5604.8 | 0 | 9865.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 35641000000 | 26140.452 | 11-DEC-15:00 | 9001.312 | 6750.984 | 5604.8 | 0 | 4783.356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 580621000000 | [7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 32675800000 | 26140.452 |  | 9001.312 | 6750.984 | 5604.8 | 0 | 4783.356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 67822600000 | 45017.357 |  | 9001.312 | 6750.984 | 5604.8 | 0 | 23660.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 17232.02 | 268.97 | 0 | 17500.99
Cost per Total Building Area ($/m2) | 18.54 | 0.29 | 0 | 18.83
Cost per Net Conditioned Building Area ($/m2) | 18.54 | 0.29 | 0 | 18.83
4-atlanta
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 549.63 | 591.32 | 591.32
Net Site Energy | 549.63 | 591.32 | 591.32
Total Source Energy | 1678.8 | 1806.13 | 1806.13
Net Source Energy | 1678.8 | 1806.13 | 1806.13
Area (m2)
Total Building Area | 929.5
Net Conditioned Building Area | 929.5
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 64.88 | 0 | 0 | 0 | 0
Cooling | 93.15 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 109.85 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 134.31 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 137.43 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 10.01 | 0 | 0 | 0 | 10.03
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 474.74 | 74.89 | 0 | 0 | 0 | 10.03
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 474.74 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 474.74 | 100
Total On-Site and Utility Electric Sources | 474.74 | 100
Total Electricity End Uses | 474.74 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
FIRST_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 80.5 | 0 | 90 | N
FIRST_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 53.67 | 90 | 90 | E
FIRST_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 80.5 | 180 | 90 | S
FIRST_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 53.67 | 270 | 90 | W
FIRST_FLOOR_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 464.75 | 0 | 180
SECOND_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 80.5 | 0 | 90 | N
SECOND_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 53.67 | 90 | 90 | E
SECOND_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 80.5 | 180 | 90 | S
SECOND_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 53.67 | 270 | 90 | W
WEST-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 36.51 | 270 | 45
EAST-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 36.51 | 90 | 45
SOUTH-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 217.73 | 180 | 18.43
NORTH-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 217.73 | 0 | 18.44
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
FIRST_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_NORTH
FIRST_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_EAST
FIRST_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_SOUTH
FIRST_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_WEST
SECOND_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_NORTH
SECOND_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_EAST
SECOND_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_SOUTH
SECOND_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_2:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 24730.86 | 2.96
PSZ-AC_1:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 33139.23 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC_2:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.22 | 1742.5 | 1 | General
PSZ-AC_1:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.83 | 2615.3 | 1 | General
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
Nominal Capacity [W]
PSZ-AC_2:1_UNITARY_PACKAGE_HEATCOIL | 19477.48
PSZ-AC_1:2_UNITARY_PACKAGE_HEATCOIL | 26956.81
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 7515.5363 | 13.212 | 31.3575 | 0 | 0.0001 | 55767.2016 | 3191.2908
February | 6561.5367 | 11.8004 | 28.6784 | 0 | 0.0001 | 51005.5199 | 2810.715
March | 7001.0395 | 13.3043 | 34.0967 | 0 | 0.0001 | 60649.3724 | 3064.8693
April | 7262.1698 | 13.9012 | 35.8621 | 0 | 0.0001 | 63790.4687 | 3188.4847
May | 8559.3456 | 16.4829 | 42.7514 | 0 | 0.0002 | 76045.9892 | 3767.1268
June | 9381.0046 | 18.0718 | 46.888 | 0 | 0.0002 | 83404.2026 | 4129.3693
July | 9936.7807 | 19.1438 | 49.6725 | 0 | 0.0002 | 88357.1166 | 4374.1363
August | 10073.6414 | 19.4081 | 50.3596 | 0 | 0.0002 | 89579.3714 | 4434.438
September | 8830.9881 | 17.0097 | 44.1266 | 0 | 0.0002 | 78492.1963 | 3887.0286
October | 7348.5079 | 14.1448 | 36.6725 | 0 | 0.0001 | 65232.6669 | 3233.6268
November | 6506.8871 | 12.2805 | 31.2749 | 0 | 0.0001 | 55629.3505 | 2840.7213
December | 7118.586 | 12.8097 | 31.1497 | 0 | 0.0001 | 55400.7556 | 3050.0223
Annual Sum or Average | 96096.0235 | 181.5692 | 462.8899 | 0 | 0.0017 | 823354.2118 | 41971.8291
Minimum of Months | 6506.8871 | 11.8004 | 28.6784 | 0 | 0.0001 | 51005.5199 | 2810.715
Maximum of Months | 10073.6414 | 19.4081 | 50.3596 | 0 | 0.0002 | 89579.3714 | 4434.438
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 32154800000 | 22841.846 | 23-JAN-15:00 | 9001.312 | 6750.984 | 4357.796 | 0 | 2731.754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 29409300000 | 23985.089 | 22-FEB-15:00 | 9001.312 | 6750.984 | 4357.796 | 0 | 3874.996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 34969900000 | 27097.377 | 28-MAR-14:00 | 9001.312 | 6750.984 | 4357.796 | 0 | 6987.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 36781000000 | 30037.161 | 14-APR-14:00 | 9001.312 | 6750.984 | 4357.796 | 0 | 9927.068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 43847400000 | 32252.265 | 15-MAY-14:00 | 9001.312 | 6750.984 | 4357.796 | 0 | 12142.172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 48090100000 | 33974.367 | 19-JUN-14:00 | 9001.312 | 6750.984 | 4357.796 | 0 | 13864.274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 50945900000 | 36497.485 | 03-JUL-14:00 | 9001.312 | 6750.984 | 4357.796 | 0 | 16387.393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 51650600000 | 34791.379 | 17-AUG-14:00 | 9001.312 | 6750.984 | 4357.796 | 0 | 14681.286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 45257900000 | 32793.544 | 11-SEP-13:00 | 9001.312 | 6750.984 | 4357.796 | 0 | 12683.452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 37612500000 | 29409.163 | 02-OCT-14:39 | 9001.312 | 6750.984 | 4357.796 | 0 | 9299.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 32075400000 | 26294.042 | 22-NOV-14:00 | 9001.312 | 6750.984 | 4357.796 | 0 | 6183.949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 31943600000 | 22898.678 | 05-DEC-14:50 | 9001.312 | 6750.984 | 4357.796 | 0 | 2788.585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 474738000000 | [7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 29409300000 | 22841.846 |  | 9001.312 | 6750.984 | 4357.796 | 0 | 2731.754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 51650600000 | 36497.485 |  | 9001.312 | 6750.984 | 4357.796 | 0 | 16387.393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 15025.15 | 714.23 | 0 | 15739.38
Cost per Total Building Area ($/m2) | 16.16 | 0.77 | 0 | 16.93
Cost per Net Conditioned Building Area ($/m2) | 16.16 | 0.77 | 0 | 16.93
5-losangeles
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 405.83 | 436.61 | 436.61
Net Site Energy | 405.83 | 436.61 | 436.61
Total Source Energy | 1227.49 | 1320.59 | 1320.59
Net Source Energy | 1227.49 | 1320.59 | 1320.59
Area (m2)
Total Building Area | 929.5
Net Conditioned Building Area | 929.5
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 4.29 | 0 | 0 | 0 | 0
Cooling | 29.75 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 109.85 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 134.31 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 117.66 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 9.97 | 0 | 0 | 0 | 10.03
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 391.58 | 14.25 | 0 | 0 | 0 | 10.03
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 391.58 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 391.58 | 100
Total On-Site and Utility Electric Sources | 391.58 | 100
Total Electricity End Uses | 391.58 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
FIRST_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 80.5 | 0 | 90 | N
FIRST_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 53.67 | 90 | 90 | E
FIRST_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 80.5 | 180 | 90 | S
FIRST_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 53.67 | 270 | 90 | W
FIRST_FLOOR_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 464.75 | 0 | 180
SECOND_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 80.5 | 0 | 90 | N
SECOND_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 53.67 | 90 | 90 | E
SECOND_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 80.5 | 180 | 90 | S
SECOND_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 53.67 | 270 | 90 | W
WEST-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 36.51 | 270 | 45
EAST-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 36.51 | 90 | 45
SOUTH-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 217.73 | 180 | 18.43
NORTH-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 217.73 | 0 | 18.44
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
FIRST_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_NORTH
FIRST_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_EAST
FIRST_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_SOUTH
FIRST_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_WEST
SECOND_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_NORTH
SECOND_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_EAST
SECOND_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_SOUTH
SECOND_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_2:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17691.52 | 3.05
PSZ-AC_1:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 25541.98 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC_2:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.07 | 1526.78 | 1 | General
PSZ-AC_1:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.54 | 2204.27 | 1 | General
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
Nominal Capacity [W]
PSZ-AC_2:1_UNITARY_PACKAGE_HEATCOIL | 10380.99
PSZ-AC_1:2_UNITARY_PACKAGE_HEATCOIL | 14155.72
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 2839.8127 | 2.4382 | 25.0563 | 0 | 0 | 151181.1843 | 1059.3098
February | 2519.4744 | 2.1607 | 22.682 | 0 | 0 | 136857.1661 | 941.1963
March | 2858.8305 | 2.4492 | 26.1763 | 0 | 0 | 157941.9123 | 1069.3088
April | 2734.7981 | 2.3429 | 25.0522 | 0 | 0 | 151159.5255 | 1022.9515
May | 2914.4457 | 2.4964 | 26.7688 | 0 | 0 | 161517.5531 | 1090.3652
June | 2913.5195 | 2.4955 | 26.7763 | 0 | 0 | 161562.4372 | 1090.0673
July | 3108.3933 | 2.6624 | 28.5827 | 0 | 0 | 172462.1721 | 1163.0248
August | 3358.5635 | 2.8764 | 30.9158 | 0 | 0 | 186539.9105 | 1256.7275
September | 3033.9831 | 2.5986 | 27.8997 | 0 | 0 | 168341.2647 | 1135.1876
October | 2905.0835 | 2.4884 | 26.6866 | 0 | 0 | 161021.3706 | 1086.874
November | 2715.084 | 2.3257 | 24.9205 | 0 | 0 | 150365.2878 | 1015.7267
December | 2778.498 | 2.3829 | 24.9971 | 0 | 0 | 150825.5019 | 1037.908
Annual Sum or Average | 34680.4863 | 29.7174 | 316.5144 | 0 | 0.0001 | 1909775.2862 | 12968.6476
Minimum of Months | 2519.4744 | 2.1607 | 22.682 | 0 | 0 | 136857.1661 | 941.1963
Maximum of Months | 3358.5635 | 2.8764 | 30.9158 | 0 | 0 | 186539.9105 | 1256.7275
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 30997800000 | 26089.243 | 26-JAN-13:00 | 9001.312 | 6750.984 | 3731.05 | 0 | 6605.896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 28060900000 | 24905.829 | 13-FEB-11:00 | 9001.312 | 6750.984 | 3731.05 | 0 | 5422.483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 32384000000 | 26036.835 | 31-MAR-14:39 | 9001.312 | 6750.984 | 3731.05 | 0 | 6553.488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 30993400000 | 26343.087 | 13-APR-11:00 | 9001.312 | 6750.984 | 3731.05 | 0 | 6859.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 33117200000 | 27372.41 | 30-MAY-13:09 | 9001.312 | 6750.984 | 3731.05 | 0 | 7889.064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 33126400000 | 27339.217 | 28-JUN-13:00 | 9001.312 | 6750.984 | 3731.05 | 0 | 7855.871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 35361200000 | 27978.304 | 24-JUL-14:00 | 9001.312 | 6750.984 | 3731.05 | 0 | 8494.957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 38247700000 | 30145.641 | 09-AUG-14:50 | 9001.312 | 6750.984 | 3731.05 | 0 | 10662.294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 34516300000 | 28761.112 | 25-SEP-14:00 | 9001.312 | 6750.984 | 3731.05 | 0 | 9277.765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 33015400000 | 27456.338 | 05-OCT-14:20 | 9001.312 | 6750.984 | 3731.05 | 0 | 7972.991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 30830500000 | 25715.926 | 10-NOV-14:00 | 9001.312 | 6750.984 | 3731.05 | 0 | 6232.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 30924900000 | 26128.483 | 19-DEC-12:00 | 9001.312 | 6750.984 | 3731.05 | 0 | 6645.137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 391576000000 | [7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 28060900000 | 24905.829 |  | 9001.312 | 6750.984 | 3731.05 | 0 | 5422.483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 38247700000 | 30145.641 |  | 9001.312 | 6750.984 | 3731.05 | 0 | 10662.294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 14717 | 122.85 | 0 | 14839.85
Cost per Total Building Area ($/m2) | 15.83 | 0.13 | 0 | 15.97
Cost per Net Conditioned Building Area ($/m2) | 15.83 | 0.13 | 0 | 15.97
6-lasvegas
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 563.62 | 606.37 | 606.37
Net Site Energy | 563.62 | 606.37 | 606.37
Total Source Energy | 1921.43 | 2067.16 | 2067.16
Net Source Energy | 1921.43 | 2067.16 | 2067.16
Area (m2)
Total Building Area | 929.5
Net Conditioned Building Area | 929.5
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 28.27 | 0 | 0 | 0 | 0
Cooling | 112.43 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 109.85 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 134.31 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 168.94 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 9.82 | 0 | 0 | 0 | 10.03
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 525.53 | 38.09 | 0 | 0 | 0 | 10.03
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 525.53 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 525.53 | 100
Total On-Site and Utility Electric Sources | 525.53 | 100
Total Electricity End Uses | 525.53 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
FIRST_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 80.5 | 0 | 90 | N
FIRST_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 53.67 | 90 | 90 | E
FIRST_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 80.5 | 180 | 90 | S
FIRST_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 53.67 | 270 | 90 | W
FIRST_FLOOR_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 464.75 | 0 | 180
SECOND_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 80.5 | 0 | 90 | N
SECOND_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 53.67 | 90 | 90 | E
SECOND_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 80.5 | 180 | 90 | S
SECOND_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 53.67 | 270 | 90 | W
WEST-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 36.51 | 270 | 45
EAST-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 36.51 | 90 | 45
SOUTH-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 217.73 | 180 | 18.43
NORTH-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 217.73 | 0 | 18.44
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
FIRST_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_NORTH
FIRST_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_EAST
FIRST_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_SOUTH
FIRST_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_WEST
SECOND_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_NORTH
SECOND_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_EAST
SECOND_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_SOUTH
SECOND_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_2:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 24859.46 | 2.96
PSZ-AC_1:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 37396.16 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC_2:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.49 | 2129.86 | 1 | General
PSZ-AC_1:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 2.26 | 3227.29 | 1 | General
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
Nominal Capacity [W]
PSZ-AC_2:1_UNITARY_PACKAGE_HEATCOIL | 15459.99
PSZ-AC_1:2_UNITARY_PACKAGE_HEATCOIL | 21245.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 8412.67 | 13.2893 | 53.1649 | 0 | 0.0001 | 265130.2717 | 3499.1924
February | 7172.3548 | 11.6409 | 48.2487 | 0 | 0.0001 | 240625.1678 | 3015.6044
March | 8203.8509 | 13.3242 | 55.274 | 0 | 0.0001 | 275662.1433 | 3450.2509
April | 8644.4929 | 14.1453 | 59.2337 | 0 | 0.0001 | 295413.6479 | 3646.526
May | 10193.2602 | 16.6845 | 69.8927 | 0 | 0.0001 | 348572.7526 | 4300.3603
June | 12553.0676 | 20.5562 | 86.1593 | 0 | 0.0002 | 429699.1937 | 5296.874
July | 13665.2267 | 22.3796 | 93.8133 | 0 | 0.0002 | 467871.5046 | 5766.3859
August | 13665.0171 | 22.3789 | 93.8081 | 0 | 0.0002 | 467845.5981 | 5766.256
September | 11289.1883 | 18.4836 | 77.4563 | 0 | 0.0001 | 386294.6783 | 4763.2566
October | 8950.0637 | 14.6457 | 61.3319 | 0 | 0.0001 | 305877.6828 | 3775.4735
November | 7648.8458 | 12.4565 | 51.8515 | 0 | 0.0001 | 258594.3843 | 3220.3387
December | 8202.429 | 13.059 | 52.7932 | 0 | 0.0001 | 263280.2431 | 3422.3254
Annual Sum or Average | 118600.467 | 193.0436 | 803.0275 | 0 | 0.0015 | 4004867.2682 | 49922.8442
Minimum of Months | 7172.3548 | 11.6409 | 48.2487 | 0 | 0.0001 | 240625.1678 | 3015.6044
Maximum of Months | 13665.2267 | 22.3796 | 93.8133 | 0 | 0.0002 | 467871.5046 | 5766.3859
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 34791500000 | 21109.576 | 19-JAN-14:00 | 9001.312 | 6750.984 | 5357.147 | 0 | 0.132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 31575800000 | 24037.218 | 08-FEB-15:00 | 9001.312 | 6750.984 | 5357.147 | 0 | 2927.775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 36173500000 | 28487.568 | 31-MAR-14:00 | 9001.312 | 6750.984 | 5357.147 | 0 | 7378.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 38765400000 | 33446.964 | 21-APR-14:00 | 9001.312 | 6750.984 | 5357.147 | 0 | 12337.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 45741100000 | 35328.681 | 31-MAY-14:00 | 9001.312 | 6750.984 | 5357.147 | 0 | 14219.237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 56386900000 | 41434.632 | 27-JUN-14:00 | 9001.312 | 6750.984 | 5357.147 | 0 | 20325.188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 61396000000 | 40091.407 | 24-JUL-14:00 | 9001.312 | 6750.984 | 5357.147 | 0 | 18981.963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 61392600000 | 39812.822 | 04-AUG-14:00 | 9001.312 | 6750.984 | 5357.147 | 0 | 18703.378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 50691100000 | 39077.647 | 01-SEP-14:00 | 9001.312 | 6750.984 | 5357.147 | 0 | 17968.203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 40138500000 | 33501.318 | 03-OCT-14:00 | 9001.312 | 6750.984 | 5357.147 | 0 | 12391.874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 33933800000 | 25543.69 | 10-NOV-14:50 | 9001.312 | 6750.984 | 5357.147 | 0 | 4434.246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 34548700000 | 23981.28 | 05-DEC-14:00 | 9001.312 | 6750.984 | 5357.147 | 0 | 2871.837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 525535000000 | [7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 31575800000 | 21109.576 |  | 9001.312 | 6750.984 | 5357.147 | 0 | 0.132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 61396000000 | 41434.632 |  | 9001.312 | 6750.984 | 5357.147 | 0 | 20325.188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 14231.15 | 293.61 | 0 | 14524.76
Cost per Total Building Area ($/m2) | 15.31 | 0.32 | 0 | 15.63
Cost per Net Conditioned Building Area ($/m2) | 15.31 | 0.32 | 0 | 15.63
7-sanfrancisco
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 435 | 467.99 | 467.99
Net Site Energy | 435 | 467.99 | 467.99
Total Source Energy | 1240.68 | 1334.78 | 1334.78
Net Source Energy | 1240.68 | 1334.78 | 1334.78
Area (m2)
Total Building Area | 929.5
Net Conditioned Building Area | 929.5
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 42.59 | 0 | 0 | 0 | 0
Cooling | 11.28 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 109.85 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 134.31 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 126.82 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 10.15 | 0 | 0 | 0 | 10.03
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 382.26 | 52.74 | 0 | 0 | 0 | 10.03
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 382.26 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 382.26 | 100
Total On-Site and Utility Electric Sources | 382.26 | 100
Total Electricity End Uses | 382.26 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
FIRST_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 80.5 | 0 | 90 | N
FIRST_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 53.67 | 90 | 90 | E
FIRST_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 80.5 | 180 | 90 | S
FIRST_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 53.67 | 270 | 90 | W
FIRST_FLOOR_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 464.75 | 0 | 180
SECOND_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 80.5 | 0 | 90 | N
SECOND_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 53.67 | 90 | 90 | E
SECOND_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 80.5 | 180 | 90 | S
SECOND_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 53.67 | 270 | 90 | W
WEST-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 36.51 | 270 | 45
EAST-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 36.51 | 90 | 45
SOUTH-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 217.73 | 180 | 18.43
NORTH-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 217.73 | 0 | 18.44
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
FIRST_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 6.88 | 0.61 | 0.61 | No | FIRST_FLOOR_WALL_NORTH
FIRST_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 6.88 | 0.61 | 0.61 | No | FIRST_FLOOR_WALL_EAST
FIRST_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 6.88 | 0.61 | 0.61 | No | FIRST_FLOOR_WALL_SOUTH
FIRST_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 6.88 | 0.61 | 0.61 | No | FIRST_FLOOR_WALL_WEST
SECOND_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 6.88 | 0.61 | 0.61 | No | SECOND_FLOOR_WALL_NORTH
SECOND_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 6.88 | 0.61 | 0.61 | No | SECOND_FLOOR_WALL_EAST
SECOND_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 6.88 | 0.61 | 0.61 | No | SECOND_FLOOR_WALL_SOUTH
SECOND_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 6.88 | 0.61 | 0.61 | No | SECOND_FLOOR_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_2:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20080.15 | 3.05
PSZ-AC_1:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 26518.78 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC_2:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.21 | 1732.92 | 1 | General
PSZ-AC_1:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.6 | 2288.57 | 1 | General
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
Nominal Capacity [W]
PSZ-AC_2:1_UNITARY_PACKAGE_HEATCOIL | 14093.13
PSZ-AC_1:2_UNITARY_PACKAGE_HEATCOIL | 19006.23
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 3516.8614 | 3.0519 | 25.2429 | 0 | 0 | 152286.6233 | 1294.2068
February | 2739.1261 | 2.3582 | 23.0147 | 0 | 0 | 138858.5087 | 1018.233
March | 3099.6553 | 2.668 | 26.1582 | 0 | 0 | 157825.3493 | 1152.6036
April | 2833.9141 | 2.4338 | 24.8866 | 0 | 0 | 150156.9263 | 1056.7506
May | 2895.9283 | 2.4817 | 26.3876 | 0 | 0 | 159216.4209 | 1082.7931
June | 2865.4043 | 2.4548 | 26.2537 | 0 | 0 | 158409.4017 | 1071.8204
July | 2908.7437 | 2.4915 | 26.7157 | 0 | 0 | 161196.6792 | 1088.2295
August | 3022.0882 | 2.5886 | 27.7626 | 0 | 0 | 167513.5847 | 1130.6523
September | 2902.1396 | 2.4858 | 26.6651 | 0 | 0 | 160891.4005 | 1085.7894
October | 2869.6717 | 2.4587 | 26.2369 | 0 | 0 | 158307.3584 | 1073.2458
November | 2847.8213 | 2.4478 | 24.6473 | 0 | 0 | 148711.8265 | 1060.8338
December | 3376.809 | 2.926 | 25.0221 | 0 | 0 | 150957.9701 | 1245.0608
Annual Sum or Average | 35878.163 | 30.8468 | 308.9934 | 0 | 0.0001 | 1864332.0497 | 13360.2191
Minimum of Months | 2739.1261 | 2.3582 | 23.0147 | 0 | 0 | 138858.5087 | 1018.233
Maximum of Months | 3516.8614 | 3.0519 | 27.7626 | 0 | 0 | 167513.5847 | 1294.2068
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 31224500000 | 20521.068 | 27-JAN-15:00 | 9001.312 | 6750.984 | 4021.488 | 0 | 747.283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 28471200000 | 23529.551 | 15-FEB-15:00 | 9001.312 | 6750.984 | 4021.488 | 0 | 3755.767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 32360100000 | 21104.518 | 01-MAR-14:30 | 9001.312 | 6750.984 | 4021.488 | 0 | 1330.734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 30787800000 | 25087.088 | 13-APR-14:00 | 9001.312 | 6750.984 | 4021.488 | 0 | 5313.303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 32645300000 | 26274.31 | 17-MAY-13:00 | 9001.312 | 6750.984 | 4021.488 | 0 | 6500.525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 32479900000 | 27381.744 | 16-JUN-14:00 | 9001.312 | 6750.984 | 4021.488 | 0 | 7607.959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 33051400000 | 29563.845 | 03-JUL-12:00 | 9001.312 | 6750.984 | 4021.488 | 0 | 9790.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 34346600000 | 27969.489 | 15-AUG-11:00 | 9001.312 | 6750.984 | 4021.488 | 0 | 8195.704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 32988800000 | 31942.042 | 28-SEP-14:00 | 9001.312 | 6750.984 | 4021.488 | 0 | 12168.258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 32459000000 | 26210.766 | 31-OCT-13:20 | 9001.312 | 6750.984 | 4021.488 | 0 | 6436.981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 30491500000 | 21168.151 | 08-NOV-14:50 | 9001.312 | 6750.984 | 4021.488 | 0 | 1394.367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 30952100000 | 20537.009 | 07-DEC-14:00 | 9001.312 | 6750.984 | 4021.488 | 0 | 763.225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 382258000000 | [7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 28471200000 | 20521.068 |  | 9001.312 | 6750.984 | 4021.488 | 0 | 747.283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 34346600000 | 31942.042 |  | 9001.312 | 6750.984 | 4021.488 | 0 | 12168.258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 16402.5 | 462.11 | 0 | 16864.61
Cost per Total Building Area ($/m2) | 17.65 | 0.5 | 0 | 18.14
Cost per Net Conditioned Building Area ($/m2) | 17.65 | 0.5 | 0 | 18.14
8-baltimore
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 594.44 | 639.53 | 639.53
Net Site Energy | 594.44 | 639.53 | 639.53
Total Source Energy | 1751.61 | 1884.46 | 1884.46
Net Source Energy | 1751.61 | 1884.46 | 1884.46
Area (m2)
Total Building Area | 929.5
Net Conditioned Building Area | 929.5
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 140.43 | 0 | 0 | 0 | 0
Cooling | 69.38 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 109.85 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 134.31 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 130.29 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 10.17 | 0 | 0 | 0 | 10.03
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 443.83 | 150.61 | 0 | 0 | 0 | 10.03
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 443.83 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 443.83 | 100
Total On-Site and Utility Electric Sources | 443.83 | 100
Total Electricity End Uses | 443.83 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
FIRST_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 0 | 90 | N
FIRST_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 90 | 90 | E
FIRST_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 180 | 90 | S
FIRST_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 270 | 90 | W
FIRST_FLOOR_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 464.75 | 0 | 180
SECOND_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 0 | 90 | N
SECOND_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 90 | 90 | E
SECOND_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 180 | 90 | S
SECOND_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 270 | 90 | W
WEST-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 36.51 | 270 | 45
EAST-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 36.51 | 90 | 45
SOUTH-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 217.73 | 180 | 18.43
NORTH-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 217.73 | 0 | 18.44
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
FIRST_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_NORTH
FIRST_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_EAST
FIRST_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_SOUTH
FIRST_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_WEST
SECOND_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_NORTH
SECOND_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_EAST
SECOND_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_SOUTH
SECOND_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_2:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 24699.27 | 2.96
PSZ-AC_1:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 32059.86 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC_2:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.17 | 1669.36 | 1 | General
PSZ-AC_1:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.72 | 2462.12 | 1 | General
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
Nominal Capacity [W]
PSZ-AC_2:1_UNITARY_PACKAGE_HEATCOIL | 21508.47
PSZ-AC_1:2_UNITARY_PACKAGE_HEATCOIL | 30135.15
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 7620.4259 | 12.6998 | 31.9617 | 0 | 0.0001 | 1987.1243 | 3166.1986
February | 6489.5531 | 11.1347 | 28.9832 | 0 | 0.0001 | 1802.0793 | 2725.5562
March | 6195.8319 | 11.6406 | 33.2475 | 0 | 0.0001 | 2067.6156 | 2694.535
April | 5501.3334 | 10.7976 | 32.0704 | 0 | 0.0001 | 1994.5666 | 2434.7238
May | 6388.4953 | 12.7237 | 38.2628 | 0 | 0.0002 | 2379.7512 | 2844.257
June | 7654.7117 | 15.2579 | 45.915 | 0 | 0.0002 | 2855.6817 | 3409.1288
July | 8256.8477 | 16.4612 | 49.5433 | 0 | 0.0002 | 3081.3469 | 3677.5725
August | 8497.9929 | 16.9433 | 50.9979 | 0 | 0.0002 | 3171.8171 | 3785.1049
September | 6652.0605 | 13.2538 | 39.8702 | 0 | 0.0002 | 2479.722 | 2962.0768
October | 6081.4461 | 11.9582 | 35.574 | 0 | 0.0001 | 2212.4735 | 2693.4809
November | 5982.3949 | 11.2163 | 31.9734 | 0 | 0.0001 | 1988.3756 | 2599.5805
December | 7133.9939 | 12.2091 | 31.6884 | 0 | 0.0001 | 1970.2643 | 2993.3508
Annual Sum or Average | 82455.0873 | 156.2962 | 450.0878 | 0 | 0.0018 | 27990.818 | 35985.5656
Minimum of Months | 5501.3334 | 10.7976 | 28.9832 | 0 | 0.0001 | 1802.0793 | 2434.7238
Maximum of Months | 8497.9929 | 16.9433 | 50.9979 | 0 | 0.0002 | 3171.8171 | 3785.1049
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 31508600000 | 19883.78 | 17-JAN-12:39 | 9001.312 | 6750.984 | 4131.484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 28574500000 | 19892.365 | 15-FEB-15:00 | 9001.312 | 6750.984 | 4131.484 | 0 | 8.585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 32784900000 | 25191.967 | 10-MAR-10:00 | 9001.312 | 6750.984 | 4131.484 | 0 | 5308.187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 31626700000 | 26494.25 | 05-APR-14:00 | 9001.312 | 6750.984 | 4131.484 | 0 | 6610.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 37734300000 | 29842.151 | 15-MAY-14:00 | 9001.312 | 6750.984 | 4131.484 | 0 | 9958.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 45280800000 | 35173.697 | 30-JUN-14:00 | 9001.312 | 6750.984 | 4131.484 | 0 | 15289.917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 48859100000 | 36096.849 | 25-JUL-13:30 | 9001.312 | 6750.984 | 4131.484 | 0 | 16213.069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 50293600000 | 36043.154 | 17-AUG-14:00 | 9001.312 | 6750.984 | 4131.484 | 0 | 16159.374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 39319500000 | 32119.366 | 08-SEP-14:00 | 9001.312 | 6750.984 | 4131.484 | 0 | 12235.586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 35081900000 | 29504.753 | 03-OCT-14:00 | 9001.312 | 6750.984 | 4131.484 | 0 | 9620.973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 31528500000 | 26802.494 | 03-NOV-13:00 | 9001.312 | 6750.984 | 4131.484 | 0 | 6918.714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 31241300000 | 19883.78 | 01-DEC-08:09 | 9001.312 | 6750.984 | 4131.484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 443834000000 | [7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 28574500000 | 19883.78 |  | 9001.312 | 6750.984 | 4131.484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 50293600000 | 36096.849 |  | 9001.312 | 6750.984 | 4131.484 | 0 | 16213.069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 9069.31 | 1454.38 | 0 | 10523.69
Cost per Total Building Area ($/m2) | 9.76 | 1.56 | 0 | 11.32
Cost per Net Conditioned Building Area ($/m2) | 9.76 | 1.56 | 0 | 11.32
9-albuquerque
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 531.5 | 571.81 | 571.81
Net Site Energy | 531.5 | 571.81 | 571.81
Total Source Energy | 1568.59 | 1687.56 | 1687.56
Net Source Energy | 1568.59 | 1687.56 | 1687.56
Area (m2)
Total Building Area | 929.5
Net Conditioned Building Area | 929.5
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 77.43 | 0 | 0 | 0 | 0
Cooling | 48.6 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 109.85 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 134.31 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 151.17 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 10.14 | 0 | 0 | 0 | 10.03
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 443.93 | 87.57 | 0 | 0 | 0 | 10.03
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 443.93 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 443.93 | 100
Total On-Site and Utility Electric Sources | 443.93 | 100
Total Electricity End Uses | 443.93 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
FIRST_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 0 | 90 | N
FIRST_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 90 | 90 | E
FIRST_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 180 | 90 | S
FIRST_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 270 | 90 | W
FIRST_FLOOR_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 464.75 | 0 | 180
SECOND_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 0 | 90 | N
SECOND_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 90 | 90 | E
SECOND_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 180 | 90 | S
SECOND_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 270 | 90 | W
WEST-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 36.51 | 270 | 45
EAST-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 36.51 | 90 | 45
SOUTH-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 217.73 | 180 | 18.43
NORTH-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 217.73 | 0 | 18.44
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
FIRST_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_NORTH
FIRST_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_EAST
FIRST_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_SOUTH
FIRST_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_WEST
SECOND_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_NORTH
SECOND_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_EAST
SECOND_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_SOUTH
SECOND_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_2:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 22159.2 | 2.96
PSZ-AC_1:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 33385.41 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC_2:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.34 | 1912.34 | 1 | General
PSZ-AC_1:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 2.02 | 2881.16 | 1 | General
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
Nominal Capacity [W]
PSZ-AC_2:1_UNITARY_PACKAGE_HEATCOIL | 18017.56
PSZ-AC_1:2_UNITARY_PACKAGE_HEATCOIL | 25607.72
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 9988.666 | 16.5188 | 40.3769 | 0 | 0.0002 | 41979.4189 | 4188.0601
February | 8695.0119 | 14.6508 | 36.6161 | 0 | 0.0001 | 38071.2951 | 3672.2684
March | 9497.3487 | 16.3108 | 41.6627 | 0 | 0.0002 | 43320.5221 | 4041.3536
April | 8891.5594 | 15.5319 | 40.4202 | 0 | 0.0002 | 42030.3877 | 3809.2197
May | 10390.9062 | 18.1922 | 47.4596 | 0 | 0.0002 | 49350.4125 | 4455.6022
June | 11312.7775 | 19.8123 | 51.7031 | 0 | 0.0002 | 53763.0112 | 4851.4957
July | 12480.54 | 21.8606 | 57.0576 | 0 | 0.0002 | 59330.8527 | 5352.6078
August | 12161.5867 | 21.301 | 55.5943 | 0 | 0.0002 | 57809.2702 | 5215.7236
September | 10168.4433 | 17.805 | 46.4557 | 0 | 0.0002 | 48306.5085 | 4360.4309
October | 9229.4873 | 16.1077 | 41.8783 | 0 | 0.0002 | 43546.4846 | 3952.5758
November | 9135.0253 | 15.5333 | 39.233 | 0 | 0.0002 | 40793.1087 | 3871.948
December | 9986.2901 | 16.4568 | 40.053 | 0 | 0.0002 | 41642.2152 | 4181.3675
Annual Sum or Average | 121937.6427 | 210.0813 | 538.5105 | 0 | 0.0021 | 559943.4876 | 51952.6534
Minimum of Months | 8695.0119 | 14.6508 | 36.6161 | 0 | 0.0001 | 38071.2951 | 3672.2684
Maximum of Months | 12480.54 | 21.8606 | 57.0576 | 0 | 0.0002 | 59330.8527 | 5352.6078
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 33281800000 | 20545.914 | 27-JAN-14:00 | 9001.312 | 6750.984 | 4793.499 | 0 | 0.119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 30183400000 | 22082.518 | 14-FEB-15:00 | 9001.312 | 6750.984 | 4793.499 | 0 | 1536.722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 34345000000 | 22981.394 | 02-MAR-14:00 | 9001.312 | 6750.984 | 4793.499 | 0 | 2435.598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 33322200000 | 28683.591 | 21-APR-14:00 | 9001.312 | 6750.984 | 4793.499 | 0 | 8137.796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 39125600000 | 30888.28 | 31-MAY-14:00 | 9001.312 | 6750.984 | 4793.499 | 0 | 10342.485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 42624000000 | 33499.221 | 29-JUN-13:00 | 9001.312 | 6750.984 | 4793.499 | 0 | 12953.425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 47038200000 | 34296.49 | 31-JUL-14:00 | 9001.312 | 6750.984 | 4793.499 | 0 | 13750.694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 45831900000 | 34416.369 | 01-AUG-13:00 | 9001.312 | 6750.984 | 4793.499 | 0 | 13870.573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 38298000000 | 30549.094 | 01-SEP-14:50 | 9001.312 | 6750.984 | 4793.499 | 0 | 10003.299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 34524200000 | 28359.141 | 13-OCT-14:00 | 9001.312 | 6750.984 | 4793.499 | 0 | 7813.346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 32341300000 | 20814.705 | 08-NOV-15:50 | 9001.312 | 6750.984 | 4793.499 | 0 | 268.909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 33014400000 | 20545.796 | 01-DEC-08:09 | 9001.312 | 6750.984 | 4793.499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 443930000000 | [7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 30183400000 | 20545.796 |  | 9001.312 | 6750.984 | 4793.499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 47038200000 | 34416.369 |  | 9001.312 | 6750.984 | 4793.499 | 0 | 13870.573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 9203.43 | 599.96 | 0 | 9803.39
Cost per Total Building Area ($/m2) | 9.9 | 0.65 | 0 | 10.55
Cost per Net Conditioned Building Area ($/m2) | 9.9 | 0.65 | 0 | 10.55
10-seattle
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 501.63 | 539.68 | 539.68
Net Site Energy | 501.63 | 539.68 | 539.68
Total Source Energy | 790.39 | 850.33 | 850.33
Net Source Energy | 790.39 | 850.33 | 850.33
Area (m2)
Total Building Area | 929.5
Net Conditioned Building Area | 929.5
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 118.13 | 0 | 0 | 0 | 0
Cooling | 11.69 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 109.85 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 134.31 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 117.39 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 10.27 | 0 | 0 | 0 | 10.03
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 373.23 | 128.4 | 0 | 0 | 0 | 10.03
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 373.23 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 373.23 | 100
Total On-Site and Utility Electric Sources | 373.23 | 100
Total Electricity End Uses | 373.23 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
FIRST_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 0 | 90 | N
FIRST_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 90 | 90 | E
FIRST_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 180 | 90 | S
FIRST_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 270 | 90 | W
FIRST_FLOOR_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 464.75 | 0 | 180
SECOND_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 0 | 90 | N
SECOND_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 90 | 90 | E
SECOND_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 180 | 90 | S
SECOND_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 270 | 90 | W
WEST-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 36.51 | 270 | 45
EAST-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 36.51 | 90 | 45
SOUTH-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 217.73 | 180 | 18.43
NORTH-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 217.73 | 0 | 18.44
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
FIRST_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_NORTH
FIRST_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_EAST
FIRST_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_SOUTH
FIRST_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_WEST
SECOND_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_NORTH
SECOND_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_EAST
SECOND_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_SOUTH
SECOND_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_2:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18088.76 | 3.05
PSZ-AC_1:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 25043.37 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC_2:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.09 | 1561.06 | 1 | General
PSZ-AC_1:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.51 | 2161.24 | 1 | General
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
Nominal Capacity [W]
PSZ-AC_2:1_UNITARY_PACKAGE_HEATCOIL | 16977.45
PSZ-AC_1:2_UNITARY_PACKAGE_HEATCOIL | 23881.94
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 2979.4747 | 3.7265 | 6.5374 | 0 | 0 | 86311.2326 | 1140.6514
February | 2236.2926 | 2.9568 | 5.9275 | 0 | 0 | 78290.8178 | 873.2569
March | 2350.1678 | 3.1915 | 6.7665 | 0 | 0 | 89385.4657 | 926.7341
April | 1822.0479 | 2.6489 | 6.3602 | 0 | 0 | 84044.846 | 737.1731
May | 1622.2659 | 2.5379 | 6.8086 | 0 | 0 | 89992.1334 | 675.5635
June | 1584.3081 | 2.5134 | 6.8719 | 0 | 0 | 90833.1813 | 663.4917
July | 1661.7309 | 2.6387 | 7.2239 | 0 | 0 | 95486.0782 | 696.1869
August | 1723.4802 | 2.7375 | 7.4974 | 0 | 0 | 99100.2759 | 722.1405
September | 1592.5957 | 2.5078 | 6.7883 | 0 | 0 | 89725.8694 | 664.9567
October | 1738.8548 | 2.6037 | 6.5538 | 0 | 0 | 86612.6991 | 711.6334
November | 2368.3366 | 3.1431 | 6.3524 | 0 | 0 | 83904.1251 | 926.0747
December | 2947.6292 | 3.6886 | 6.4799 | 0 | 0 | 85552.5246 | 1128.6674
Annual Sum or Average | 24627.1845 | 34.8944 | 80.1678 | 0 | 0.0003 | 1059239.249 | 9866.5301
Minimum of Months | 1584.3081 | 2.5078 | 5.9275 | 0 | 0 | 78290.8178 | 663.4917
Maximum of Months | 2979.4747 | 3.7265 | 7.4974 | 0 | 0 | 99100.2759 | 1140.6514
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 30412700000 | 19474.599 | 02-JAN-08:09 | 9001.312 | 6750.984 | 3722.303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 27586600000 | 19697.703 | 22-FEB-14:00 | 9001.312 | 6750.984 | 3722.303 | 0 | 223.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 31495900000 | 20904.142 | 29-MAR-14:00 | 9001.312 | 6750.984 | 3722.303 | 0 | 1429.543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 29614100000 | 20609.098 | 19-APR-14:00 | 9001.312 | 6750.984 | 3722.303 | 0 | 1134.498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 31709700000 | 25525.11 | 05-MAY-13:50 | 9001.312 | 6750.984 | 3722.303 | 0 | 6050.511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 32006100000 | 27484.962 | 28-JUN-14:00 | 9001.312 | 6750.984 | 3722.303 | 0 | 8010.363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 33645600000 | 28970.937 | 24-JUL-14:00 | 9001.312 | 6750.984 | 3722.303 | 0 | 9496.338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 34919100000 | 28340.988 | 07-AUG-14:00 | 9001.312 | 6750.984 | 3722.303 | 0 | 8866.388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 31615900000 | 28011.442 | 01-SEP-14:00 | 9001.312 | 6750.984 | 3722.303 | 0 | 8536.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 30518900000 | 21243.947 | 17-OCT-14:00 | 9001.312 | 6750.984 | 3722.303 | 0 | 1769.347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 29564500000 | 19474.599 | 01-NOV-08:09 | 9001.312 | 6750.984 | 3722.303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 30145400000 | 19474.599 | 01-DEC-08:20 | 9001.312 | 6750.984 | 3722.303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 373234000000 | [7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 27586600000 | 19474.599 |  | 9001.312 | 6750.984 | 3722.303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 34919100000 | 28970.937 |  | 9001.312 | 6750.984 | 3722.303 | 0 | 9496.338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 7533.06 | 1087.29 | 0 | 8620.35
Cost per Total Building Area ($/m2) | 8.1 | 1.17 | 0 | 9.27
Cost per Net Conditioned Building Area ($/m2) | 8.1 | 1.17 | 0 | 9.27
11-chicago
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 658.28 | 708.2 | 708.2
Net Site Energy | 658.28 | 708.2 | 708.2
Total Source Energy | 1767.3 | 1901.34 | 1901.34
Net Source Energy | 1767.3 | 1901.34 | 1901.34
Area (m2)
Total Building Area | 929.5
Net Conditioned Building Area | 929.5
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 220.7 | 0 | 0 | 0 | 0
Cooling | 53.75 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 109.85 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 134.31 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 129.34 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 10.33 | 0 | 0 | 0 | 10.03
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 427.25 | 231.03 | 0 | 0 | 0 | 10.03
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 427.25 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 427.25 | 100
Total On-Site and Utility Electric Sources | 427.25 | 100
Total Electricity End Uses | 427.25 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
FIRST_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 0 | 90 | N
FIRST_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 90 | 90 | E
FIRST_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 180 | 90 | S
FIRST_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 270 | 90 | W
FIRST_FLOOR_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 464.75 | 0 | 180
SECOND_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 0 | 90 | N
SECOND_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 90 | 90 | E
SECOND_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 180 | 90 | S
SECOND_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 270 | 90 | W
WEST-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 36.51 | 270 | 45
EAST-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 36.51 | 90 | 45
SOUTH-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 217.73 | 180 | 18.43
NORTH-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 217.73 | 0 | 18.44
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
FIRST_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_NORTH
FIRST_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_EAST
FIRST_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_SOUTH
FIRST_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_WEST
SECOND_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_NORTH
SECOND_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_EAST
SECOND_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_SOUTH
SECOND_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_2:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 24433.89 | 2.96
PSZ-AC_1:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 31547.92 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC_2:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.16 | 1663.84 | 1 | General
PSZ-AC_1:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.71 | 2437.42 | 1 | General
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
Nominal Capacity [W]
PSZ-AC_2:1_UNITARY_PACKAGE_HEATCOIL | 27734.52
PSZ-AC_1:2_UNITARY_PACKAGE_HEATCOIL | 39095.64
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 13900.5039 | 22.4247 | 58.8489 | 0 | 0.0002 | 13543.9359 | 5748.6531
February | 12035.0801 | 19.8182 | 53.3664 | 0 | 0.0002 | 12282.8232 | 5015.7093
March | 12702.7386 | 21.671 | 60.8436 | 0 | 0.0002 | 14005.0037 | 5365.9987
April | 10961.2632 | 19.5782 | 57.7667 | 0 | 0.0002 | 13298.0461 | 4714.3115
May | 12544.9577 | 22.778 | 68.3373 | 0 | 0.0002 | 15731.9353 | 5430.918
June | 14730.6873 | 26.7828 | 80.4606 | 0 | 0.0002 | 18522.8879 | 6380.6135
July | 15922.8081 | 28.9534 | 86.9911 | 0 | 0.0003 | 20026.2901 | 6897.2856
August | 15659.0142 | 28.4726 | 85.543 | 0 | 0.0003 | 19692.9034 | 6782.9065
September | 12852.9883 | 23.3646 | 70.1792 | 0 | 0.0002 | 16155.9987 | 5566.8844
October | 11505.6933 | 20.6985 | 61.5219 | 0 | 0.0002 | 14162.7136 | 4962.5964
November | 11788.1385 | 20.3105 | 57.6606 | 0 | 0.0002 | 13272.6146 | 4998.7472
December | 13422.6087 | 21.9074 | 58.3464 | 0 | 0.0002 | 13428.7247 | 5575.2709
Annual Sum or Average | 158026.4818 | 276.7599 | 799.8657 | 0 | 0.0024 | 184123.8772 | 67439.8951
Minimum of Months | 10961.2632 | 19.5782 | 53.3664 | 0 | 0.0002 | 12282.8232 | 4714.3115
Maximum of Months | 15922.8081 | 28.9534 | 86.9911 | 0 | 0.0003 | 20026.2901 | 6897.2856
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 31427700000 | 19853.552 | 02-JAN-08:09 | 9001.312 | 6750.984 | 4101.255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 28501400000 | 19853.552 | 01-FEB-08:09 | 9001.312 | 6750.984 | 4101.255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 32497600000 | 22502.26 | 31-MAR-14:00 | 9001.312 | 6750.984 | 4101.255 | 0 | 2648.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 30857100000 | 24098.816 | 28-APR-14:39 | 9001.312 | 6750.984 | 4101.255 | 0 | 4245.265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 36504800000 | 29527.384 | 05-MAY-13:00 | 9001.312 | 6750.984 | 4101.255 | 0 | 9673.832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 42981000000 | 34338.025 | 08-JUN-12:00 | 9001.312 | 6750.984 | 4101.255 | 0 | 14484.473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 46469500000 | 34863.75 | 13-JUL-14:00 | 9001.312 | 6750.984 | 4101.255 | 0 | 15010.198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 45695900000 | 34388.036 | 04-AUG-14:00 | 9001.312 | 6750.984 | 4101.255 | 0 | 14534.484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 37488800000 | 30593.855 | 06-SEP-12:39 | 9001.312 | 6750.984 | 4101.255 | 0 | 10740.304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 32863500000 | 27301.922 | 31-OCT-13:30 | 9001.312 | 6750.984 | 4101.255 | 0 | 7448.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 30798100000 | 26663.459 | 02-NOV-14:39 | 9001.312 | 6750.984 | 4101.255 | 0 | 6809.907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 31160300000 | 19853.552 | 01-DEC-08:09 | 9001.312 | 6750.984 | 4101.255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 427246000000 | [7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 28501400000 | 19853.552 |  | 9001.312 | 6750.984 | 4101.255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 46469500000 | 34863.75 |  | 9001.312 | 6750.984 | 4101.255 | 0 | 15010.198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 6804.59 | 1907.46 | 0 | 8712.05
Cost per Total Building Area ($/m2) | 7.32 | 2.05 | 0 | 9.37
Cost per Net Conditioned Building Area ($/m2) | 7.32 | 2.05 | 0 | 9.37
12-boulder
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 572.3 | 615.71 | 615.71
Net Site Energy | 572.3 | 615.71 | 615.71
Total Source Energy | 1557.8 | 1675.95 | 1675.95
Net Source Energy | 1557.8 | 1675.95 | 1675.95
Area (m2)
Total Building Area | 929.5
Net Conditioned Building Area | 929.5
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 142.91 | 0 | 0 | 0 | 0
Cooling | 28.34 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 109.85 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 134.31 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 146.57 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 10.32 | 0 | 0 | 0 | 10.03
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 419.07 | 153.23 | 0 | 0 | 0 | 10.03
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 419.07 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 419.07 | 100
Total On-Site and Utility Electric Sources | 419.07 | 100
Total Electricity End Uses | 419.07 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
FIRST_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 0 | 90 | N
FIRST_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 90 | 90 | E
FIRST_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 180 | 90 | S
FIRST_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 270 | 90 | W
FIRST_FLOOR_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 464.75 | 0 | 180
SECOND_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 0 | 90 | N
SECOND_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 90 | 90 | E
SECOND_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 180 | 90 | S
SECOND_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 270 | 90 | W
WEST-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 36.51 | 270 | 45
EAST-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 36.51 | 90 | 45
SOUTH-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 217.73 | 180 | 18.43
NORTH-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 217.73 | 0 | 18.44
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
FIRST_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_NORTH
FIRST_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_EAST
FIRST_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_SOUTH
FIRST_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_WEST
SECOND_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_NORTH
SECOND_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_EAST
SECOND_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_SOUTH
SECOND_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_2:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 21802.09 | 2.96
PSZ-AC_1:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 32051.66 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC_2:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.32 | 1881.52 | 1 | General
PSZ-AC_1:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.94 | 2766.06 | 1 | General
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
Nominal Capacity [W]
PSZ-AC_2:1_UNITARY_PACKAGE_HEATCOIL | 24407.5
PSZ-AC_1:2_UNITARY_PACKAGE_HEATCOIL | 35119.42
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 10580.6263 | 16.9688 | 39.9064 | 0 | 0.0002 | 41486.4464 | 4384.3658
February | 9230.2725 | 15.056 | 36.1823 | 0 | 0.0001 | 37616.7726 | 3849.6187
March | 9917.7032 | 16.6158 | 41.25 | 0 | 0.0002 | 42888.6968 | 4179.328
April | 8877.0213 | 15.3181 | 39.3346 | 0 | 0.0002 | 40900.2756 | 3784.514
May | 9397.8634 | 16.4003 | 42.6355 | 0 | 0.0002 | 44333.7759 | 4024.5595
June | 9926.5665 | 17.3768 | 45.3253 | 0 | 0.0002 | 47131.0425 | 4256.2497
July | 11200.3163 | 19.614 | 51.1817 | 0 | 0.0002 | 53220.8836 | 4803.1332
August | 11034.9252 | 19.3233 | 50.4205 | 0 | 0.0002 | 52429.2786 | 4732.1076
September | 9416.3773 | 16.4782 | 42.9661 | 0 | 0.0002 | 44677.8444 | 4036.9573
October | 9168.2285 | 15.8549 | 40.8104 | 0 | 0.0002 | 42435.0914 | 3912.0251
November | 9452.4419 | 15.7369 | 38.7769 | 0 | 0.0002 | 40316.6634 | 3973.5171
December | 10582.9276 | 16.911 | 39.5825 | 0 | 0.0002 | 41149.2429 | 4379.2921
Annual Sum or Average | 118785.27 | 201.6541 | 508.3722 | 0 | 0.002 | 528586.0141 | 50315.668
Minimum of Months | 8877.0213 | 15.056 | 36.1823 | 0 | 0.0001 | 37616.7726 | 3784.514
Maximum of Months | 11200.3163 | 19.614 | 51.1817 | 0 | 0.0002 | 53220.8836 | 4803.1332
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 32891000000 | 20399.888 | 24-JAN-15:30 | 9001.312 | 6750.984 | 4647.579 | 0 | 0.013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 29823000000 | 20399.875 | 01-FEB-08:09 | 9001.312 | 6750.984 | 4647.579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 34002700000 | 24089.791 | 30-MAR-14:00 | 9001.312 | 6750.984 | 4647.579 | 0 | 3689.916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 32426200000 | 27258.882 | 26-APR-14:00 | 9001.312 | 6750.984 | 4647.579 | 0 | 6859.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 35148400000 | 29077.04 | 23-MAY-14:00 | 9001.312 | 6750.984 | 4647.579 | 0 | 8677.165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 37366100000 | 32058.898 | 28-JUN-13:39 | 9001.312 | 6750.984 | 4647.579 | 0 | 11659.023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 42194200000 | 32973.506 | 18-JUL-13:00 | 9001.312 | 6750.984 | 4647.579 | 0 | 12573.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 41566600000 | 33331.933 | 30-AUG-13:00 | 9001.312 | 6750.984 | 4647.579 | 0 | 12932.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 35421100000 | 30305.623 | 06-SEP-14:50 | 9001.312 | 6750.984 | 4647.579 | 0 | 9905.748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 33643100000 | 28288.91 | 05-OCT-14:00 | 9001.312 | 6750.984 | 4647.579 | 0 | 7889.035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 31963500000 | 21069.104 | 10-NOV-13:00 | 9001.312 | 6750.984 | 4647.579 | 0 | 669.229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 32623600000 | 20399.875 | 01-DEC-08:09 | 9001.312 | 6750.984 | 4647.579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 419069000000 | [7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 29823000000 | 20399.875 |  | 9001.312 | 6750.984 | 4647.579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 42194200000 | 33331.933 |  | 9001.312 | 6750.984 | 4647.579 | 0 | 12932.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 8692.68 | 1051.47 | 0 | 9744.15
Cost per Total Building Area ($/m2) | 9.35 | 1.13 | 0 | 10.48
Cost per Net Conditioned Building Area ($/m2) | 9.35 | 1.13 | 0 | 10.48
13-minneapolis
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 745.84 | 802.41 | 802.41
Net Site Energy | 745.84 | 802.41 | 802.41
Total Source Energy | 1802.5 | 1939.21 | 1939.21
Net Source Energy | 1802.5 | 1939.21 | 1939.21
Area (m2)
Total Building Area | 929.5
Net Conditioned Building Area | 929.5
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 314.04 | 0 | 0 | 0 | 0
Cooling | 48.24 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 109.85 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 134.31 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 128.94 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 10.46 | 0 | 0 | 0 | 10.03
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 421.34 | 324.5 | 0 | 0 | 0 | 10.03
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 421.34 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 421.34 | 100
Total On-Site and Utility Electric Sources | 421.34 | 100
Total Electricity End Uses | 421.34 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
FIRST_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 0 | 90 | N
FIRST_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 90 | 90 | E
FIRST_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 180 | 90 | S
FIRST_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 270 | 90 | W
FIRST_FLOOR_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 464.75 | 0 | 180
SECOND_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 0 | 90 | N
SECOND_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 90 | 90 | E
SECOND_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 180 | 90 | S
SECOND_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 270 | 90 | W
WEST-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 36.51 | 270 | 45
EAST-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 36.51 | 90 | 45
SOUTH-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 217.73 | 180 | 18.43
NORTH-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 217.73 | 0 | 18.44
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
FIRST_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_NORTH
FIRST_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_EAST
FIRST_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_SOUTH
FIRST_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_WEST
SECOND_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_NORTH
SECOND_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_EAST
SECOND_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_SOUTH
SECOND_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_2:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 23322.06 | 2.96
PSZ-AC_1:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 30082.73 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC_2:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.16 | 1663.49 | 1 | General
PSZ-AC_1:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.7 | 2425.09 | 1 | General
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
Nominal Capacity [W]
PSZ-AC_2:1_UNITARY_PACKAGE_HEATCOIL | 31331.82
PSZ-AC_1:2_UNITARY_PACKAGE_HEATCOIL | 44251.94
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 11523.3459 | 16.7717 | 20.6056 | 0 | 0.0002 | 13529.3127 | 4591.5812
February | 9556.9506 | 14.3989 | 18.6825 | 0 | 0.0001 | 12269.6152 | 3854.819
March | 8957.3782 | 14.6521 | 21.2763 | 0 | 0.0002 | 13979.6274 | 3723.5306
April | 7249.5095 | 12.8028 | 20.2945 | 0 | 0.0001 | 13338.9031 | 3103.8435
May | 8284.1695 | 15.0489 | 24.5548 | 0 | 0.0002 | 16140.7172 | 3586.865
June | 9288.7303 | 16.9098 | 27.6498 | 0 | 0.0002 | 18175.3139 | 4025.2654
July | 9851.3846 | 17.936 | 29.3307 | 0 | 0.0002 | 19280.2671 | 4269.2698
August | 9955.6809 | 18.1258 | 29.641 | 0 | 0.0002 | 19484.2467 | 4314.4622
September | 7731.7636 | 14.0674 | 22.989 | 0 | 0.0002 | 15111.5904 | 3349.7882
October | 7463.3856 | 13.1633 | 20.8373 | 0 | 0.0002 | 13695.5946 | 3193.7713
November | 8662.3563 | 14.0018 | 20.0292 | 0 | 0.0002 | 13159.429 | 3584.8532
December | 10739.4923 | 16.0063 | 20.4266 | 0 | 0.0002 | 13414.1015 | 4315.1396
Annual Sum or Average | 109264.1474 | 183.8848 | 276.3173 | 0 | 0.002 | 181578.7188 | 45913.189
Minimum of Months | 7249.5095 | 12.8028 | 18.6825 | 0 | 0.0001 | 12269.6152 | 3103.8435
Maximum of Months | 11523.3459 | 18.1258 | 29.641 | 0 | 0.0002 | 19484.2467 | 4591.5812
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 31393800000 | 19840.883 | 03-JAN-11:09 | 9001.312 | 6750.984 | 4088.587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 28470700000 | 19840.883 | 06-FEB-11:50 | 9001.312 | 6750.984 | 4088.587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 32438700000 | 20398.739 | 23-MAR-14:00 | 9001.312 | 6750.984 | 4088.587 | 0 | 557.856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 30951900000 | 23695.288 | 27-APR-14:00 | 9001.312 | 6750.984 | 4088.587 | 0 | 3854.405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 37453300000 | 29981.425 | 31-MAY-11:00 | 9001.312 | 6750.984 | 4088.587 | 0 | 10140.542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 42174400000 | 33841.235 | 29-JUN-14:00 | 9001.312 | 6750.984 | 4088.587 | 0 | 14000.352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 44738400000 | 33344.462 | 13-JUL-14:00 | 9001.312 | 6750.984 | 4088.587 | 0 | 13503.579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 45211700000 | 33116.945 | 25-AUG-14:00 | 9001.312 | 6750.984 | 4088.587 | 0 | 13276.062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 35065300000 | 30530.519 | 14-SEP-14:00 | 9001.312 | 6750.984 | 4088.587 | 0 | 10689.636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 31779600000 | 23582.427 | 06-OCT-14:00 | 9001.312 | 6750.984 | 4088.587 | 0 | 3741.544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 30535500000 | 21549.712 | 02-NOV-15:09 | 9001.312 | 6750.984 | 4088.587 | 0 | 1708.829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 31126400000 | 19840.883 | 05-DEC-13:50 | 9001.312 | 6750.984 | 4088.587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 421340000000 | [7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 28470700000 | 19840.883 |  | 9001.312 | 6750.984 | 4088.587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 45211700000 | 33841.235 |  | 9001.312 | 6750.984 | 4088.587 | 0 | 14000.352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 8743.71 | 2560.65 | 0 | 11304.36
Cost per Total Building Area ($/m2) | 9.41 | 2.75 | 0 | 12.16
Cost per Net Conditioned Building Area ($/m2) | 9.41 | 2.75 | 0 | 12.16
14-helena
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 652.44 | 701.92 | 701.92
Net Site Energy | 652.44 | 701.92 | 701.92
Total Source Energy | 1660.44 | 1786.37 | 1786.37
Net Source Energy | 1660.44 | 1786.37 | 1786.37
Area (m2)
Total Building Area | 929.5
Net Conditioned Building Area | 929.5
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 244.32 | 0 | 0 | 0 | 0
Cooling | 17.18 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 109.85 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 134.31 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 136.3 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 10.48 | 0 | 0 | 0 | 10.03
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 397.64 | 254.8 | 0 | 0 | 0 | 10.03
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 397.64 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 397.64 | 100
Total On-Site and Utility Electric Sources | 397.64 | 100
Total Electricity End Uses | 397.64 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
FIRST_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 0 | 90 | N
FIRST_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 90 | 90 | E
FIRST_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 180 | 90 | S
FIRST_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 270 | 90 | W
FIRST_FLOOR_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 464.75 | 0 | 180
SECOND_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 0 | 90 | N
SECOND_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 90 | 90 | E
SECOND_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 180 | 90 | S
SECOND_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 270 | 90 | W
WEST-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 36.51 | 270 | 45
EAST-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 36.51 | 90 | 45
SOUTH-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 217.73 | 180 | 18.43
NORTH-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 217.73 | 0 | 18.44
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
FIRST_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_NORTH
FIRST_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_EAST
FIRST_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_SOUTH
FIRST_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 3.24 | 0.39 | 0.495 | No | FIRST_FLOOR_WALL_WEST
SECOND_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_NORTH
SECOND_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_EAST
SECOND_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_SOUTH
SECOND_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 3.24 | 0.39 | 0.495 | No | SECOND_FLOOR_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_2:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20714.27 | 2.96
PSZ-AC_1:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 29367.49 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC_2:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.25 | 1787.64 | 1 | General
PSZ-AC_1:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.77 | 2534.41 | 1 | General
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
Nominal Capacity [W]
PSZ-AC_2:1_UNITARY_PACKAGE_HEATCOIL | 29866.9
PSZ-AC_1:2_UNITARY_PACKAGE_HEATCOIL | 42805.11
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 10918.2718 | 16.4683 | 23.7658 | 0 | 0.0002 | 563394.8123 | 4412.7282
February | 9288.4553 | 14.3778 | 21.5482 | 0 | 0.0002 | 510897.4878 | 3789.5697
March | 9160.8299 | 15.0873 | 24.5323 | 0 | 0.0002 | 581823.479 | 3825.1761
April | 7970.6726 | 13.6051 | 23.0736 | 0 | 0.0002 | 547305.323 | 3374.4148
May | 7980.3829 | 13.9952 | 24.4525 | 0 | 0.0002 | 580071.5384 | 3414.6323
June | 8526.0238 | 15.0802 | 26.588 | 0 | 0.0002 | 630747.6705 | 3660.4902
July | 9111.2924 | 16.1342 | 28.4808 | 0 | 0.0002 | 675654.7902 | 3913.5748
August | 8926.5365 | 15.8062 | 27.9004 | 0 | 0.0002 | 661885.6447 | 3834.1396
September | 7783.4944 | 13.7503 | 24.2124 | 0 | 0.0002 | 574390.7929 | 3340.0958
October | 8111.4221 | 13.9311 | 23.7912 | 0 | 0.0002 | 564340.0998 | 3442.292
November | 8878.3556 | 14.4319 | 23.0882 | 0 | 0.0002 | 547542.8925 | 3688.847
December | 10502.4309 | 16.0361 | 23.5657 | 0 | 0.0002 | 558690.8227 | 4263.5072
Annual Sum or Average | 107158.1683 | 178.7036 | 294.9992 | 0 | 0.0021 | 6996745.3538 | 44959.4674
Minimum of Months | 7783.4944 | 13.6051 | 21.5482 | 0 | 0.0002 | 510897.4878 | 3340.0958
Maximum of Months | 10918.2718 | 16.4683 | 28.4808 | 0 | 0.0002 | 675654.7902 | 4412.7282
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 32019100000 | 20074.352 | 02-JAN-08:09 | 9001.312 | 6750.984 | 4322.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 29035500000 | 20074.352 | 01-FEB-08:09 | 9001.312 | 6750.984 | 4322.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 33066400000 | 20824.424 | 30-MAR-14:00 | 9001.312 | 6750.984 | 4322.055 | 0 | 750.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 31104700000 | 20074.437 | 14-APR-14:50 | 9001.312 | 6750.984 | 4322.055 | 0 | 0.085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 32966900000 | 25868.825 | 17-MAY-14:00 | 9001.312 | 6750.984 | 4322.055 | 0 | 5794.473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 35846900000 | 32248.018 | 30-JUN-14:00 | 9001.312 | 6750.984 | 4322.055 | 0 | 12173.666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 38399100000 | 31708.553 | 21-JUL-14:00 | 9001.312 | 6750.984 | 4322.055 | 0 | 11634.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 37616500000 | 30490.38 | 09-AUG-14:00 | 9001.312 | 6750.984 | 4322.055 | 0 | 10416.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 32644000000 | 28155.457 | 12-SEP-13:00 | 9001.312 | 6750.984 | 4322.055 | 0 | 8081.105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 32072800000 | 23952.625 | 06-OCT-14:00 | 9001.312 | 6750.984 | 4322.055 | 0 | 3878.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 31118200000 | 20074.352 | 01-NOV-08:09 | 9001.312 | 6750.984 | 4322.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 31751700000 | 20074.352 | 01-DEC-08:09 | 9001.312 | 6750.984 | 4322.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 397642000000 | [7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 29035500000 | 20074.352 |  | 9001.312 | 6750.984 | 4322.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 38399100000 | 32248.018 |  | 9001.312 | 6750.984 | 4322.055 | 0 | 12173.666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 8150.47 | 2029.83 | 0 | 10180.3
Cost per Total Building Area ($/m2) | 8.77 | 2.18 | 0 | 10.95
Cost per Net Conditioned Building Area ($/m2) | 8.77 | 2.18 | 0 | 10.95
15-duluth
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 794.51 | 854.77 | 854.77
Net Site Energy | 794.51 | 854.77 | 854.77
Total Source Energy | 1783.34 | 1918.6 | 1918.6
Net Source Energy | 1783.34 | 1918.6 | 1918.6
Area (m2)
Total Building Area | 929.5
Net Conditioned Building Area | 929.5
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 393.33 | 0 | 0 | 0 | 0
Cooling | 22.96 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 109.85 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 134.31 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 123.39 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 10.68 | 0 | 0 | 0 | 10.03
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 390.51 | 404 | 0 | 0 | 0 | 10.03
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 390.51 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 390.51 | 100
Total On-Site and Utility Electric Sources | 390.51 | 100
Total Electricity End Uses | 390.51 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
FIRST_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 0 | 90 | N
FIRST_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 90 | 90 | E
FIRST_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 180 | 90 | S
FIRST_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 270 | 90 | W
FIRST_FLOOR_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 464.75 | 0 | 180
SECOND_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 0 | 90 | N
SECOND_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 90 | 90 | E
SECOND_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 180 | 90 | S
SECOND_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 270 | 90 | W
WEST-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 36.51 | 270 | 45
EAST-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 36.51 | 90 | 45
SOUTH-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 217.73 | 180 | 18.43
NORTH-ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 217.73 | 0 | 18.44
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
FIRST_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 3.24 | 0.49 | 0.49 | No | FIRST_FLOOR_WALL_NORTH
FIRST_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 3.24 | 0.49 | 0.49 | No | FIRST_FLOOR_WALL_EAST
FIRST_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 3.24 | 0.49 | 0.49 | No | FIRST_FLOOR_WALL_SOUTH
FIRST_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 3.24 | 0.49 | 0.49 | No | FIRST_FLOOR_WALL_WEST
SECOND_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 3.24 | 0.49 | 0.49 | No | SECOND_FLOOR_WALL_NORTH
SECOND_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 3.24 | 0.49 | 0.49 | No | SECOND_FLOOR_WALL_EAST
SECOND_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 3.24 | 0.49 | 0.49 | No | SECOND_FLOOR_WALL_SOUTH
SECOND_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 3.24 | 0.49 | 0.49 | No | SECOND_FLOOR_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_2:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20198.92 | 2.96
PSZ-AC_1:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 26617.96 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC_2:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.13 | 1619.86 | 1 | General
PSZ-AC_1:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.6 | 2292.8 | 1 | General
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
Nominal Capacity [W]
PSZ-AC_2:1_UNITARY_PACKAGE_HEATCOIL | 32924.2
PSZ-AC_1:2_UNITARY_PACKAGE_HEATCOIL | 46664.05
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 11598.9594 | 16.7456 | 20.2976 | 0 | 0.0002 | 13326.2389 | 4608.6991
February | 10011.5116 | 14.7261 | 18.4062 | 0 | 0.0001 | 12086.1936 | 4003.9733
March | 9754.4208 | 15.2805 | 20.9703 | 0 | 0.0002 | 13775.4463 | 3990.2983
April | 7761.2291 | 13.0858 | 19.7059 | 0 | 0.0001 | 12949.6186 | 3263.6038
May | 7351.3045 | 13.1384 | 21.087 | 0 | 0.0002 | 13860.3986 | 3162.3253
June | 7896.5485 | 14.3673 | 23.4794 | 0 | 0.0002 | 15433.9474 | 3421.1942
July | 8702.9805 | 15.8393 | 25.8927 | 0 | 0.0002 | 17020.318 | 3771.0363
August | 8520.7643 | 15.5026 | 25.334 | 0 | 0.0002 | 16653.0407 | 3691.5945
September | 7120.0747 | 12.8295 | 20.7634 | 0 | 0.0002 | 13648.0991 | 3072.8281
October | 7678.2292 | 13.2083 | 20.3496 | 0 | 0.0002 | 13373.7604 | 3253.7848
November | 9119.0554 | 14.3202 | 19.7184 | 0 | 0.0001 | 12953.2338 | 3733.7322
December | 11132.648 | 16.2685 | 20.1202 | 0 | 0.0002 | 13211.0277 | 4442.1644
Annual Sum or Average | 106647.7261 | 175.3122 | 256.1249 | 0 | 0.0019 | 168291.3229 | 44415.2342
Minimum of Months | 7120.0747 | 12.8295 | 18.4062 | 0 | 0.0001 | 12086.1936 | 3072.8281
Maximum of Months | 11598.9594 | 16.7456 | 25.8927 | 0 | 0.0002 | 17020.318 | 4608.6991
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 30922500000 | 19664.951 | 02-JAN-08:09 | 9001.312 | 6750.984 | 3912.654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 28045100000 | 19664.951 | 01-FEB-08:09 | 9001.312 | 6750.984 | 3912.654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 31964900000 | 19664.951 | 01-MAR-08:09 | 9001.312 | 6750.984 | 3912.654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 30048600000 | 20438.613 | 04-APR-14:00 | 9001.312 | 6750.984 | 3912.654 | 0 | 773.662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 32162000000 | 25476.692 | 31-MAY-14:00 | 9001.312 | 6750.984 | 3912.654 | 0 | 5811.741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 35813300000 | 30287.922 | 14-JUN-14:00 | 9001.312 | 6750.984 | 3912.654 | 0 | 10622.972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 39494400000 | 31970.298 | 06-JUL-14:00 | 9001.312 | 6750.984 | 3912.654 | 0 | 12305.348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 38642100000 | 30879.473 | 11-AUG-14:00 | 9001.312 | 6750.984 | 3912.654 | 0 | 11214.522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 31669400000 | 28347.52 | 07-SEP-14:00 | 9001.312 | 6750.984 | 3912.654 | 0 | 8682.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 31032800000 | 21746.331 | 06-OCT-14:00 | 9001.312 | 6750.984 | 3912.654 | 0 | 2081.381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 30057000000 | 19664.951 | 01-NOV-08:09 | 9001.312 | 6750.984 | 3912.654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 30655200000 | 19664.951 | 01-DEC-08:09 | 9001.312 | 6750.984 | 3912.654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 390507000000 | [7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 28045100000 | 19664.951 |  | 9001.312 | 6750.984 | 3912.654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 39494400000 | 31970.298 |  | 9001.312 | 6750.984 | 3912.654 | 0 | 12305.348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 8082.78 | 3174.19 | 0 | 11256.98
Cost per Total Building Area ($/m2) | 8.7 | 3.41 | 0 | 12.11
Cost per Net Conditioned Building Area ($/m2) | 8.7 | 3.41 | 0 | 12.11
16-fairbanks
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 1054.36 | 1134.32 | 1134.32
Net Site Energy | 1054.36 | 1134.32 | 1134.32
Total Source Energy | 2136.06 | 2298.07 | 2298.07
Net Source Energy | 2136.06 | 2298.07 | 2298.07
Area (m2)
Total Building Area | 929.5
Net Conditioned Building Area | 929.5
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 646.36 | 0 | 0 | 0 | 0
Cooling | 16.38 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 109.85 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 134.31 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 136.52 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 10.94 | 0 | 0 | 0 | 10.03
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 397.06 | 657.3 | 0 | 0 | 0 | 10.03
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 397.06 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 397.06 | 100
Total On-Site and Utility Electric Sources | 397.06 | 100
Total Electricity End Uses | 397.06 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
FIRST_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.313 | 0.33 | 80.5 | 0 | 90 | N
FIRST_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.313 | 0.33 | 53.67 | 90 | 90 | E
FIRST_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.313 | 0.33 | 80.5 | 180 | 90 | S
FIRST_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.313 | 0.33 | 53.67 | 270 | 90 | W
FIRST_FLOOR_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 464.75 | 0 | 180
SECOND_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.313 | 0.33 | 80.5 | 0 | 90 | N
SECOND_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.313 | 0.33 | 53.67 | 90 | 90 | E
SECOND_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.313 | 0.33 | 80.5 | 180 | 90 | S
SECOND_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.313 | 0.33 | 53.67 | 270 | 90 | W
WEST-ROOF | ROOFS | 0.3 | 0.273 | 0.29 | 36.51 | 270 | 45
EAST-ROOF | ROOFS | 0.3 | 0.273 | 0.29 | 36.51 | 90 | 45
SOUTH-ROOF | ROOFS | 0.3 | 0.273 | 0.29 | 217.73 | 180 | 18.43
NORTH-ROOF | ROOFS | 0.3 | 0.273 | 0.29 | 217.73 | 0 | 18.44
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
FIRST_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 2.62 | 0.49 | 0.49 | No | FIRST_FLOOR_WALL_NORTH
FIRST_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 2.62 | 0.49 | 0.49 | No | FIRST_FLOOR_WALL_EAST
FIRST_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 2.62 | 0.49 | 0.49 | No | FIRST_FLOOR_WALL_SOUTH
FIRST_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 2.62 | 0.49 | 0.49 | No | FIRST_FLOOR_WALL_WEST
SECOND_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 2.62 | 0.49 | 0.49 | No | SECOND_FLOOR_WALL_NORTH
SECOND_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 2.62 | 0.49 | 0.49 | No | SECOND_FLOOR_WALL_EAST
SECOND_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 2.62 | 0.49 | 0.49 | No | SECOND_FLOOR_WALL_SOUTH
SECOND_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 2.62 | 0.49 | 0.49 | No | SECOND_FLOOR_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_2:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18919.65 | 2.96
PSZ-AC_1:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 31242.78 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC_2:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.14 | 1632.77 | 1 | General
PSZ-AC_1:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.89 | 2696.25 | 1 | General
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
Nominal Capacity [W]
PSZ-AC_2:1_UNITARY_PACKAGE_HEATCOIL | 41123.39
PSZ-AC_1:2_UNITARY_PACKAGE_HEATCOIL | 57966
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 13394.2606 | 14.324 | 45.338 | 0 | 0.0002 | 9092.3052 | 4968.9658
February | 11622.713 | 12.5141 | 41.1106 | 0 | 0.0002 | 8245.0621 | 4324.7746
March | 10701.585 | 11.9498 | 46.797 | 0 | 0.0002 | 9388.1247 | 4047.8175
April | 7911.3116 | 9.2844 | 44.0169 | 0 | 0.0002 | 8832.6332 | 3061.7121
May | 6793.8421 | 8.4406 | 47.5818 | 0 | 0.0002 | 9549.7977 | 2701.2006
June | 7377.1658 | 9.2236 | 52.8877 | 0 | 0.0002 | 10614.8799 | 2942.1046
July | 7548.9645 | 9.4408 | 54.1677 | 0 | 0.0002 | 10871.8059 | 3010.9763
August | 7174.7745 | 8.9666 | 51.3536 | 0 | 0.0002 | 10306.9821 | 2860.7776
September | 6646.1313 | 8.1371 | 44.0375 | 0 | 0.0001 | 8838.0732 | 2624.0105
October | 8869.0745 | 10.2158 | 45.3147 | 0 | 0.0002 | 9092.3052 | 3402.7203
November | 11292.1799 | 12.3547 | 44.0533 | 0 | 0.0002 | 8836.4584 | 4232.0295
December | 12657.1708 | 13.6368 | 44.9564 | 0 | 0.0002 | 9016.4344 | 4711.0677
Annual Sum or Average | 111989.1735 | 128.4885 | 561.6152 | 0 | 0.002 | 112684.8621 | 42888.1572
Minimum of Months | 6646.1313 | 8.1371 | 41.1106 | 0 | 0.0001 | 8245.0621 | 2624.0105
Maximum of Months | 13394.2606 | 14.324 | 54.1677 | 0 | 0.0002 | 10871.8059 | 4968.9658
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 32037700000 | 20081.314 | 02-JAN-08:09 | 9001.312 | 6750.984 | 4329.018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 29052400000 | 20081.314 | 01-FEB-08:09 | 9001.312 | 6750.984 | 4329.018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 33080100000 | 20081.314 | 01-MAR-08:09 | 9001.312 | 6750.984 | 4329.018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 31122700000 | 20120.707 | 25-APR-14:00 | 9001.312 | 6750.984 | 4329.018 | 0 | 39.393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 33649700000 | 25840.959 | 24-MAY-14:00 | 9001.312 | 6750.984 | 4329.018 | 0 | 5759.645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 37402700000 | 28498.463 | 21-JUN-14:00 | 9001.312 | 6750.984 | 4329.018 | 0 | 8417.149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 38308000000 | 28161.111 | 11-JUL-14:00 | 9001.312 | 6750.984 | 4329.018 | 0 | 8079.797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 36317800000 | 28164.935 | 15-AUG-14:30 | 9001.312 | 6750.984 | 4329.018 | 0 | 8083.621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 31141900000 | 21298.975 | 01-SEP-14:00 | 9001.312 | 6750.984 | 4329.018 | 0 | 1217.661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 32037700000 | 20081.314 | 02-OCT-07:10 | 9001.312 | 6750.984 | 4329.018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 31136200000 | 20081.314 | 01-NOV-08:09 | 9001.312 | 6750.984 | 4329.018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 31770400000 | 20081.314 | 01-DEC-08:09 | 9001.312 | 6750.984 | 4329.018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 397057000000 | [7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 29052400000 | 20081.314 |  | 9001.312 | 6750.984 | 4329.018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 38308000000 | 28498.463 |  | 9001.312 | 6750.984 | 4329.018 | 0 | 8417.149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 10795.82 | 2699.8 | 0 | 13495.62
Cost per Total Building Area ($/m2) | 11.61 | 2.9 | 0 | 14.52
Cost per Net Conditioned Building Area ($/m2) | 11.61 | 2.9 | 0 | 14.52

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago-O'Hare | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7A | 8A
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fabric
Exterior walls
| Construction Type | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed
| R-value (m2·K / W) | 1.4205 | 1.4205 | 1.4205 | 2.0964 | 2.0964 | 2.0964 | 2.0964 | 2.7473 | 2.7473 | 2.7473 | 2.7473 | 2.7473 | 2.7473 | 2.7473 | 2.7473 | 3.1949
Roof
| Construction Type | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic
| R-value (m2·K / W) | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 3.663
Window
| U-Factor (W / m2·K) | 6.88 | 6.88 | 6.88 | 3.24 | 3.24 | 3.24 | 6.88 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 2.62
| SHGC | 0.25 | 0.25 | 0.25 | 0.39 | 0.39 | 0.39 | 0.61 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.49 | 0.49
| Visible transmittance | 0.25 | 0.25 | 0.25 | 0.495 | 0.495 | 0.495 | 0.61 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.49 | 0.49
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 10 cm slab-on-grade with carpet | 10 cm slab-on-grade with carpet | 10 cm slab-on-grade with carpet | 10 cm slab-on-grade with carpet | 10 cm slab-on-grade with carpet | 10 cm slab-on-grade with carpet | 10 cm slab-on-grade with carpet | 10 cm slab-on-grade with carpet | 10 cm slab-on-grade with carpet | 10 cm slab-on-grade with carpet | 10 cm slab-on-grade with carpet | 10 cm slab-on-grade with carpet | 10 cm slab-on-grade with carpet | 10 cm slab-on-grade with carpet | 10 cm slab-on-grade with carpet | 10 cm slab-on-grade with carpet
| R-value (m2·K / W) | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC_2:1_UNITARY_PACKAGE_COOLCOIL | 28.5048 | 27.5008 | 29.1575 | 24.7309 | 17.6915 | 24.8595 | 20.0801 | 24.6993 | 22.1592 | 18.0888 | 24.4339 | 21.8021 | 23.3221 | 20.7143 | 20.1989 | 18.9197
| PSZ-AC_1:2_UNITARY_PACKAGE_COOLCOIL | 34.9209 | 35.7792 | 39.6302 | 33.1392 | 25.542 | 37.3962 | 26.5188 | 32.0599 | 33.3854 | 25.0434 | 31.5479 | 32.0517 | 30.0827 | 29.3675 | 26.618 | 31.2428
Heating (kW)
| PSZ-AC_2:1_UNITARY_PACKAGE_HEATCOIL | 9.6915 | 19.2197 | 15.0379 | 19.4775 | 10.381 | 15.46 | 14.0931 | 21.5085 | 18.0176 | 16.9775 | 27.7345 | 24.4075 | 31.3318 | 29.8669 | 32.9242 | 41.1234
| PSZ-AC_1:2_UNITARY_PACKAGE_HEATCOIL | 14.5559 | 26.0059 | 19.9414 | 26.9568 | 14.1557 | 21.2457 | 19.0062 | 30.1351 | 25.6077 | 23.8819 | 39.0956 | 35.1194 | 44.2519 | 42.8051 | 46.6641 | 57.966
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC_2:1_UNITARY_PACKAGE_COOLCOIL | 2.96 | 2.96 | 2.96 | 2.96 | 3.05 | 2.96 | 3.05 | 2.96 | 2.96 | 3.05 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96
| PSZ-AC_1:2_UNITARY_PACKAGE_COOLCOIL | 2.96 | 2.96 | 2.78 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96
| Heating Efficiency (%) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
HVAC Control
| Economizer | None | None | Fixed Dry Bulb | None | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | None | Fixed Dry Bulb | Fixed Dry Bulb | None | Fixed Dry Bulb | None | Fixed Dry Bulb | None | None
Fan Max Flow Rate (m3/s )
| PSZ-AC_2:1_UNITARY_PACKAGE_FAN | 1.33 | 1.3 | 1.57 | 1.22 | 1.07 | 1.49 | 1.21 | 1.17 | 1.34 | 1.09 | 1.16 | 1.32 | 1.16 | 1.25 | 1.13 | 1.14
| PSZ-AC_1:2_UNITARY_PACKAGE_FAN | 1.77 | 1.87 | 2.35 | 1.83 | 1.54 | 2.26 | 1.6 | 1.72 | 2.02 | 1.51 | 1.71 | 1.94 | 1.7 | 1.77 | 1.6 | 1.89
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.077961 | 0.11544 | 0.10684 | 0.11394 | 0.1353 | 0.097487 | 0.15447 | 0.073563 | 0.074634 | 0.07266 | 0.057335 | 0.074674 | 0.074708 | 0.07379 | 0.074513 | 0.097882
| Total Cost ($/m2) | 14.04 | 18.29 | 18.54 | 16.16 | 15.83 | 15.31 | 17.65 | 9.76 | 9.9 | 8.1 | 7.32 | 9.35 | 9.41 | 8.77 | 8.7 | 11.61
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011467 | 0.0080884 | 0.0082481 | 0.0095371 | 0.0086211 | 0.0077083 | 0.008762 | 0.0096566 | 0.0068512 | 0.008468 | 0.0082563 | 0.006862 | 0.0078911 | 0.0079664 | 0.0078569 | 0.0041074
| Total Cost ($/m2) | 0.12 | 0.49 | 0.29 | 0.77 | 0.13 | 0.32 | 0.5 | 1.56 | 0.65 | 1.17 | 2.05 | 1.13 | 2.75 | 2.18 | 3.41 | 2.9
Total Utility Costs
| Cost Intensity ($/m2) | 14.16 | 18.78 | 18.83 | 16.93 | 15.97 | 15.63 | 18.14 | 11.32 | 10.55 | 9.27 | 9.37 | 10.48 | 12.16 | 10.95 | 12.11 | 14.52
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 60802.7778 | 39877.7778 | 44363.8889 | 25875 | 8263.8889 | 31230.5556 | 3133.3333 | 19272.2222 | 13500 | 3247.2222 | 14930.5556 | 7872.2222 | 13400 | 4772.2222 | 6377.7778 | 4550
| Interior Lighting | 30513.8889 | 30513.8889 | 30513.8889 | 30513.8889 | 30513.8889 | 30513.8889 | 30513.8889 | 30513.8889 | 30513.8889 | 30513.8889 | 30513.8889 | 30513.8889 | 30513.8889 | 30513.8889 | 30513.8889 | 30513.8889
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 37308.3333 | 37308.3333 | 37308.3333 | 37308.3333 | 37308.3333 | 37308.3333 | 37308.3333 | 37308.3333 | 37308.3333 | 37308.3333 | 37308.3333 | 37308.3333 | 37308.3333 | 37308.3333 | 37308.3333 | 37308.3333
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 38811.1111 | 39580.5556 | 49097.2222 | 38175 | 32683.3333 | 46927.7778 | 35227.7778 | 36191.6667 | 41991.6667 | 32608.3333 | 35927.7778 | 40713.8889 | 35816.6667 | 37861.1111 | 34275 | 37922.2222
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 167438.8889 | 147280.5556 | 161283.3333 | 131872.2222 | 108772.2222 | 145980.5556 | 106183.3333 | 123286.1111 | 123313.8889 | 103675 | 118680.5556 | 116408.3333 | 117038.8889 | 110455.5556 | 108475 | 110294.4444
Gas (MJ)
| Heating | 250 | 45990 | 22940 | 64880 | 4290 | 28270 | 42590 | 140430 | 77430 | 118130 | 220700 | 142910 | 314040 | 244320 | 393330 | 646360
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 9560 | 9790 | 9660 | 10010 | 9970 | 9820 | 10150 | 10170 | 10140 | 10270 | 10330 | 10320 | 10460 | 10480 | 10680 | 10940
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 9810 | 55780 | 32610 | 74890 | 14250 | 38090 | 52740 | 150610 | 87570 | 128400 | 231030 | 153230 | 324500 | 254800 | 404000 | 657300
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 612580 | 585990 | 613230 | 549630 | 405830 | 563620 | 435000 | 594440 | 531500 | 501630 | 658280 | 572300 | 745840 | 652440 | 794510 | 1054360
| On-Site Production (MJ) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 235.4922 | 154.4486 | 171.8236 | 100.2152 | 32.0065 | 120.9575 | 12.1356 | 74.6423 | 52.2862 | 12.5767 | 57.8268 | 30.4895 | 51.8989 | 18.4831 | 24.7015 | 17.6224
| Interior Lighting (elec) | 118.1818 | 118.1818 | 118.1818 | 118.1818 | 118.1818 | 118.1818 | 118.1818 | 118.1818 | 118.1818 | 118.1818 | 118.1818 | 118.1818 | 118.1818 | 118.1818 | 118.1818 | 118.1818
| Exterior Lighting (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (elec) | 144.497 | 144.497 | 144.497 | 144.497 | 144.497 | 144.497 | 144.497 | 144.497 | 144.497 | 144.497 | 144.497 | 144.497 | 144.497 | 144.497 | 144.497 | 144.497
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 150.3174 | 153.2975 | 190.156 | 147.8537 | 126.5842 | 181.7536 | 136.4389 | 140.1721 | 162.6358 | 126.2937 | 139.1501 | 157.6869 | 138.7197 | 146.638 | 132.7488 | 146.8747
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 648.4992 | 570.425 | 624.6584 | 510.7477 | 421.2803 | 565.39 | 411.2534 | 477.4933 | 477.6009 | 401.5385 | 459.6557 | 450.8553 | 453.2975 | 427.7999 | 420.1291 | 427.1759
Gas (MJ/m2)
| Heating (gas) | 0.26896 | 49.4782 | 24.6799 | 69.801 | 4.6154 | 30.4142 | 45.8203 | 151.0812 | 83.3029 | 127.0898 | 237.4395 | 153.7493 | 337.8591 | 262.851 | 423.163 | 695.3846
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 10.2851 | 10.5325 | 10.3927 | 10.7692 | 10.7262 | 10.5648 | 10.9198 | 10.9414 | 10.9091 | 11.049 | 11.1135 | 11.1027 | 11.2534 | 11.2749 | 11.49 | 11.7698
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 10.5541 | 60.0108 | 35.0834 | 80.5702 | 15.3308 | 40.979 | 56.7402 | 162.0334 | 94.2119 | 138.1388 | 248.553 | 164.8521 | 349.1124 | 274.1259 | 434.6423 | 707.1544
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 659.0425 | 630.4357 | 659.7418 | 591.3179 | 436.6111 | 606.369 | 467.9935 | 639.5266 | 571.8128 | 539.6772 | 708.2087 | 615.7074 | 802.4099 | 701.9258 | 854.7714 | 1134.3303
| On-Site Production (MJ/m2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 31.4961 | 29.4461 | 27.386 | 22.8418 | 26.0892 | 21.1096 | 20.5211 | 19.8838 | 20.5459 | 19.4746 | 19.8536 | 20.3999 | 19.8409 | 20.0744 | 19.665 | 20.0813
| Feb | 32.5272 | 29.9895 | 29.0409 | 23.9851 | 24.9058 | 24.0372 | 23.5296 | 19.8924 | 22.0825 | 19.6977 | 19.8536 | 20.3999 | 19.8409 | 20.0744 | 19.665 | 20.0813
| Mar | 32.8214 | 30.1166 | 33.7236 | 27.0974 | 26.0368 | 28.4876 | 21.1045 | 25.192 | 22.9814 | 20.9041 | 22.5023 | 24.0898 | 20.3987 | 20.8244 | 19.665 | 20.0813
| Apr | 33.7215 | 31.7097 | 34.1857 | 30.0372 | 26.3431 | 33.447 | 25.0871 | 26.4943 | 28.6836 | 20.6091 | 24.0988 | 27.2589 | 23.6953 | 20.0744 | 20.4386 | 20.1207
| May | 35.8552 | 35.9702 | 38.2229 | 32.2523 | 27.3724 | 35.3287 | 26.2743 | 29.8422 | 30.8883 | 25.5251 | 29.5274 | 29.077 | 29.9814 | 25.8688 | 25.4767 | 25.841
| Jun | 37.1082 | 36.1487 | 45.0174 | 33.9744 | 27.3392 | 41.4346 | 27.3817 | 35.1737 | 33.4992 | 27.485 | 34.338 | 32.0589 | 33.8412 | 32.248 | 30.2879 | 28.4985
| Jul | 36.4565 | 37.3103 | 43.9037 | 36.4975 | 27.9783 | 40.0914 | 29.5638 | 36.0968 | 34.2965 | 28.9709 | 34.8638 | 32.9735 | 33.3445 | 31.7086 | 31.9703 | 28.1611
| Aug | 37.1143 | 37.3533 | 44.3091 | 34.7914 | 30.1456 | 39.8128 | 27.9695 | 36.0432 | 34.4164 | 28.341 | 34.388 | 33.3319 | 33.1169 | 30.4904 | 30.8795 | 28.1649
| Sep | 36.1766 | 36.2488 | 40.6829 | 32.7935 | 28.7611 | 39.0776 | 31.942 | 32.1194 | 30.5491 | 28.0114 | 30.5939 | 30.3056 | 30.5305 | 28.1555 | 28.3475 | 21.299
| Oct | 35.5372 | 32.8741 | 34.3883 | 29.4092 | 27.4563 | 33.5013 | 26.2108 | 29.5048 | 28.3591 | 21.2439 | 27.3019 | 28.2889 | 23.5824 | 23.9526 | 21.7463 | 20.0813
| Nov | 33.3667 | 30.7556 | 31.2228 | 26.294 | 25.7159 | 25.5437 | 21.1682 | 26.8025 | 20.8147 | 19.4746 | 26.6635 | 21.0691 | 21.5497 | 20.0744 | 19.665 | 20.0813
| Dec | 31.3755 | 29.1543 | 26.1405 | 22.8987 | 26.1285 | 23.9813 | 20.537 | 19.8838 | 20.5458 | 19.4746 | 19.8536 | 20.3999 | 19.8409 | 20.0744 | 19.665 | 20.0813
Time of Peak Electrical Demand
| Jan | 06-JAN-13:00 | 03-JAN-13:00 | 27-JAN-14:00 | 23-JAN-15:00 | 26-JAN-13:00 | 19-JAN-14:00 | 27-JAN-15:00 | 17-JAN-12:39 | 27-JAN-14:00 | 02-JAN-08:09 | 02-JAN-08:09 | 24-JAN-15:30 | 03-JAN-11:09 | 02-JAN-08:09 | 02-JAN-08:09 | 02-JAN-08:09
| Feb | 22-FEB-15:00 | 23-FEB-14:00 | 28-FEB-15:00 | 22-FEB-15:00 | 13-FEB-11:00 | 08-FEB-15:00 | 15-FEB-15:00 | 15-FEB-15:00 | 14-FEB-15:00 | 22-FEB-14:00 | 01-FEB-08:09 | 01-FEB-08:09 | 06-FEB-11:50 | 01-FEB-08:09 | 01-FEB-08:09 | 01-FEB-08:09
| Mar | 13-MAR-14:00 | 29-MAR-11:00 | 17-MAR-14:00 | 28-MAR-14:00 | 31-MAR-14:39 | 31-MAR-14:00 | 01-MAR-14:30 | 10-MAR-10:00 | 02-MAR-14:00 | 29-MAR-14:00 | 31-MAR-14:00 | 30-MAR-14:00 | 23-MAR-14:00 | 30-MAR-14:00 | 01-MAR-08:09 | 01-MAR-08:09
| Apr | 03-APR-14:39 | 21-APR-14:00 | 26-APR-14:00 | 14-APR-14:00 | 13-APR-11:00 | 21-APR-14:00 | 13-APR-14:00 | 05-APR-14:00 | 21-APR-14:00 | 19-APR-14:00 | 28-APR-14:39 | 26-APR-14:00 | 27-APR-14:00 | 14-APR-14:50 | 04-APR-14:00 | 25-APR-14:00
| May | 24-MAY-14:00 | 18-MAY-14:00 | 30-MAY-14:00 | 15-MAY-14:00 | 30-MAY-13:09 | 31-MAY-14:00 | 17-MAY-13:00 | 15-MAY-14:00 | 31-MAY-14:00 | 05-MAY-13:50 | 05-MAY-13:00 | 23-MAY-14:00 | 31-MAY-11:00 | 17-MAY-14:00 | 31-MAY-14:00 | 24-MAY-14:00
| Jun | 28-JUN-14:00 | 13-JUN-14:00 | 28-JUN-14:00 | 19-JUN-14:00 | 28-JUN-13:00 | 27-JUN-14:00 | 16-JUN-14:00 | 30-JUN-14:00 | 29-JUN-13:00 | 28-JUN-14:00 | 08-JUN-12:00 | 28-JUN-13:39 | 29-JUN-14:00 | 30-JUN-14:00 | 14-JUN-14:00 | 21-JUN-14:00
| Jul | 13-JUL-14:00 | 18-JUL-12:00 | 19-JUL-14:00 | 03-JUL-14:00 | 24-JUL-14:00 | 24-JUL-14:00 | 03-JUL-12:00 | 25-JUL-13:30 | 31-JUL-14:00 | 24-JUL-14:00 | 13-JUL-14:00 | 18-JUL-13:00 | 13-JUL-14:00 | 21-JUL-14:00 | 06-JUL-14:00 | 11-JUL-14:00
| Aug | 21-AUG-14:00 | 31-AUG-13:00 | 01-AUG-14:00 | 17-AUG-14:00 | 09-AUG-14:50 | 04-AUG-14:00 | 15-AUG-11:00 | 17-AUG-14:00 | 01-AUG-13:00 | 07-AUG-14:00 | 04-AUG-14:00 | 30-AUG-13:00 | 25-AUG-14:00 | 09-AUG-14:00 | 11-AUG-14:00 | 15-AUG-14:30
| Sep | 01-SEP-14:00 | 15-SEP-14:00 | 08-SEP-14:30 | 11-SEP-13:00 | 25-SEP-14:00 | 01-SEP-14:00 | 28-SEP-14:00 | 08-SEP-14:00 | 01-SEP-14:50 | 01-SEP-14:00 | 06-SEP-12:39 | 06-SEP-14:50 | 14-SEP-14:00 | 12-SEP-13:00 | 07-SEP-14:00 | 01-SEP-14:00
| Oct | 06-OCT-14:00 | 13-OCT-14:00 | 13-OCT-14:00 | 02-OCT-14:39 | 05-OCT-14:20 | 03-OCT-14:00 | 31-OCT-13:20 | 03-OCT-14:00 | 13-OCT-14:00 | 17-OCT-14:00 | 31-OCT-13:30 | 05-OCT-14:00 | 06-OCT-14:00 | 06-OCT-14:00 | 06-OCT-14:00 | 02-OCT-07:10
| Nov | 07-NOV-14:00 | 03-NOV-14:39 | 13-NOV-15:00 | 22-NOV-14:00 | 10-NOV-14:00 | 10-NOV-14:50 | 08-NOV-14:50 | 03-NOV-13:00 | 08-NOV-15:50 | 01-NOV-08:09 | 02-NOV-14:39 | 10-NOV-13:00 | 02-NOV-15:09 | 01-NOV-08:09 | 01-NOV-08:09 | 01-NOV-08:09
| Dec | 19-DEC-14:30 | 19-DEC-15:20 | 11-DEC-15:00 | 05-DEC-14:50 | 19-DEC-12:00 | 05-DEC-14:00 | 07-DEC-14:00 | 01-DEC-08:09 | 01-DEC-08:09 | 01-DEC-08:20 | 01-DEC-08:09 | 01-DEC-08:09 | 05-DEC-13:50 | 01-DEC-08:09 | 01-DEC-08:09 | 01-DEC-08:09
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 10.03 | 10.03 | 10.03 | 10.03 | 10.03 | 10.03 | 10.03 | 10.03 | 10.03 | 10.03 | 10.03 | 10.03 | 10.03 | 10.03 | 10.03 | 10.03
| Total Building | 10.03 | 10.03 | 10.03 | 10.03 | 10.03 | 10.03 | 10.03 | 10.03 | 10.03 | 10.03 | 10.03 | 10.03 | 10.03 | 10.03 | 10.03 | 10.03
Emissions
| Carbon Equivalent (kg) | 46096.6535 | 50133.2429 | 49275.5734 | 41971.8291 | 12968.6476 | 49922.8442 | 13360.2191 | 35985.5656 | 51952.6534 | 9866.5301 | 67439.8951 | 50315.668 | 45913.189 | 44959.4674 | 44415.2342 | 42888.1572
| CO2 (kg) | 106840.743 | 126180.8183 | 116197.3221 | 96096.0235 | 34680.4863 | 118600.467 | 35878.163 | 82455.0873 | 121937.6427 | 24627.1845 | 158026.4818 | 118785.27 | 109264.1474 | 107158.1683 | 106647.7261 | 111989.1735
| NOX (kg) | 187.9876 | 164.6717 | 195.0634 | 181.5692 | 29.7174 | 193.0436 | 30.8468 | 156.2962 | 210.0813 | 34.8944 | 276.7599 | 201.6541 | 183.8848 | 178.7036 | 175.3122 | 128.4885
| SO2 (kg) | 716.7035 | 702.5477 | 648.5627 | 462.8899 | 316.5144 | 803.0275 | 308.9934 | 450.0878 | 538.5105 | 80.1678 | 799.8657 | 508.3722 | 276.3173 | 294.9992 | 256.1249 | 561.6152
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0033 | 0.002 | 0.0018 | 0.0017 | 0.0001 | 0.0015 | 0.0001 | 0.0018 | 0.0021 | 0.0003 | 0.0024 | 0.002 | 0.002 | 0.0021 | 0.0019 | 0.002
| Water Environmental Factors (m3) | 88.7015 | 239.6443 | 4790.8353 | 823.3542 | 1909.7753 | 4004.8673 | 1864.332 | 27.9908 | 559.9435 | 1059.2392 | 184.1239 | 528.586 | 181.5787 | 6996.7454 | 168.2913 | 112.6849

## Picture
DOE Commercial Building Benchmark - Outpatient Health Care

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 10.6 | 60.1 | 3133.79
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 5.5
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.6
BLDG_LIGHT_EXTD_SCH | Fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 15.2 | 104.6 | 5454.14
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 15
|  |  | Sun, Hol, Other | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 13.6
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0 | 0 | 8.5 | 46.7 | 2435.07
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 3.8
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4
BLDG_OCC_EXTD_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 13.5 | 90.4 | 4713.71
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 11.7
|  |  | Sun, Hol, Other | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 11.2
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 15.3 | 96.7 | 5042.21
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 12.2
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 8
BLDG_EQUIP_EXTD_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 15.3 | 99.9 | 5209.07
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 12.2
|  |  | Sun, Hol, Other | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 11.2
Kitchen_Elec_Equip_SCH | Fraction | Through 12/31 | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 5.95 | 23.8 | 1241
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 5.95
|  |  | SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 7.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 5.95
Kitchen_Gas_Equip_SCH | Fraction | Through 12/31 | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65 | 21.9 | 1141.93
|  |  | SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65
Kitchen_Exhaust_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 2.72 | 19.04 | 992.8
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.2 | 0.2 | 13.64 | 82.96 | 4325.77
|  |  | Sat, WinterDesign | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 8.36
|  |  | Sun, Hol, Other | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 6.4
INFIL_SCH | fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INFIL_HALF_ON_SCH | fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84 | 4380
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12
|  |  | SummerDesign, WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12
INFIL_QUARTER_ON_SCH | fraction | Through 12/31 | WD | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6 | 42 | 2190
|  |  | Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | SummerDesign, WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0.01 | 0.01 | 7.83 | 41.88 | 2183.74
|  |  | Sat, WinterDesign | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 2.49
|  |  | Sun, Hol, Other | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.24
BLDG_SWH_EXTD_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 11.48 | 77 | 4015
|  |  | Sat, WinterDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 9.8
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 9.8
Hours_of_operation | on/off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | on/off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | All | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 3528 | 183960
CLGSETP_SCH | Temperature | Through 12/31 | All | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 4032 | 210240
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ER_Exam1_Mult4_Flr_1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
ER_Exam1_Mult4_Flr_1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
ER_Exam1_Mult4_Flr_1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
ER_Exam1_Mult4_Flr_1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
ER_Exam2_Flr_1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
ER_Exam2_Flr_1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
ER_Exam2_Flr_1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
ER_Exam2_Flr_1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
ER_Exam3_Mult4_Flr_1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
ER_Exam3_Mult4_Flr_1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
ER_Exam3_Mult4_Flr_1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
ER_Exam3_Mult4_Flr_1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
ER_Exam4_Flr_1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
ER_Exam4_Flr_1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
ER_Exam4_Flr_1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
ER_Exam4_Flr_1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
ER_Exam5_Mult4_Flr_1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
ER_Exam5_Mult4_Flr_1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
ER_Exam5_Mult4_Flr_1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
ER_Exam5_Mult4_Flr_1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
OR1_Flr_2 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
OR1_Flr_2 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
OR1_Flr_2 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
OR1_Flr_2 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
OR2_Mult5_Flr_2 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
OR2_Mult5_Flr_2 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
OR2_Mult5_Flr_2 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
OR2_Mult5_Flr_2 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
OR3_Flr_2 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
OR3_Flr_2 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
OR3_Flr_2 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
OR3_Flr_2 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
OR4_Flr_2 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
OR4_Flr_2 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
OR4_Flr_2 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
OR4_Flr_2 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom1_Mult10_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom1_Mult10_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom1_Mult10_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
PatRoom1_Mult10_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom2_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom2_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom2_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
PatRoom2_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom3_Mult10_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom3_Mult10_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom3_Mult10_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
PatRoom3_Mult10_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom4_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom4_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom4_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
PatRoom4_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom5_Mult10_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom5_Mult10_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom5_Mult10_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
PatRoom5_Mult10_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PhysTherapy_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PhysTherapy_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PhysTherapy_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
PhysTherapy_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom6_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom6_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom6_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
PatRoom6_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom7_Mult10_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom7_Mult10_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom7_Mult10_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
PatRoom7_Mult10_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom8_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom8_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom8_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
PatRoom8_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Lab_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Lab_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Lab_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Lab_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom1_Mult10_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom1_Mult10_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom1_Mult10_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
PatRoom1_Mult10_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom2_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom2_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom2_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
PatRoom2_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom3_Mult10_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom3_Mult10_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom3_Mult10_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
PatRoom3_Mult10_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom4_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom4_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom4_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
PatRoom4_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom5_Mult10_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom5_Mult10_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom5_Mult10_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
PatRoom5_Mult10_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Radiology_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Radiology_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Radiology_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Radiology_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom6_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom6_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom6_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
PatRoom6_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom7_Mult10_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom7_Mult10_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom7_Mult10_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
PatRoom7_Mult10_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom8_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom8_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom8_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
PatRoom8_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Lab_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Lab_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Lab_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Lab_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_Flr_5 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Kitchen_Flr_5 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Kitchen_Flr_5 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Kitchen_Flr_5 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_Flr_5_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Kitchen_Flr_5_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Kitchen_Flr_5_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Kitchen_Flr_5_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Kitchen_Flr_5_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
SHWSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SHWSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SHWSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720