## BuildingSummary
Building Summary - Primary School new construction version 1.0_3.0
|  | Value | Data Source
Program
| Building Name | Benchmark Primary School New
| Available Fuel Types | gas, electricity
| Principal Building Activity | Education
Form
| Total Floor Area (m2) | 6871 | Pless, S.; Torcellini, P.; Long, N. (2007). Technical Support Document: Development of the Advanced Energy Design Guide for K-12 Schools--30% Energy Savings. 178 pp.; NREL Report No. TP-550-42114. http://www.nrel.gov/docs/fy07osti/42114.pdf
| Building Shape | "E" Shape
Aspect Ratio
| Number of Floors | 1
Window Fraction (Window to Wall Ratio)
| South | 0.35
| East | 0.35
| North | 0.35
| West | 0.35
| Total | 0.35
| Skylight/TDD Percentage | 0.19%
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | See pictures
| Floor to Ceiling Height (m) | 4
| Roof type | Flat built-up | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel-Framed | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 2512
| Net Dimensions - Total Area (m2) | 1619.42
| Wall to Skin Ratio | 0.27
Roof
| Construction Type | Insulation Entirely Above Deck | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 6871
| Net Dimensions - Total Area (m2) | 6871
| Roof to Skin Ratio | 0.73
Window Dimensions (m2)
| South | 324.79 | Pless, S.; Torcellini, P.; Long, N. (2007). Technical Support Document: Development of the Advanced Energy Design Guide for K-12 Schools--30% Energy Savings. 178 pp.; NREL Report No. TP-550-42114. http://www.nrel.gov/docs/fy07osti/42114.pdf
| East | 114.8
| North | 324.79
| West | 114.8
| Total Area (m2) | 879.18
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 13.38
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 10 cm concrete slab-on-grade
| Dimensions - Total Area (m2) | 6871
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 2932
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 13742
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.37 | 2003 CBECS
HVAC |  |  | 2003 CBECS
| System Type | CAV, PSZ-AC (gym, kitchen, & cafeteria) | 2003 CBECS
| Heating Type | gas boiler, gas furnace (gym, kitchen, & cafeteria) | 2003 CBECS
| Cooling Type | PACU
| Fan Control | Constant
Service Water Heating
| SWH Type | Storage Tank | Standard 90.1-2004
| Fuel | Natural Gas
| Thermal Efficiency (%) | 80
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 589.92

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
First Floor
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 15 | 0 | 0 | 5 | 0.6 | 183.15 | 0 | 0.49196
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 15 | 0 | 0 | 5 | 0.6 | 882.45 | 0 | 0.39302
CORRIDOR_POD_1_ZN_1_FLR_1 | Yes | 1 | 192 | 768 | 4 | 12 | 4.2 | 10 | 19.2 | 5.38 | 4 | 0 | 0 | 0 | 0.3 | 57.6 | 0 | 0.2891
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 15 | 0 | 0 | 5 | 0.6 | 183.15 | 0 | 0.49196
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 15 | 0 | 0 | 5 | 0.6 | 882.45 | 0 | 0.39302
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 15 | 0 | 0 | 5 | 0.6 | 183.15 | 0 | 0.49196
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 15 | 0 | 0 | 5 | 0.6 | 882.45 | 0 | 0.39302
CORRIDOR_POD_2_ZN_1_FLR_1 | Yes | 1 | 192 | 768 | 4 | 12 | 4.2 | 10 | 19.2 | 5.38 | 4 | 0 | 0 | 0 | 0.3 | 57.6 | 0 | 0.2891
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 15 | 0 | 0 | 5 | 0.6 | 183.15 | 0 | 0.49196
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 15 | 0 | 0 | 5 | 0.6 | 882.45 | 0 | 0.39302
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 15 | 0 | 0 | 5 | 0.6 | 183.15 | 0 | 0.49196
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 15 | 0 | 0 | 5 | 0.6 | 882.45 | 0 | 0.39302
CORRIDOR_POD_3_ZN_1_FLR_1 | Yes | 1 | 192 | 768 | 4 | 12 | 4.2 | 10 | 19.2 | 5.38 | 4 | 0 | 0 | 0 | 0.3 | 57.6 | 0 | 0.2891
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 15 | 0 | 0 | 5 | 0.6 | 183.15 | 0 | 0.49196
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | Yes | 1 | 315 | 1260 | 4 | 140 | 49 | 4 | 78.75 | 15.064 | 8.07 | 0 | 0 | 5 | 0.6 | 582.75 | 0 | 0.39302
COMPUTER_CLASS_ZN_1_FLR_1 | Yes | 1 | 162 | 648 | 4 | 72 | 25.2 | 3.33 | 48.6486 | 15.064 | 20 | 0 | 0 | 5 | 0.6 | 340.4432 | 0 | 0.39302
MAIN_CORRIDOR_ZN_1_FLR_1 | Yes | 1 | 546 | 2184 | 4 | 36 | 12.6 | 0 | 0 | 13.988 | 4 | 0 | 0 | 2.5 | 0.3 | 163.8 | 0 | 0.29003
LOBBY_ZN_1_FLR_1 | Yes | 1 | 171 | 684 | 4 | 76 | 26.6 | 0 | 0 | 13.988 | 4 | 0 | 0 | 2.5 | 0.3 | 51.3 | 0 | 0.39302
MECH_ZN_1_FLR_1 | Yes | 1 | 252 | 1008 | 4 | 0 | 0 | 100 | 2.52 | 16.14 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27209
BATH_ZN_1_FLR_1 | Yes | 1 | 190 | 760 | 4 | 40 | 14 | 100 | 1.9 | 9.684 | 4 | 0 | 0 | 0 | 0 | 0 | 283.1682 | 0.32937
OFFICES_ZN_1_FLR_1 | Yes | 1 | 441 | 1764 | 4 | 168 | 58.8 | 20 | 22.05 | 11.836 | 10.8 | 0 | 0 | 2.5 | 0.3 | 187.425 | 0 | 0.37575
GYM_ZN_1_FLR_1 | Yes | 1 | 357 | 1428 | 4 | 68 | 37.18 | 3.33 | 107.2072 | 15.064 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32392
KITCHEN_ZN_1_FLR_1 | Yes | 1 | 168 | 672 | 4 | 32 | 11.2 | 6.67 | 25.1874 | 12.912 | 190.452 | 1431.08 | 378.54 | 0 | 0 | 0 | 2359.735 | 0.32392
CAFETERIA_ZN_1_FLR_1 | Yes | 1 | 315 | 1260 | 4 | 144 | 50.4 | 1.3935 | 226.0419 | 15.064 | 25.3936 | 0 | 0 | 3.8 | 0.9 | 1142.4592 | 0 | 0.39648
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | Yes | 1 | 399 | 1596 | 4 | 160 | 56 | 4.35 | 91.7241 | 13.988 | 15 | 0 | 0 | 5 | 0.6 | 698.0207 | 0 | 0.3812
Building Total Conditioned Zones |  |  | 6871 | 27484 |  | 2512 | 892.58 |  | 1406.3793
Data Source | [7 empty] | 1 |  | 2 | 4, 5 | 4, 5 | 4, 5 | 3 | 3 | 3 | 4 | 4
Sources
[1] Pless, S.; Torcellini, P.; Long, N. (2007). Technical Support Document: Development of the Advanced Energy Design Guide for K-12 Schools--30% Energy Savings. 178 pp.; NREL Report No. TP-550-42114. http://www.nrel.gov/docs/fy07osti/42114.pdf
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report
[5] Smith, V. A. and D.R. Fisher. (2001). Estimating Food Service Loads and Profiles. ASHRAE Transactions 2001. V. 107. Pt 2. Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.

## Query (hidden)
1-miami
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 6374.3 | 927.71 | 927.71
Net Site Energy | 6374.3 | 927.71 | 927.71
Total Source Energy | 20072.74 | 2921.37 | 2921.37
Net Source Energy | 20072.74 | 2921.37 | 2921.37
Area (m2)
Total Building Area | 6871
Net Conditioned Building Area | 6871
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 72.08 | 0 | 0 | 0 | 0
Cooling | 2232.68 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1297.99 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 61.76 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1256.13 | 361.03 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 961.3 | 0 | 0 | 0 | 0 | 0
Pumps | 0.07 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 48.15 | 0 | 0 | 0 | 589.92
Refrigeration | 83.11 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5893.04 | 481.26 | 0 | 0 | 0 | 589.92
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 5893.04 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 5893.04 | 100
Total On-Site and Utility Electric Sources | 5893.04 | 100
Total Electricity End Uses | 5893.04 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 162 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 546 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 171 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 252 | 90 | 0
BATH_ZN_1_FLR_1_WALL_5 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 190 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 441 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 168 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 399 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 4.2 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 4.2 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 4.2 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 49 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 25.2 | 6.88 | 0.25 | 0.25 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 26.6 | 6.88 | 0.25 | 0.25 | No | LOBBY_ZN_1_FLR_1_WALL_1
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 14 | 6.88 | 0.25 | 0.25 | No | BATH_ZN_1_FLR_1_WALL_5
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 29.4 | 6.88 | 0.25 | 0.25 | No | OFFICES_ZN_1_FLR_1_WALL_1
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 29.4 | 6.88 | 0.25 | 0.25 | No | OFFICES_ZN_1_FLR_1_WALL_2
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 23.8 | 6.88 | 0.25 | 0.25 | No | GYM_ZN_1_FLR_1_WALL_2
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 11.2 | 6.88 | 0.25 | 0.25 | No | KITCHEN_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 21 | 6.88 | 0.25 | 0.25 | No | CAFETERIA_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 29.4 | 6.88 | 0.25 | 0.25 | No | CAFETERIA_ZN_1_FLR_1_WALL_3
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 29.4 | 6.88 | 0.25 | 0.25 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 26.6 | 6.88 | 0.25 | 0.25 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
HEATSYS1 BOILER | Boiler:HotWater | 3597984.2 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 247796.7 | 3
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 199305.24 | 3
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 197878.44 | 3
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 287861.2 | 3
PSZ-AC_2:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 73966.93 | 3.69
PSZ-AC_1:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 87625.94 | 3.69
PSZ-AC_2:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 97039.16 | 3.69
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.67 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.02 | 0 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 2.26 | 0 | 1 | Zone Exhaust Fans
VAV_POD_1 FAN | Fan:VariableVolume | 0.28 | 655.15 | 14.97 | 35482.14 | 1 | Fan Energy
VAV_POD_2 FAN | Fan:VariableVolume | 0.28 | 655.15 | 12.04 | 28538.62 | 1 | Fan Energy
VAV_POD_3 FAN | Fan:VariableVolume | 0.28 | 655.15 | 11.95 | 28334.32 | 1 | Fan Energy
VAV_OTHER FAN | Fan:VariableVolume | 0.28 | 655.15 | 17.39 | 41219 | 1 | Fan Energy
PSZ-AC_2:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.48 | 4976.9 | 1 | General
PSZ-AC_1:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.53 | 5041 | 1 | General
PSZ-AC_2:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.91 | 5582.52 | 1 | General
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001977 | 90911.96 | 3218.68
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006155 | 283019.49 | 10020.12
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001874 | 86168.26 | 3050.73
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002058 | 94629.9 | 3350.31
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006458 | 296928.36 | 10512.55
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001967 | 90438.02 | 3201.9
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006092 | 280123.28 | 9917.58
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001868 | 85909.58 | 3041.57
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002059 | 94657.12 | 3351.27
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00646 | 297046.79 | 10516.74
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001968 | 90491.36 | 3203.79
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006113 | 281058.42 | 9950.68
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001884 | 86624.01 | 3066.86
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002068 | 95076 | 3366.1
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004329 | 199062.44 | 7047.67
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002702 | 124251.52 | 4399.04
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004672 | 214802.98 | 7604.96
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001861 | 85572.75 | 3029.65
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002193 | 100838.97 | 3570.14
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002094 | 96296.96 | 3409.33
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005107 | 234823.24 | 8313.76
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005172 | 237830.46 | 8420.23
VAV_POD_1_HEATC | 0.000381 | 17499.84 | 289.17
VAV_POD_2_HEATC | 0.000345 | 15843.13 | 261.34
VAV_POD_3_HEATC | 0.000304 | 13995.95 | 231.27
VAV_OTHER_HEATC | 8.9e-05 | 4083.37 | 68.27
Nominal Capacity [W]
PSZ-AC_2:5_UNITARY_PACKAGE_HEATCOIL | 41464.77
PSZ-AC_1:6_UNITARY_PACKAGE_HEATCOIL | 91359.55
PSZ-AC_2:7_UNITARY_PACKAGE_HEATCOIL | 87515.05
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 84190.2605 | 145.777 | 546.2112 | 0 | 0.0025 | 67599.0916 | 36087.9072
February | 77269.2351 | 134.4261 | 506.2903 | 0 | 0.0023 | 62658.9743 | 33184.6485
March | 89424.6933 | 155.5945 | 586.1051 | 0 | 0.0027 | 72536.9383 | 38407.1736
April | 84127.1062 | 146.8003 | 554.7163 | 0 | 0.0025 | 68652.552 | 36174.3287
May | 99378.2134 | 173.6482 | 657.1282 | 0 | 0.003 | 81327.389 | 42755.7893
June | 100322.7255 | 175.4194 | 664.3248 | 0 | 0.003 | 82218.1439 | 43174.2578
July | 83190.0235 | 145.1911 | 548.7416 | 0 | 0.0025 | 67913.1436 | 35773.9878
August | 88721.6812 | 154.7106 | 584.1684 | 0 | 0.0027 | 72297.5092 | 38139.2391
September | 95163.312 | 166.3634 | 629.8879 | 0 | 0.0029 | 77956.1416 | 40950.4239
October | 94225.7095 | 164.5586 | 622.3778 | 0 | 0.0028 | 77026.5506 | 40530.355
November | 88384.8727 | 154.185 | 582.4366 | 0 | 0.0027 | 72083.2256 | 38000.6386
December | 80207.3873 | 139.4128 | 524.5601 | 0 | 0.0024 | 64919.9619 | 34433.9904
Annual Sum or Average | 1064605.2202 | 1856.087 | 7006.948 | 0 | 0.032 | 867189.6213 | 457612.7398
Minimum of Months | 77269.2351 | 134.4261 | 506.2903 | 0 | 0.0023 | 62658.9743 | 33184.6485
Maximum of Months | 100322.7255 | 175.4194 | 664.3248 | 0 | 0.003 | 82218.1439 | 43174.2578
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 459373000000 | 438972.264 | 06-JAN-11:50 | 84768.624 | 81262.495 | 71524.253 | 0 | 197575.521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3841.37 | 0 | 0
February | 425803000000 | 444202.518 | 23-FEB-11:50 | 84768.624 | 81262.495 | 71663.073 | 0 | 202666.943 | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 | 3841.379 | 0 | 0
March | 492929000000 | 449829.463 | 14-MAR-10:39 | 84768.624 | 81262.495 | 71524.253 | 0 | 208432.658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3841.433 | 0 | 0
April | 466532000000 | 457673.989 | 03-APR-13:00 | 84768.624 | 77263.149 | 72147.463 | 0 | 220882.797 | 0 | 0.006 | 0 | 0 | 0 | 0 | 0 | 2611.951 | 0 | 0
May | 552665000000 | 498522.433 | 22-MAY-06:10 | 84768.624 | 29771.525 | 92642.785 | 0 | 288602.784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2736.714 | 0 | 0
June | 558718000000 | 507756.05 | 26-JUN-10:00 | 84768.624 | 81262.495 | 71524.253 | 0 | 267446.444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2754.234 | 0 | 0
July | 461508000000 | 415286.556 | 13-JUL-11:00 | 47093.68 | 47274.638 | 71524.253 | 0 | 246902.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2491.073 | 0 | 0
August | 491302000000 | 431313.365 | 21-AUG-13:00 | 47093.68 | 43275.293 | 71524.253 | 0 | 266930.184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2489.954 | 0 | 0
September | 529755000000 | 486210.767 | 18-SEP-11:00 | 84768.624 | 80410.298 | 71829.49 | 0 | 246587.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2614.775 | 0 | 0
October | 523438000000 | 479501.201 | 06-OCT-13:00 | 84768.624 | 76410.953 | 72285.63 | 0 | 243421.055 | 0 | 0.006 | 0 | 0 | 0 | 0 | 0 | 2614.934 | 0 | 0
November | 489846000000 | 455136.459 | 01-NOV-11:50 | 84768.624 | 80410.298 | 71551.013 | 0 | 214565.161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3841.363 | 0 | 0
December | 441167000000 | 423110.064 | 15-DEC-14:00 | 84768.624 | 76410.953 | 71524.253 | 0 | 187792.913 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 2613.319 | 0 | 0
Annual Sum or Average | 5893040000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 425803000000 | 415286.556 |  | 47093.68 | 29771.525 | 71524.253 | 0 | 187792.913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2489.954 | 0 | 0
Maximum of Months | 558718000000 | 507756.05 |  | 84768.624 | 81262.495 | 92642.785 | 0 | 288602.784 | 0 | 0.006 | 0 | 0 | 0 | 0 | 0 | 3841.433 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 146160.01 | 5512.53 | 0 | 151672.54
Cost per Total Building Area ($/m2) | 21.27 | 0.8 | 0 | 22.07
Cost per Net Conditioned Building Area ($/m2) | 21.27 | 0.8 | 0 | 22.07
2-houston
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 6601.14 | 960.72 | 960.72
Net Site Energy | 6601.14 | 960.72 | 960.72
Total Source Energy | 1238.1 | 180.19 | 180.19
Net Source Energy | 1238.1 | 180.19 | 180.19
Area (m2)
Total Building Area | 6871
Net Conditioned Building Area | 6871
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 710.01 | 0 | 0 | 0 | 0
Cooling | 1800.74 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1297.99 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 61.74 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1256.13 | 361.03 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 967.94 | 0 | 0 | 0 | 0 | 0
Pumps | 0.63 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 62.75 | 0 | 0 | 0 | 589.92
Refrigeration | 82.18 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5467.35 | 1133.79 | 0 | 0 | 0 | 589.92
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 5467.35 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 5467.35 | 100
Total On-Site and Utility Electric Sources | 5467.35 | 100
Total Electricity End Uses | 5467.35 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 162 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 546 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 171 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 252 | 90 | 0
BATH_ZN_1_FLR_1_WALL_5 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 190 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 441 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 168 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 399 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 4.2 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 4.2 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 4.2 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 49 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 25.2 | 6.88 | 0.25 | 0.25 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 26.6 | 6.88 | 0.25 | 0.25 | No | LOBBY_ZN_1_FLR_1_WALL_1
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 14 | 6.88 | 0.25 | 0.25 | No | BATH_ZN_1_FLR_1_WALL_5
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 29.4 | 6.88 | 0.25 | 0.25 | No | OFFICES_ZN_1_FLR_1_WALL_1
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 29.4 | 6.88 | 0.25 | 0.25 | No | OFFICES_ZN_1_FLR_1_WALL_2
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 23.8 | 6.88 | 0.25 | 0.25 | No | GYM_ZN_1_FLR_1_WALL_2
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 11.2 | 6.88 | 0.25 | 0.25 | No | KITCHEN_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 21 | 6.88 | 0.25 | 0.25 | No | CAFETERIA_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 29.4 | 6.88 | 0.25 | 0.25 | No | CAFETERIA_ZN_1_FLR_1_WALL_3
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 29.4 | 6.88 | 0.25 | 0.25 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 26.6 | 6.88 | 0.25 | 0.25 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
HEATSYS1 BOILER | Boiler:HotWater | 3700174.33 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 250491.98 | 3
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 200422.92 | 3
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 200689.75 | 3
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 282399.29 | 3
PSZ-AC_2:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 72548.93 | 3.69
PSZ-AC_1:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 85990.21 | 3.69
PSZ-AC_2:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 96377.88 | 3.69
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.67 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.02 | 0 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 2.26 | 0 | 1 | Zone Exhaust Fans
VAV_POD_1 FAN | Fan:VariableVolume | 0.28 | 655.15 | 15.13 | 35868.08 | 1 | Fan Energy
VAV_POD_2 FAN | Fan:VariableVolume | 0.28 | 655.15 | 12.11 | 28698.66 | 1 | Fan Energy
VAV_POD_3 FAN | Fan:VariableVolume | 0.28 | 655.15 | 12.12 | 28736.87 | 1 | Fan Energy
VAV_OTHER FAN | Fan:VariableVolume | 0.28 | 655.15 | 17.06 | 40436.9 | 1 | Fan Energy
PSZ-AC_2:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.42 | 4881.37 | 1 | General
PSZ-AC_1:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.46 | 4946.89 | 1 | General
PSZ-AC_2:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.88 | 5544.48 | 1 | General
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002045 | 94048.33 | 3329.72
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006458 | 296948.78 | 10513.27
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001792 | 82416.83 | 2917.91
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002056 | 94557.08 | 3347.73
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006248 | 287275.64 | 10170.8
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002036 | 93601.32 | 3313.89
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006417 | 295070.27 | 10446.77
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001787 | 82155.42 | 2908.66
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002057 | 94582.5 | 3348.63
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00625 | 287381.34 | 10174.54
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002037 | 93653.84 | 3315.75
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006439 | 296065.66 | 10482.01
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001803 | 82898.78 | 2934.98
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002066 | 94984.61 | 3362.87
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004189 | 192597.36 | 6818.78
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002625 | 120685.42 | 4272.79
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004385 | 201615.99 | 7138.08
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001972 | 90670.51 | 3210.13
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002046 | 94053.26 | 3329.89
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002031 | 93375.2 | 3305.89
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005138 | 236248.36 | 8364.21
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005069 | 233062.15 | 8251.41
VAV_POD_1_HEATC | 0.001082 | 49755.65 | 803.6
VAV_POD_2_HEATC | 0.000941 | 43287.75 | 697.21
VAV_POD_3_HEATC | 0.000864 | 39708.96 | 641.41
VAV_OTHER_HEATC | 0.000641 | 29473.34 | 483.9
Nominal Capacity [W]
PSZ-AC_2:5_UNITARY_PACKAGE_HEATCOIL | 54739.18
PSZ-AC_1:6_UNITARY_PACKAGE_HEATCOIL | 120607.13
PSZ-AC_2:7_UNITARY_PACKAGE_HEATCOIL | 115531.87
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 108349.5941 | 137.6926 | 551.3274 | 0 | 0.0016 | 188045.4938 | 42570.6462
February | 93816.7485 | 119.4185 | 480.1021 | 0 | 0.0014 | 163753.0895 | 36885.7479
March | 109295.8805 | 141.3506 | 590.5331 | 0 | 0.0017 | 201429.5581 | 43258.9542
April | 103173.5324 | 134.4159 | 571.2244 | 0 | 0.0016 | 194847.8726 | 40962.4867
May | 123760.3741 | 161.7384 | 692.2291 | 0 | 0.0019 | 236125.5023 | 49200.6333
June | 130193.1746 | 170.3674 | 731.3227 | 0 | 0.0021 | 249461.6711 | 51786.6281
July | 109460.516 | 143.0177 | 611.7882 | 0 | 0.0017 | 208686.2612 | 43511.5496
August | 115457.2174 | 150.5926 | 641.6607 | 0 | 0.0018 | 218874.8743 | 45861.7572
September | 115564.4512 | 151.1065 | 647.4947 | 0 | 0.0018 | 220866.5351 | 45952.56
October | 113307.215 | 147.7469 | 629.1315 | 0 | 0.0018 | 214600.9145 | 45002.3948
November | 104487.1055 | 135.397 | 568.2694 | 0 | 0.0016 | 193836.6723 | 41389.8791
December | 103363.2717 | 131.606 | 529.458 | 0 | 0.0015 | 180587.5604 | 40643.7567
Annual Sum or Average | 1330229.0811 | 1724.4501 | 7244.5413 | 0 | 0.0205 | 2471116.0052 | 527026.9938
Minimum of Months | 93816.7485 | 119.4185 | 480.1021 | 0 | 0.0014 | 163753.0895 | 36885.7479
Maximum of Months | 130193.1746 | 170.3674 | 731.3227 | 0 | 0.0021 | 249461.6711 | 51786.6281
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 416051000000 | 426992.449 | 03-JAN-11:50 | 84768.624 | 81262.495 | 71366.165 | 0 | 185752.861 | 0 | 0.923 | 0 | 0 | 0 | 0 | 0 | 3841.381 | 0 | 0
February | 362304000000 | 397391.488 | 21-FEB-11:39 | 84768.624 | 81262.495 | 71366.165 | 0 | 156151.565 | 0 | 1.163 | 0 | 0 | 0 | 0 | 0 | 3841.476 | 0 | 0
March | 445663000000 | 417158.889 | 24-MAR-11:00 | 84768.624 | 81262.495 | 71366.165 | 0 | 177145.021 | 0 | 0.897 | 0 | 0 | 0 | 0 | 0 | 2615.687 | 0 | 0
April | 431101000000 | 432983.682 | 10-APR-11:00 | 84768.624 | 81262.495 | 71366.165 | 0 | 192967.71 | 0 | 0.41 | 0 | 0 | 0 | 0 | 0 | 2618.277 | 0 | 0
May | 522428000000 | 489999.835 | 18-MAY-13:00 | 84768.624 | 77263.149 | 71368.169 | 0 | 253985.398 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 2614.494 | 0 | 0
June | 551934000000 | 479062.042 | 13-JUN-14:00 | 84768.624 | 75263.477 | 71416.428 | 0 | 245003.076 | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 | 2610.433 | 0 | 0
July | 461719000000 | 451944.356 | 18-JUL-11:00 | 47093.68 | 47274.638 | 71366.165 | 0 | 283717.568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2492.305 | 0 | 0
August | 484261000000 | 424480.644 | 31-AUG-10:00 | 47093.68 | 47274.638 | 71366.165 | 0 | 256255.042 | 0 | 1.465 | 0 | 0 | 0 | 0 | 0 | 2489.654 | 0 | 0
September | 488668000000 | 500961.804 | 15-SEP-13:00 | 84768.624 | 76410.953 | 71366.165 | 0 | 265797.902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2618.159 | 0 | 0
October | 474805000000 | 460967.147 | 30-OCT-12:00 | 84768.624 | 80410.298 | 71366.165 | 0 | 221804.848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2617.212 | 0 | 0
November | 428864000000 | 436575.302 | 27-NOV-12:00 | 84768.624 | 80410.298 | 71366.165 | 0 | 197414.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2615.845 | 0 | 0
December | 399550000000 | 409454.777 | 20-DEC-11:50 | 84768.624 | 80410.298 | 71366.165 | 0 | 169066.797 | 0 | 1.483 | 0 | 0 | 0 | 0 | 0 | 3841.41 | 0 | 0
Annual Sum or Average | 5467350000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 362304000000 | 397391.488 |  | 47093.68 | 47274.638 | 71366.165 | 0 | 156151.565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2489.654 | 0 | 0
Maximum of Months | 551934000000 | 500961.804 |  | 84768.624 | 81262.495 | 71416.428 | 0 | 283717.568 | 0 | 1.483 | 0 | 0 | 0 | 0 | 0 | 3841.476 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 181316.56 | 9211.2 | 0 | 190527.76
Cost per Total Building Area ($/m2) | 26.39 | 1.34 | 0 | 27.73
Cost per Net Conditioned Building Area ($/m2) | 26.39 | 1.34 | 0 | 27.73
3-phoenix
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 6548.37 | 953.04 | 953.04
Net Site Energy | 6548.37 | 953.04 | 953.04
Total Source Energy | 18490.26 | 2691.06 | 2691.06
Net Source Energy | 18490.26 | 2691.06 | 2691.06
Area (m2)
Total Building Area | 6871
Net Conditioned Building Area | 6871
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 655.96 | 0 | 0 | 0 | 0
Cooling | 1655.21 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1297.99 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 61.73 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1256.13 | 361.03 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1122.63 | 0 | 0 | 0 | 0 | 0
Pumps | 0.63 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 56.03 | 0 | 0 | 0 | 589.92
Refrigeration | 81.04 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5475.35 | 1073.02 | 0 | 0 | 0 | 589.92
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 5475.35 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 5475.35 | 100
Total On-Site and Utility Electric Sources | 5475.35 | 100
Total Electricity End Uses | 5475.35 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 162 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 546 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 171 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 252 | 90 | 0
BATH_ZN_1_FLR_1_WALL_5 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 190 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 441 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 168 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 399 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 4.2 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 4.2 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 4.2 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 49 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 25.2 | 6.88 | 0.25 | 0.25 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 26.6 | 6.88 | 0.25 | 0.25 | No | LOBBY_ZN_1_FLR_1_WALL_1
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 14 | 6.88 | 0.25 | 0.25 | No | BATH_ZN_1_FLR_1_WALL_5
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 29.4 | 6.88 | 0.25 | 0.25 | No | OFFICES_ZN_1_FLR_1_WALL_1
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 29.4 | 6.88 | 0.25 | 0.25 | No | OFFICES_ZN_1_FLR_1_WALL_2
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 23.8 | 6.88 | 0.25 | 0.25 | No | GYM_ZN_1_FLR_1_WALL_2
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 11.2 | 6.88 | 0.25 | 0.25 | No | KITCHEN_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 21 | 6.88 | 0.25 | 0.25 | No | CAFETERIA_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 29.4 | 6.88 | 0.25 | 0.25 | No | CAFETERIA_ZN_1_FLR_1_WALL_3
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 29.4 | 6.88 | 0.25 | 0.25 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 26.6 | 6.88 | 0.25 | 0.25 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
HEATSYS1 BOILER | Boiler:HotWater | 4112863.37 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 299129.09 | 3
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 238546.65 | 3
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 239832.83 | 3
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 324852.22 | 3
PSZ-AC_2:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 64179.95 | 3.69
PSZ-AC_1:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 85213.31 | 3.69
PSZ-AC_2:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 88158.55 | 3.69
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.67 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.02 | 0 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 2.26 | 0 | 1 | Zone Exhaust Fans
VAV_POD_1 FAN | Fan:VariableVolume | 0.28 | 655.15 | 18.07 | 42832.45 | 1 | Fan Energy
VAV_POD_2 FAN | Fan:VariableVolume | 0.28 | 655.15 | 14.41 | 34157.62 | 1 | Fan Energy
VAV_POD_3 FAN | Fan:VariableVolume | 0.28 | 655.15 | 14.49 | 34341.79 | 1 | Fan Energy
VAV_OTHER FAN | Fan:VariableVolume | 0.28 | 655.15 | 19.62 | 46515.76 | 1 | Fan Energy
PSZ-AC_2:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.8 | 5432.65 | 1 | General
PSZ-AC_1:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.7 | 5287.57 | 1 | General
PSZ-AC_2:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 4.43 | 6331.83 | 1 | General
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002391 | 109949.08 | 3892.67
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.007687 | 353462.93 | 12514.12
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001938 | 89098.44 | 3154.47
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002342 | 107683.59 | 3812.47
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.007017 | 322658.61 | 11423.51
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002386 | 109691.4 | 3883.55
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.007656 | 352017.3 | 12462.94
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001933 | 88861.43 | 3146.08
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002342 | 107698.85 | 3813.01
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.007018 | 322694.18 | 11424.77
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002386 | 109730.07 | 3884.92
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.007681 | 353169.13 | 12503.72
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001949 | 89623.86 | 3173.07
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002348 | 107980.39 | 3822.97
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004686 | 215465.97 | 7628.43
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002882 | 132503.77 | 4691.21
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004594 | 211232.37 | 7478.54
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00241 | 110814.2 | 3923.3
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002091 | 96129.92 | 3403.42
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002215 | 101856.02 | 3606.14
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005946 | 273400.51 | 9679.56
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005667 | 260558.84 | 9224.91
VAV_POD_1_HEATC | 0.0006 | 27565.27 | 453.3
VAV_POD_2_HEATC | 0.000538 | 24720.73 | 405.61
VAV_POD_3_HEATC | 0.000477 | 21953.73 | 361.06
VAV_OTHER_HEATC | 0.000268 | 12342.81 | 205.27
Nominal Capacity [W]
PSZ-AC_2:5_UNITARY_PACKAGE_HEATCOIL | 46183.18
PSZ-AC_1:6_UNITARY_PACKAGE_HEATCOIL | 101755.65
PSZ-AC_2:7_UNITARY_PACKAGE_HEATCOIL | 97473.68
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 84264.4695 | 134.877 | 422.7281 | 0 | 0.0012 | 3122304.6788 | 35068.4967
February | 76635.6712 | 123.4066 | 389.8142 | 0 | 0.0011 | 2879240.4029 | 31968.4943
March | 94287.638 | 155.1285 | 503.452 | 0 | 0.0014 | 3718768.9672 | 39665.3783
April | 87526.0933 | 145.4416 | 477.7486 | 0 | 0.0013 | 3528983.6199 | 36966.2778
May | 102117.4387 | 170.7171 | 564.8389 | 0 | 0.0015 | 4172345.188 | 43232.9498
June | 115101.3411 | 193.0696 | 641.3317 | 0 | 0.0017 | 4737413.4228 | 48795.2348
July | 99841.8671 | 167.2789 | 554.9001 | 0 | 0.0015 | 4098947.6744 | 42306.568
August | 102841.8924 | 172.1169 | 570.2111 | 0 | 0.0016 | 4212037.3938 | 43558.7388
September | 104339.0619 | 174.8144 | 579.8993 | 0 | 0.0016 | 4283612.0384 | 44212.2558
October | 95609.2923 | 159.0288 | 522.994 | 0 | 0.0014 | 3863205.3291 | 40395.9005
November | 88095.4601 | 144.556 | 467.6059 | 0 | 0.0013 | 3453970.0221 | 37021.5231
December | 84982.6925 | 135.2519 | 420.7272 | 0 | 0.0012 | 3107483.1265 | 35289.0643
Annual Sum or Average | 1135642.9183 | 1875.6873 | 6116.2513 | 0 | 0.0167 | 45178300 | 478480.8822
Minimum of Months | 76635.6712 | 123.4066 | 389.8142 | 0 | 0.0011 | 2879240.4029 | 31968.4943
Maximum of Months | 115101.3411 | 193.0696 | 641.3317 | 0 | 0.0017 | 4737413.4228 | 48795.2348
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 378405000000 | 358421.315 | 27-JAN-14:00 | 84768.624 | 77263.149 | 83124.264 | 0 | 110721.638 | 0 | 1.54 | 0 | 0 | 0 | 0 | 0 | 2542.099 | 0 | 0
February | 348947000000 | 368492.267 | 28-FEB-14:00 | 84768.624 | 77263.149 | 83124.264 | 0 | 120787.455 | 0 | 0.537 | 0 | 0 | 0 | 0 | 0 | 2548.237 | 0 | 0
March | 450693000000 | 403705.362 | 17-MAR-15:09 | 84768.624 | 75263.477 | 83124.264 | 0 | 158119.636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2429.36 | 0 | 0
April | 427692000000 | 416354.402 | 26-APR-13:00 | 84768.624 | 77263.149 | 83124.264 | 0 | 168644.969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2553.394 | 0 | 0
May | 505664000000 | 458756.216 | 30-MAY-13:00 | 84768.624 | 77263.149 | 83124.264 | 0 | 211004.895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2595.283 | 0 | 0
June | 574147000000 | 556451.362 | 08-JUN-14:00 | 84768.624 | 75263.477 | 84268.808 | 0 | 309623.498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2526.954 | 0 | 0
July | 496769000000 | 482717 | 11-JUL-15:00 | 47093.68 | 41275.62 | 83124.264 | 0 | 308745.775 | 0 | 0.012 | 0 | 0 | 0 | 0 | 0 | 2477.648 | 0 | 0
August | 510474000000 | 470256.186 | 01-AUG-15:00 | 47093.68 | 41275.62 | 83124.264 | 0 | 296291.955 | 0 | 0.016 | 0 | 0 | 0 | 0 | 0 | 2470.65 | 0 | 0
September | 519149000000 | 508036.597 | 25-SEP-13:00 | 84768.624 | 76410.953 | 83678.964 | 0 | 260576.127 | 0 | 0.016 | 0 | 0 | 0 | 0 | 0 | 2601.913 | 0 | 0
October | 468198000000 | 443321.277 | 03-OCT-09:30 | 84768.624 | 80410.298 | 83124.264 | 0 | 192395.166 | 0 | 7.986 | 0 | 0 | 0 | 0 | 0 | 2614.939 | 0 | 0
November | 418601000000 | 392235.406 | 13-NOV-14:00 | 84768.624 | 76410.953 | 83124.264 | 0 | 145340.333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2591.231 | 0 | 0
December | 376609000000 | 376150.825 | 13-DEC-12:39 | 84768.624 | 80410.298 | 83124.264 | 0 | 125283.11 | 0 | 14.441 | 0 | 0 | 0 | 0 | 0 | 2550.088 | 0 | 0
Annual Sum or Average | 5475350000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 348947000000 | 358421.315 |  | 47093.68 | 41275.62 | 83124.264 | 0 | 110721.638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2429.36 | 0 | 0
Maximum of Months | 574147000000 | 556451.362 |  | 84768.624 | 80410.298 | 84268.808 | 0 | 309623.498 | 0 | 14.441 | 0 | 0 | 0 | 0 | 0 | 2614.939 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 135299.91 | 9014.29 | 0 | 144314.2
Cost per Total Building Area ($/m2) | 19.69 | 1.31 | 0 | 21
Cost per Net Conditioned Building Area ($/m2) | 19.69 | 1.31 | 0 | 21
4-atlanta
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 6293.09 | 915.89 | 915.89
Net Site Energy | 6293.09 | 915.89 | 915.89
Total Source Energy | 17855.62 | 2598.69 | 2598.69
Net Source Energy | 17855.62 | 2598.69 | 2598.69
Area (m2)
Total Building Area | 6871
Net Conditioned Building Area | 6871
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 1021.99 | 0 | 0 | 0 | 0
Cooling | 1207 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1297.99 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 61.72 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1256.13 | 361.03 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 929.59 | 0 | 0 | 0 | 0 | 0
Pumps | 0.87 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 75.75 | 0 | 0 | 0 | 589.92
Refrigeration | 81.02 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 4834.32 | 1458.78 | 0 | 0 | 0 | 589.92
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 4834.32 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 4834.32 | 100
Total On-Site and Utility Electric Sources | 4834.32 | 100
Total Electricity End Uses | 4834.32 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 162 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 546 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 171 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 252 | 90 | 0
BATH_ZN_1_FLR_1_WALL_5 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 190 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 441 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 168 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 399 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 4.2 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 4.2 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 4.2 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 49 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 25.2 | 3.24 | 0.25 | 0.318 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 26.6 | 3.24 | 0.25 | 0.318 | No | LOBBY_ZN_1_FLR_1_WALL_1
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 14 | 3.24 | 0.25 | 0.318 | No | BATH_ZN_1_FLR_1_WALL_5
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 29.4 | 3.24 | 0.25 | 0.318 | No | OFFICES_ZN_1_FLR_1_WALL_1
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 29.4 | 3.24 | 0.25 | 0.318 | No | OFFICES_ZN_1_FLR_1_WALL_2
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 23.8 | 3.24 | 0.25 | 0.318 | No | GYM_ZN_1_FLR_1_WALL_2
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 11.2 | 3.24 | 0.25 | 0.318 | No | KITCHEN_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 21 | 3.24 | 0.25 | 0.318 | No | CAFETERIA_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 29.4 | 3.24 | 0.25 | 0.318 | No | CAFETERIA_ZN_1_FLR_1_WALL_3
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 29.4 | 3.24 | 0.25 | 0.318 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 26.6 | 3.24 | 0.25 | 0.318 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
HEATSYS1 BOILER | Boiler:HotWater | 3424531.64 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 235204.81 | 3
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 187871.21 | 3
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 189233.81 | 3
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 264550.05 | 3
PSZ-AC_2:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 65403.95 | 3.69
PSZ-AC_1:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 86970.34 | 3.69
PSZ-AC_2:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 90697.19 | 3.69
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.67 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.02 | 0 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 2.26 | 0 | 1 | Zone Exhaust Fans
VAV_POD_1 FAN | Fan:VariableVolume | 0.28 | 655.15 | 14.21 | 33679.1 | 1 | Fan Energy
VAV_POD_2 FAN | Fan:VariableVolume | 0.28 | 655.15 | 11.35 | 26901.38 | 1 | Fan Energy
VAV_POD_3 FAN | Fan:VariableVolume | 0.28 | 655.15 | 11.43 | 27096.49 | 1 | Fan Energy
VAV_OTHER FAN | Fan:VariableVolume | 0.28 | 655.15 | 15.98 | 37881.06 | 1 | Fan Energy
PSZ-AC_2:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.26 | 4663.84 | 1 | General
PSZ-AC_1:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.5 | 5003.28 | 1 | General
PSZ-AC_2:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.65 | 5217.68 | 1 | General
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001852 | 85156.08 | 3014.89
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006153 | 282896 | 10015.74
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001624 | 74658.29 | 2643.23
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001806 | 83017.51 | 2939.18
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005466 | 251330.64 | 8898.19
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001837 | 84473.58 | 2990.73
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006074 | 279290.65 | 9888.1
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001616 | 74325.97 | 2631.46
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001806 | 83054.96 | 2940.51
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005469 | 251482.17 | 8903.56
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001839 | 84544.48 | 2993.24
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006097 | 280317.35 | 9924.45
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001634 | 75142.62 | 2660.37
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00182 | 83670.06 | 2962.28
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003686 | 169470.31 | 5999.98
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002342 | 107674.31 | 3812.14
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004002 | 183994.35 | 6514.2
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001856 | 85355.89 | 3021.97
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001903 | 87487.54 | 3097.44
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001829 | 84081.35 | 2976.84
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004692 | 215728.78 | 7637.73
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004452 | 204698.58 | 7247.22
VAV_POD_1_HEATC | 0.001399 | 64342.46 | 1013.41
VAV_POD_2_HEATC | 0.001209 | 55577.21 | 866.79
VAV_POD_3_HEATC | 0.001116 | 51297.6 | 808.85
VAV_OTHER_HEATC | 0.000902 | 41462.88 | 673.77
Nominal Capacity [W]
PSZ-AC_2:5_UNITARY_PACKAGE_HEATCOIL | 59049.47
PSZ-AC_1:6_UNITARY_PACKAGE_HEATCOIL | 130104.02
PSZ-AC_2:7_UNITARY_PACKAGE_HEATCOIL | 124629.12
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 89435.0536 | 155.5384 | 364.8951 | 0 | 0.0014 | 648923.0908 | 37820.8201
February | 77346.2828 | 136.1947 | 323.8087 | 0 | 0.0012 | 575874.2014 | 32863.808
March | 83787.9324 | 155.2597 | 388.6317 | 0 | 0.0014 | 691240.7693 | 36313.9865
April | 79389.6566 | 149.7739 | 381.2917 | 0 | 0.0014 | 678211.267 | 34653.8109
May | 89840.0248 | 170.7022 | 437.4287 | 0 | 0.0016 | 778074.6126 | 39327.448
June | 95694.8362 | 182.7638 | 470.5291 | 0 | 0.0017 | 836960.5408 | 41976.9301
July | 79834.6171 | 151.3756 | 387.1652 | 0 | 0.0014 | 688665.7652 | 34918.4311
August | 86013.776 | 162.8068 | 415.7337 | 0 | 0.0015 | 739478.9712 | 37594.7638
September | 89838.7187 | 171.271 | 440.2228 | 0 | 0.0016 | 783049.8671 | 39379.6356
October | 82744.501 | 155.9596 | 396.7011 | 0 | 0.0015 | 705618.9513 | 36104.9621
November | 78879.6455 | 144.7416 | 358.8904 | 0 | 0.0013 | 638327.6237 | 34055.3068
December | 82021.4713 | 145.4817 | 348.5516 | 0 | 0.0013 | 619889.3251 | 34947.6648
Annual Sum or Average | 1014826.5161 | 1881.8689 | 4713.8497 | 0 | 0.0174 | 8384314.9857 | 439957.5677
Minimum of Months | 77346.2828 | 136.1947 | 323.8087 | 0 | 0.0012 | 575874.2014 | 32863.808
Maximum of Months | 95694.8362 | 182.7638 | 470.5291 | 0 | 0.0017 | 836960.5408 | 41976.9301
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 374163000000 | 317010.231 | 24-JAN-14:00 | 84768.624 | 77263.149 | 67457.251 | 0 | 84883.524 | 0 | 26.788 | 0 | 0 | 0 | 0 | 0 | 2610.896 | 0 | 0
February | 332044000000 | 322453.427 | 21-FEB-14:09 | 84768.624 | 77263.149 | 67457.251 | 0 | 90339.928 | 0 | 14.25 | 0 | 0 | 0 | 0 | 0 | 2610.224 | 0 | 0
March | 398563000000 | 344392.652 | 28-MAR-11:00 | 84768.624 | 81262.495 | 67457.251 | 0 | 108294.119 | 0 | 2.754 | 0 | 0 | 0 | 0 | 0 | 2607.409 | 0 | 0
April | 391050000000 | 383506.631 | 13-APR-13:00 | 84768.624 | 77263.149 | 67457.251 | 0 | 151409.436 | 0 | 0.006 | 0 | 0 | 0 | 0 | 0 | 2608.164 | 0 | 0
May | 448630000000 | 414636.023 | 22-MAY-13:00 | 84768.624 | 77263.149 | 67457.251 | 0 | 182534.16 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 2612.838 | 0 | 0
June | 482584000000 | 438196.272 | 08-JUN-14:00 | 84768.624 | 75263.477 | 67457.251 | 0 | 208093.492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2613.428 | 0 | 0
July | 397078000000 | 403569.671 | 03-JUL-11:00 | 47093.68 | 47274.638 | 67457.251 | 0 | 239256.102 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 2487.999 | 0 | 0
August | 426377000000 | 379879.497 | 17-AUG-11:00 | 47093.68 | 47274.638 | 67457.251 | 0 | 215562.564 | 0 | 3.228 | 0 | 0 | 0 | 0 | 0 | 2488.136 | 0 | 0
September | 451499000000 | 426881.724 | 11-SEP-13:00 | 84768.624 | 76410.953 | 67457.251 | 0 | 195632.631 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 2612.263 | 0 | 0
October | 406853000000 | 390907.225 | 12-OCT-15:00 | 84768.624 | 75197.923 | 67457.251 | 0 | 160882.307 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 2601.115 | 0 | 0
November | 368054000000 | 346666.521 | 22-NOV-12:00 | 84768.624 | 80410.298 | 67457.251 | 0 | 111463.941 | 0 | 2.659 | 0 | 0 | 0 | 0 | 0 | 2563.748 | 0 | 0
December | 357422000000 | 336826.662 | 26-DEC-14:00 | 84768.624 | 76410.953 | 67457.251 | 0 | 105560.304 | 0 | 15.87 | 0 | 0 | 0 | 0 | 0 | 2613.66 | 0 | 0
Annual Sum or Average | 4834320000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 332044000000 | 317010.231 |  | 47093.68 | 47274.638 | 67457.251 | 0 | 84883.524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2487.999 | 0 | 0
Maximum of Months | 482584000000 | 438196.272 |  | 84768.624 | 81262.495 | 67457.251 | 0 | 239256.102 | 0 | 26.788 | 0 | 0 | 0 | 0 | 0 | 2613.66 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 130922.3 | 14683.52 | 0 | 145605.82
Cost per Total Building Area ($/m2) | 19.05 | 2.14 | 0 | 21.19
Cost per Net Conditioned Building Area ($/m2) | 19.05 | 2.14 | 0 | 21.19
5-losangeles
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 5143.6 | 748.6 | 748.6
Net Site Energy | 5143.6 | 748.6 | 748.6
Total Source Energy | 14348.63 | 2088.29 | 2088.29
Net Source Energy | 14348.63 | 2088.29 | 2088.29
Area (m2)
Total Building Area | 6871
Net Conditioned Building Area | 6871
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 351.81 | 0 | 0 | 0 | 0
Cooling | 902.97 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1297.99 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 61.67 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1256.13 | 361.03 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 758.55 | 0 | 0 | 0 | 0 | 0
Pumps | 0.35 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 71.4 | 0 | 0 | 0 | 589.92
Refrigeration | 81.71 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 4359.37 | 784.23 | 0 | 0 | 0 | 589.92
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 4359.37 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 4359.37 | 100
Total On-Site and Utility Electric Sources | 4359.37 | 100
Total Electricity End Uses | 4359.37 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 162 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 546 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 171 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 252 | 90 | 0
BATH_ZN_1_FLR_1_WALL_5 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 190 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 441 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 168 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 399 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 4.2 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 4.2 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 4.2 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 49 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 25.2 | 3.24 | 0.25 | 0.318 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 26.6 | 3.24 | 0.25 | 0.318 | No | LOBBY_ZN_1_FLR_1_WALL_1
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 14 | 3.24 | 0.25 | 0.318 | No | BATH_ZN_1_FLR_1_WALL_5
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 29.4 | 3.24 | 0.25 | 0.318 | No | OFFICES_ZN_1_FLR_1_WALL_1
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 29.4 | 3.24 | 0.25 | 0.318 | No | OFFICES_ZN_1_FLR_1_WALL_2
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 23.8 | 3.24 | 0.25 | 0.318 | No | GYM_ZN_1_FLR_1_WALL_2
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 11.2 | 3.24 | 0.25 | 0.318 | No | KITCHEN_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 21 | 3.24 | 0.25 | 0.318 | No | CAFETERIA_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 29.4 | 3.24 | 0.25 | 0.318 | No | CAFETERIA_ZN_1_FLR_1_WALL_3
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 29.4 | 3.24 | 0.25 | 0.318 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 26.6 | 3.24 | 0.25 | 0.318 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
HEATSYS1 BOILER | Boiler:HotWater | 2998787.24 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 208092.87 | 3
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 163512.9 | 3
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 168008.74 | 3
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 230449.1 | 3
PSZ-AC_2:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 46442.34 | 3.69
PSZ-AC_1:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 53485.69 | 3.69
PSZ-AC_2:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 50068.44 | 3.69
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.67 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.02 | 0 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 2.26 | 0 | 1 | Zone Exhaust Fans
VAV_POD_1 FAN | Fan:VariableVolume | 0.28 | 655.15 | 12.57 | 29796.93 | 1 | Fan Energy
VAV_POD_2 FAN | Fan:VariableVolume | 0.28 | 655.15 | 9.88 | 23413.5 | 1 | Fan Energy
VAV_POD_3 FAN | Fan:VariableVolume | 0.28 | 655.15 | 10.15 | 24057.26 | 1 | Fan Energy
VAV_OTHER FAN | Fan:VariableVolume | 0.28 | 655.15 | 13.92 | 32998.13 | 1 | Fan Energy
PSZ-AC_2:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 2.81 | 4007.97 | 1 | General
PSZ-AC_1:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.23 | 4615.82 | 1 | General
PSZ-AC_2:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.02 | 4320.91 | 1 | General
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001797 | 82630.49 | 2925.48
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006013 | 276497.53 | 9789.21
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001472 | 67675.58 | 2396.01
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001569 | 72159.25 | 2554.75
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00451 | 207370.56 | 7341.82
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001783 | 82002.93 | 2903.26
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005924 | 272391.7 | 9643.85
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001465 | 67346.86 | 2384.37
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00157 | 72193.8 | 2555.97
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004513 | 207517.81 | 7347.03
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001785 | 82068.58 | 2905.58
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005944 | 273308.39 | 9676.3
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001481 | 68114.33 | 2411.54
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001582 | 72756.92 | 2575.91
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00305 | 140233.91 | 4964.89
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002049 | 94216.7 | 3335.68
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003613 | 166121.02 | 5881.4
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001805 | 82972.54 | 2937.59
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001735 | 79781.48 | 2824.61
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001645 | 75636.37 | 2677.85
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004307 | 198046.03 | 7011.69
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003833 | 176256.24 | 6240.23
VAV_POD_1_HEATC | 0.000556 | 25552.68 | 418.04
VAV_POD_2_HEATC | 0.000497 | 22865.95 | 372.93
VAV_POD_3_HEATC | 0.000441 | 20256.33 | 331.53
VAV_OTHER_HEATC | 0.000279 | 12813.27 | 212.38
Nominal Capacity [W]
PSZ-AC_2:5_UNITARY_PACKAGE_HEATCOIL | 43125.13
PSZ-AC_1:6_UNITARY_PACKAGE_HEATCOIL | 95017.83
PSZ-AC_2:7_UNITARY_PACKAGE_HEATCOIL | 91019.4
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 34687.1142 | 29.938 | 278.1071 | 0 | 0.0001 | 1677903.1383 | 12853.7622
February | 30894.8143 | 26.6474 | 250.8492 | 0 | 0.0001 | 1513460.4747 | 11458.0782
March | 36338.174 | 31.3073 | 301.3167 | 0 | 0.0001 | 1817972.1928 | 13496.0083
April | 33485.3547 | 28.8082 | 285.0503 | 0 | 0.0001 | 1719857.7607 | 12459.0147
May | 37392.6306 | 32.1409 | 323.4674 | 0 | 0.0002 | 1951667.5566 | 13928.5387
June | 37494.2815 | 32.2163 | 326.4786 | 0 | 0.0002 | 1969843.1898 | 13972.9071
July | 31194.6187 | 26.878 | 258.2769 | 0 | 0.0001 | 1558293.2251 | 11584.5025
August | 34726.9035 | 29.9133 | 288.992 | 0 | 0.0001 | 1743615.8883 | 12900.7427
September | 36314.5557 | 31.1976 | 317.1132 | 0 | 0.0001 | 1913339.4225 | 13536.0286
October | 36865.0567 | 31.6833 | 319.6422 | 0 | 0.0001 | 1928590.3162 | 13734.2738
November | 35368.0893 | 30.4486 | 297.3838 | 0 | 0.0001 | 1794259.1549 | 13148.2615
December | 33923.4766 | 29.2497 | 277.2109 | 0 | 0.0001 | 1672516.5908 | 12586.7318
Annual Sum or Average | 418685.0698 | 360.4286 | 3523.8882 | 0 | 0.0017 | 21261300 | 155658.8502
Minimum of Months | 30894.8143 | 26.6474 | 250.8492 | 0 | 0.0001 | 1513460.4747 | 11458.0782
Maximum of Months | 37494.2815 | 32.2163 | 326.4786 | 0 | 0.0002 | 1969843.1898 | 13972.9071
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 344033000000 | 325747.127 | 26-JAN-12:00 | 84768.624 | 81262.495 | 59123.72 | 0 | 98086.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2505.478 | 0 | 0
February | 310316000000 | 323852.199 | 13-FEB-11:50 | 84768.624 | 81262.495 | 59123.72 | 0 | 94855.357 | 0 | 0.366 | 0 | 0 | 0 | 0 | 0 | 3841.637 | 0 | 0
March | 372753000000 | 317736.256 | 31-MAR-10:50 | 84768.624 | 81262.495 | 59123.72 | 0 | 88832.216 | 0 | 0.648 | 0 | 0 | 0 | 0 | 0 | 3748.553 | 0 | 0
April | 352635000000 | 343119.026 | 11-APR-13:50 | 84768.624 | 77263.149 | 59123.72 | 0 | 119353.293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2610.239 | 0 | 0
May | 400165000000 | 366492.954 | 30-MAY-12:00 | 84768.624 | 77263.149 | 59123.72 | 0 | 142724.571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2612.889 | 0 | 0
June | 403892000000 | 352283.75 | 23-JUN-10:50 | 84768.624 | 81262.495 | 59123.72 | 0 | 123285.877 | 0 | 1.526 | 0 | 0 | 0 | 0 | 0 | 3841.509 | 0 | 0
July | 319509000000 | 284114.377 | 10-JUL-09:00 | 47093.68 | 47274.638 | 59123.72 | 0 | 128127.134 | 0 | 10.703 | 0 | 0 | 0 | 0 | 0 | 2484.501 | 0 | 0
August | 357507000000 | 309257.093 | 08-AUG-09:00 | 47093.68 | 47274.638 | 59123.72 | 0 | 153268.608 | 0 | 8.886 | 0 | 0 | 0 | 0 | 0 | 2487.561 | 0 | 0
September | 392306000000 | 368365.386 | 25-SEP-14:00 | 84768.624 | 74411.28 | 59944.607 | 0 | 146635.76 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 2605.111 | 0 | 0
October | 395433000000 | 353374.668 | 05-OCT-10:50 | 84768.624 | 80410.298 | 59123.72 | 0 | 125230.274 | 0 | 0.256 | 0 | 0 | 0 | 0 | 0 | 3841.497 | 0 | 0
November | 367891000000 | 336543.335 | 07-NOV-12:00 | 84768.624 | 80410.298 | 59123.72 | 0 | 109631.101 | 0 | 0.141 | 0 | 0 | 0 | 0 | 0 | 2609.451 | 0 | 0
December | 342929000000 | 327481.189 | 19-DEC-12:00 | 84768.624 | 80410.298 | 59123.72 | 0 | 100676.963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2501.584 | 0 | 0
Annual Sum or Average | 4359370000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 310316000000 | 284114.377 |  | 47093.68 | 47274.638 | 59123.72 | 0 | 88832.216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2484.501 | 0 | 0
Maximum of Months | 403892000000 | 368365.386 |  | 84768.624 | 81262.495 | 59944.607 | 0 | 153268.608 | 0 | 10.703 | 0 | 0 | 0 | 0 | 0 | 3841.637 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 156161.35 | 6642.81 | 0 | 162804.15
Cost per Total Building Area ($/m2) | 22.73 | 0.97 | 0 | 23.69
Cost per Net Conditioned Building Area ($/m2) | 22.73 | 0.97 | 0 | 23.69
6-lasvegas
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 6072.93 | 883.85 | 883.85
Net Site Energy | 6072.93 | 883.85 | 883.85
Total Source Energy | 19028.84 | 2769.44 | 2769.44
Net Source Energy | 19028.84 | 2769.44 | 2769.44
Area (m2)
Total Building Area | 6871
Net Conditioned Building Area | 6871
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 657.5 | 0 | 0 | 0 | 0
Cooling | 1227.2 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1297.99 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 61.66 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1256.13 | 361.03 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1064.91 | 0 | 0 | 0 | 0 | 0
Pumps | 0.63 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 65.58 | 0 | 0 | 0 | 589.92
Refrigeration | 80.3 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 4988.81 | 1084.11 | 0 | 0 | 0 | 589.92
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 4988.81 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 4988.81 | 100
Total On-Site and Utility Electric Sources | 4988.81 | 100
Total Electricity End Uses | 4988.81 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 162 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 546 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 171 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 252 | 90 | 0
BATH_ZN_1_FLR_1_WALL_5 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 190 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 441 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 168 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 399 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 4.2 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 4.2 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 4.2 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 49 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 25.2 | 3.24 | 0.25 | 0.318 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 26.6 | 3.24 | 0.25 | 0.318 | No | LOBBY_ZN_1_FLR_1_WALL_1
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 14 | 3.24 | 0.25 | 0.318 | No | BATH_ZN_1_FLR_1_WALL_5
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 29.4 | 3.24 | 0.25 | 0.318 | No | OFFICES_ZN_1_FLR_1_WALL_1
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 29.4 | 3.24 | 0.25 | 0.318 | No | OFFICES_ZN_1_FLR_1_WALL_2
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 23.8 | 3.24 | 0.25 | 0.318 | No | GYM_ZN_1_FLR_1_WALL_2
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 11.2 | 3.24 | 0.25 | 0.318 | No | KITCHEN_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 21 | 3.24 | 0.25 | 0.318 | No | CAFETERIA_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 29.4 | 3.24 | 0.25 | 0.318 | No | CAFETERIA_ZN_1_FLR_1_WALL_3
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 29.4 | 3.24 | 0.25 | 0.318 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 26.6 | 3.24 | 0.25 | 0.318 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
HEATSYS1 BOILER | Boiler:HotWater | 3792059.11 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 280917.84 | 3
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 224216.19 | 3
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 225478.62 | 3
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 310690.29 | 3
PSZ-AC_2:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 61313.94 | 3.69
PSZ-AC_1:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 71656.73 | 3.69
PSZ-AC_2:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 71886.05 | 3.69
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.67 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.02 | 0 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 2.26 | 0 | 1 | Zone Exhaust Fans
VAV_POD_1 FAN | Fan:VariableVolume | 0.28 | 655.15 | 16.97 | 40224.77 | 1 | Fan Energy
VAV_POD_2 FAN | Fan:VariableVolume | 0.28 | 655.15 | 13.54 | 32105.63 | 1 | Fan Energy
VAV_POD_3 FAN | Fan:VariableVolume | 0.28 | 655.15 | 13.62 | 32286.4 | 1 | Fan Energy
VAV_OTHER FAN | Fan:VariableVolume | 0.28 | 655.15 | 18.77 | 44487.9 | 1 | Fan Energy
PSZ-AC_2:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.7 | 5291.39 | 1 | General
PSZ-AC_1:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.72 | 5315.63 | 1 | General
PSZ-AC_2:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 4.15 | 5930.81 | 1 | General
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002131 | 97972.47 | 3468.65
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006978 | 320836.69 | 11359.01
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00181 | 83215.45 | 2946.19
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002101 | 96590.17 | 3419.71
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006325 | 290825.79 | 10296.49
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002118 | 97369.78 | 3447.31
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006898 | 317164.66 | 11229
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001802 | 82878.8 | 2934.27
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002101 | 96623.27 | 3420.88
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006328 | 290961.62 | 10301.3
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002119 | 97433.94 | 3449.58
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006922 | 318258.99 | 11267.75
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00182 | 83689.39 | 2962.97
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002114 | 97184.61 | 3440.76
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004252 | 195496.1 | 6921.41
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002658 | 122228.11 | 4327.4
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004414 | 202963.19 | 7185.78
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002152 | 98953.65 | 3503.39
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00205 | 94274.59 | 3337.73
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00205 | 94248.57 | 3336.81
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005321 | 244657.87 | 8661.95
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005091 | 234069.25 | 8287.06
VAV_POD_1_HEATC | 0.000902 | 41458.61 | 673.99
VAV_POD_2_HEATC | 0.000791 | 36348.11 | 589.34
VAV_POD_3_HEATC | 0.000719 | 33041.11 | 537.25
VAV_OTHER_HEATC | 0.000507 | 23314.34 | 384.49
Nominal Capacity [W]
PSZ-AC_2:5_UNITARY_PACKAGE_HEATCOIL | 49925.23
PSZ-AC_1:6_UNITARY_PACKAGE_HEATCOIL | 110000.52
PSZ-AC_2:7_UNITARY_PACKAGE_HEATCOIL | 105371.6
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 91248.2843 | 141.134 | 548.3777 | 0 | 0.0011 | 2734612.0972 | 37641.4082
February | 79079.2551 | 125.162 | 502.0325 | 0 | 0.001 | 2503615.3574 | 32917.7006
March | 94196.8618 | 149.761 | 604.3196 | 0 | 0.0011 | 3013742.2009 | 39280.4012
April | 91680.6815 | 148.0607 | 609.7971 | 0 | 0.0011 | 3041145.3878 | 38470.2218
May | 105497.2305 | 171.238 | 709.8167 | 0 | 0.0013 | 3539988.682 | 44357.6039
June | 117836.1531 | 191.8667 | 798.4833 | 0 | 0.0015 | 3982206.7873 | 49608.0954
July | 99988.048 | 162.6719 | 676.285 | 0 | 0.0013 | 3372773.1134 | 42080.2983
August | 105810.7987 | 171.8517 | 712.9107 | 0 | 0.0013 | 3555422.6157 | 44500.3307
September | 105088.3586 | 170.9226 | 710.339 | 0 | 0.0013 | 3542606.0336 | 44221.8853
October | 98450.3557 | 159.1093 | 655.9128 | 0 | 0.0012 | 3271134.8763 | 41322.8871
November | 88312.7449 | 140.2364 | 564.9758 | 0 | 0.0011 | 2817528.2258 | 36809.0755
December | 86311.4172 | 134.6939 | 529.9486 | 0 | 0.001 | 2642758.921 | 35729.1633
Annual Sum or Average | 1163500.1894 | 1866.7081 | 7623.1989 | 0 | 0.0144 | 38017500 | 486939.0714
Minimum of Months | 79079.2551 | 125.162 | 502.0325 | 0 | 0.001 | 2503615.3574 | 32917.7006
Maximum of Months | 117836.1531 | 191.8667 | 798.4833 | 0 | 0.0015 | 3982206.7873 | 49608.0954
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 358847000000 | 329213.729 | 18-JAN-14:00 | 84768.624 | 77263.149 | 78954.783 | 0 | 85675.477 | 0 | 4.11 | 0 | 0 | 0 | 0 | 0 | 2547.585 | 0 | 0
February | 328535000000 | 336371.975 | 08-FEB-14:00 | 84768.624 | 77263.149 | 78954.783 | 0 | 92842.682 | 0 | 1.962 | 0 | 0 | 0 | 0 | 0 | 2540.775 | 0 | 0
March | 395475000000 | 351463.509 | 31-MAR-13:00 | 84768.624 | 77263.149 | 78954.783 | 0 | 107932.015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2544.937 | 0 | 0
April | 399071000000 | 399577.479 | 21-APR-14:00 | 84768.624 | 75263.477 | 78998.722 | 0 | 158006.828 | 0 | 0.008 | 0 | 0 | 0 | 0 | 0 | 2539.821 | 0 | 0
May | 464532000000 | 429313.433 | 31-MAY-15:00 | 84768.624 | 75263.477 | 78954.783 | 0 | 187906.354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2420.195 | 0 | 0
June | 522561000000 | 512060.043 | 27-JUN-15:00 | 84768.624 | 75263.477 | 79069.331 | 0 | 270371.678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2586.933 | 0 | 0
July | 442589000000 | 417278.953 | 24-JUL-15:00 | 47093.68 | 41275.62 | 78954.783 | 0 | 247494.084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2460.785 | 0 | 0
August | 466557000000 | 416573.679 | 03-AUG-11:00 | 47093.68 | 47274.638 | 78954.783 | 0 | 240769.221 | 0 | 0.013 | 0 | 0 | 0 | 0 | 0 | 2481.344 | 0 | 0
September | 464875000000 | 433134.478 | 21-SEP-13:00 | 84768.624 | 76410.953 | 79358.595 | 0 | 190055.691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2540.615 | 0 | 0
October | 429252000000 | 412048.283 | 06-OCT-12:00 | 84768.624 | 76410.953 | 78954.783 | 0 | 169341.957 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0 | 2571.962 | 0 | 0
November | 369727000000 | 344537.324 | 10-NOV-12:00 | 84768.624 | 80410.298 | 78954.783 | 0 | 97895.878 | 0 | 2.822 | 0 | 0 | 0 | 0 | 0 | 2504.919 | 0 | 0
December | 346793000000 | 339520.198 | 05-DEC-12:00 | 84768.624 | 80410.298 | 78954.783 | 0 | 92886.068 | 0 | 8.97 | 0 | 0 | 0 | 0 | 0 | 2491.455 | 0 | 0
Annual Sum or Average | 4988810000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 328535000000 | 329213.729 |  | 47093.68 | 41275.62 | 78954.783 | 0 | 85675.477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2420.195 | 0 | 0
Maximum of Months | 522561000000 | 512060.043 |  | 84768.624 | 80410.298 | 79358.595 | 0 | 270371.678 | 0 | 8.97 | 0 | 0 | 0 | 0 | 0 | 2586.933 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 137520.17 | 8570.87 | 0 | 146091.04
Cost per Total Building Area ($/m2) | 20.01 | 1.25 | 0 | 21.26
Cost per Net Conditioned Building Area ($/m2) | 20.01 | 1.25 | 0 | 21.26
7-sanfrancisco
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 6974.35 | 1015.04 | 1015.04
Net Site Energy | 6974.35 | 1015.04 | 1015.04
Total Source Energy | 17020.18 | 2477.1 | 2477.1
Net Source Energy | 17020.18 | 2477.1 | 2477.1
Area (m2)
Total Building Area | 6871
Net Conditioned Building Area | 6871
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 1835.83 | 0 | 0 | 0 | 0
Cooling | 799.36 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1297.99 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 61.69 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1256.13 | 361.03 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1197.78 | 0 | 0 | 0 | 0 | 0
Pumps | 1.78 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 82.43 | 0 | 0 | 0 | 589.92
Refrigeration | 80.33 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 4695.06 | 2279.29 | 0 | 0 | 0 | 589.92
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 4695.06 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 4695.06 | 100
Total On-Site and Utility Electric Sources | 4695.06 | 100
Total Electricity End Uses | 4695.06 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 162 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 546 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 171 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 252 | 90 | 0
BATH_ZN_1_FLR_1_WALL_5 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 190 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 441 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 168 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 399 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 15.4 | 6.88 | 0.34 | 0.34 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 12.6 | 6.88 | 0.34 | 0.34 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 74.2 | 6.88 | 0.34 | 0.34 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 4.2 | 6.88 | 0.34 | 0.34 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_NORTH | 15.4 | 6.88 | 0.34 | 0.34 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 12.6 | 6.88 | 0.34 | 0.34 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_NORTH | 74.2 | 6.88 | 0.34 | 0.34 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 15.4 | 6.88 | 0.34 | 0.34 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 12.6 | 6.88 | 0.34 | 0.34 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 74.2 | 6.88 | 0.34 | 0.34 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 4.2 | 6.88 | 0.34 | 0.34 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_NORTH | 15.4 | 6.88 | 0.34 | 0.34 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 12.6 | 6.88 | 0.34 | 0.34 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_NORTH | 74.2 | 6.88 | 0.34 | 0.34 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 15.4 | 6.88 | 0.34 | 0.34 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 12.6 | 6.88 | 0.34 | 0.34 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 74.2 | 6.88 | 0.34 | 0.34 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 4.2 | 6.88 | 0.34 | 0.34 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_NORTH | 15.4 | 6.88 | 0.34 | 0.34 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 12.6 | 6.88 | 0.34 | 0.34 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_NORTH | 49 | 6.88 | 0.34 | 0.34 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_NORTH | 25.2 | 6.88 | 0.34 | 0.34 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 12.6 | 6.88 | 0.34 | 0.34 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 26.6 | 6.88 | 0.34 | 0.34 | No | LOBBY_ZN_1_FLR_1_WALL_1
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 14 | 6.88 | 0.34 | 0.34 | No | BATH_ZN_1_FLR_1_WALL_5
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 29.4 | 6.88 | 0.34 | 0.34 | No | OFFICES_ZN_1_FLR_1_WALL_1
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_EAST | 29.4 | 6.88 | 0.34 | 0.34 | No | OFFICES_ZN_1_FLR_1_WALL_2
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_EAST | 23.8 | 6.88 | 0.34 | 0.34 | No | GYM_ZN_1_FLR_1_WALL_2
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_1_CEILING
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_EAST | 11.2 | 6.88 | 0.34 | 0.34 | No | KITCHEN_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_EAST | 21 | 6.88 | 0.34 | 0.34 | No | CAFETERIA_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_NORTH | 29.4 | 6.88 | 0.34 | 0.34 | No | CAFETERIA_ZN_1_FLR_1_WALL_3
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_EAST | 29.4 | 6.88 | 0.34 | 0.34 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_NORTH | 26.6 | 6.88 | 0.34 | 0.34 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
HEATSYS1 BOILER | Boiler:HotWater | 4671846.52 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 342582.92 | 3
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 272803.13 | 3
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 276761.91 | 3
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 316896.41 | 3
PSZ-AC_2:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 67211.48 | 3.69
PSZ-AC_1:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 65384.93 | 3.69
PSZ-AC_2:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 91190.74 | 3.69
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.67 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.02 | 0 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 2.26 | 0 | 1 | Zone Exhaust Fans
VAV_POD_1 FAN | Fan:VariableVolume | 0.28 | 655.15 | 20.7 | 49054.63 | 1 | Fan Energy
VAV_POD_2 FAN | Fan:VariableVolume | 0.28 | 655.15 | 16.48 | 39062.82 | 1 | Fan Energy
VAV_POD_3 FAN | Fan:VariableVolume | 0.28 | 655.15 | 16.72 | 39629.68 | 1 | Fan Energy
VAV_OTHER FAN | Fan:VariableVolume | 0.28 | 655.15 | 19.14 | 45376.56 | 1 | Fan Energy
PSZ-AC_2:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 4.06 | 5800.35 | 1 | General
PSZ-AC_1:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.95 | 5642.72 | 1 | General
PSZ-AC_2:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 5.51 | 7869.76 | 1 | General
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002841 | 130644.6 | 4625.38
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.010499 | 482744.98 | 17091.26
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002103 | 96684.19 | 3423.04
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002311 | 106251.81 | 3761.77
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.007732 | 355502.4 | 12586.32
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002831 | 130171.68 | 4608.64
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.010408 | 478543.51 | 16942.51
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002096 | 96362.66 | 3411.66
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002311 | 106278.52 | 3762.72
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.007734 | 355614.15 | 12590.28
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002832 | 130225.55 | 4610.55
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.010435 | 479796.55 | 16986.88
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002112 | 97132.27 | 3438.9
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002321 | 106734.65 | 3778.87
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005175 | 237955.32 | 8424.65
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003012 | 138469.24 | 4902.41
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004378 | 201300.54 | 7126.91
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002482 | 114118.67 | 4040.3
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002285 | 105042.58 | 3718.96
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001877 | 86315.17 | 3055.93
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005784 | 265948.93 | 9415.74
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006376 | 293181.93 | 10379.91
VAV_POD_1_HEATC | 0.000514 | 23646.1 | 390.92
VAV_POD_2_HEATC | 0.000472 | 21696.47 | 357.92
VAV_POD_3_HEATC | 0.000405 | 18611.17 | 307.79
VAV_OTHER_HEATC | 0.00028 | 12872.85 | 214.04
Nominal Capacity [W]
PSZ-AC_2:5_UNITARY_PACKAGE_HEATCOIL | 47667.53
PSZ-AC_1:6_UNITARY_PACKAGE_HEATCOIL | 105026.11
PSZ-AC_2:7_UNITARY_PACKAGE_HEATCOIL | 100606.52
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 47013.0825 | 41.0169 | 298.1182 | 0 | 0.0002 | 1798330.8105 | 17180.8537
February | 39234.0884 | 34.0648 | 278.3558 | 0 | 0.0001 | 1679263.4426 | 14428.2365
March | 45967.3166 | 39.9593 | 317.4733 | 0 | 0.0002 | 1915213.3548 | 16877.964
April | 40856.2613 | 35.399 | 303.1521 | 0 | 0.0002 | 1828912.4343 | 15065.3257
May | 45233.2628 | 39.0933 | 353.1726 | 0 | 0.0002 | 2130758.965 | 16732.8238
June | 45376.6939 | 39.2271 | 352.5435 | 0 | 0.0002 | 2126956.5828 | 16780.5463
July | 40272.2338 | 35.0006 | 279.572 | 0 | 0.0001 | 1686573.9509 | 14791.2511
August | 45435.0174 | 39.5027 | 312.6981 | 0 | 0.0002 | 1886401.088 | 16679.1654
September | 43786.7963 | 37.8006 | 349.509 | 0 | 0.0002 | 2108686.539 | 16221.0221
October | 44452.6241 | 38.4142 | 347.871 | 0 | 0.0002 | 2098776.9442 | 16446.4687
November | 44212.6089 | 38.3621 | 318.2115 | 0 | 0.0002 | 1919724.4877 | 16272.9089
December | 43831.5159 | 38.202 | 284.9484 | 0 | 0.0002 | 1718921.5282 | 16039.5278
Annual Sum or Average | 525671.502 | 456.0427 | 3795.6253 | 0 | 0.0019 | 22898500 | 193516.0939
Minimum of Months | 39234.0884 | 34.0648 | 278.3558 | 0 | 0.0001 | 1679263.4426 | 14428.2365
Maximum of Months | 47013.0825 | 41.0169 | 353.1726 | 0 | 0.0002 | 2130758.965 | 17180.8537
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 368725000000 | 335490.221 | 06-JAN-15:00 | 84768.624 | 75263.477 | 91771.724 | 0 | 81058.959 | 0 | 25.69 | 0 | 0 | 0 | 0 | 0 | 2601.747 | 0 | 0
February | 344312000000 | 389935.688 | 15-FEB-14:00 | 84768.624 | 77263.149 | 91771.724 | 0 | 133531.695 | 0 | 2.722 | 0 | 0 | 0 | 0 | 0 | 2597.774 | 0 | 0
March | 392691000000 | 373225.776 | 01-MAR-12:00 | 84768.624 | 81262.495 | 91771.724 | 0 | 112843.621 | 0 | 25.318 | 0 | 0 | 0 | 0 | 0 | 2553.995 | 0 | 0
April | 374996000000 | 388730.72 | 28-APR-11:39 | 84768.624 | 81262.495 | 91771.724 | 0 | 128360.175 | 0 | 16.829 | 0 | 0 | 0 | 0 | 0 | 2550.874 | 0 | 0
May | 436886000000 | 426866.332 | 25-MAY-11:00 | 84768.624 | 81262.495 | 91771.724 | 0 | 166489.108 | 0 | 8.806 | 0 | 0 | 0 | 0 | 0 | 2565.575 | 0 | 0
June | 436106000000 | 410102.55 | 15-JUN-12:00 | 84768.624 | 77263.149 | 91771.724 | 0 | 153715.673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2583.38 | 0 | 0
July | 345811000000 | 352782.716 | 03-JUL-11:00 | 47093.68 | 47274.638 | 91771.724 | 0 | 164142.798 | 0 | 21.777 | 0 | 0 | 0 | 0 | 0 | 2478.1 | 0 | 0
August | 386783000000 | 350489.928 | 15-AUG-11:00 | 47093.68 | 47274.638 | 91771.724 | 0 | 161804.016 | 0 | 66.943 | 0 | 0 | 0 | 0 | 0 | 2478.928 | 0 | 0
September | 432360000000 | 448379.599 | 28-SEP-15:09 | 84768.624 | 75197.923 | 91771.724 | 0 | 194178.041 | 0 | 0.008 | 0 | 0 | 0 | 0 | 0 | 2463.279 | 0 | 0
October | 430328000000 | 409174.065 | 17-OCT-11:39 | 84768.624 | 80410.298 | 91771.724 | 0 | 149603.794 | 0 | 11.008 | 0 | 0 | 0 | 0 | 0 | 2608.617 | 0 | 0
November | 393616000000 | 369814.215 | 16-NOV-15:00 | 84768.624 | 74411.28 | 91771.724 | 0 | 116196.115 | 0 | 70.133 | 0 | 0 | 0 | 0 | 0 | 2596.339 | 0 | 0
December | 352443000000 | 336367.28 | 07-DEC-14:00 | 84768.624 | 76410.953 | 91771.724 | 0 | 80796.735 | 0 | 26.094 | 0 | 0 | 0 | 0 | 0 | 2593.151 | 0 | 0
Annual Sum or Average | 4695060000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 344312000000 | 335490.221 |  | 47093.68 | 47274.638 | 91771.724 | 0 | 80796.735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2463.279 | 0 | 0
Maximum of Months | 436886000000 | 448379.599 |  | 84768.624 | 81262.495 | 91771.724 | 0 | 194178.041 | 0 | 70.133 | 0 | 0 | 0 | 0 | 0 | 2608.617 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 195185.7 | 19312.82 | 0 | 214498.52
Cost per Total Building Area ($/m2) | 28.41 | 2.81 | 0 | 31.22
Cost per Net Conditioned Building Area ($/m2) | 28.41 | 2.81 | 0 | 31.22
8-baltimore
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 7117.02 | 1035.81 | 1035.81
Net Site Energy | 7117.02 | 1035.81 | 1035.81
Total Source Energy | 19740.13 | 2872.96 | 2872.96
Net Source Energy | 19740.13 | 2872.96 | 2872.96
Area (m2)
Total Building Area | 6871
Net Conditioned Building Area | 6871
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 1851.72 | 0 | 0 | 0 | 0
Cooling | 1086.16 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1297.99 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 61.65 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1256.13 | 361.03 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1034.79 | 0 | 0 | 0 | 0 | 0
Pumps | 1.51 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 86.09 | 0 | 0 | 0 | 589.92
Refrigeration | 79.95 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 4818.17 | 2298.85 | 0 | 0 | 0 | 589.92
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 4818.17 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 4818.17 | 100
Total On-Site and Utility Electric Sources | 4818.17 | 100
Total Electricity End Uses | 4818.17 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 162 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 546 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 171 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 252 | 90 | 0
BATH_ZN_1_FLR_1_WALL_5 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 190 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 441 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 168 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 399 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 49 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 25.2 | 3.24 | 0.39 | 0.495 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 26.6 | 3.24 | 0.39 | 0.495 | No | LOBBY_ZN_1_FLR_1_WALL_1
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 14 | 3.24 | 0.39 | 0.495 | No | BATH_ZN_1_FLR_1_WALL_5
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 29.4 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_1
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 29.4 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_2
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 23.8 | 3.24 | 0.39 | 0.495 | No | GYM_ZN_1_FLR_1_WALL_2
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 11.2 | 3.24 | 0.39 | 0.495 | No | KITCHEN_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 21 | 3.24 | 0.39 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 29.4 | 3.24 | 0.39 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_3
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 29.4 | 3.24 | 0.39 | 0.495 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 26.6 | 3.24 | 0.39 | 0.495 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
HEATSYS1 BOILER | Boiler:HotWater | 3755706.18 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 251923.11 | 3
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 197497.09 | 3
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 202519.12 | 3
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 273914.63 | 3
PSZ-AC_2:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 67021.59 | 3.69
PSZ-AC_1:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 85256.51 | 3.69
PSZ-AC_2:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 89415.33 | 3.69
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.67 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.02 | 0 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 2.26 | 0 | 1 | Zone Exhaust Fans
VAV_POD_1 FAN | Fan:VariableVolume | 0.28 | 655.15 | 15.22 | 36073 | 1 | Fan Energy
VAV_POD_2 FAN | Fan:VariableVolume | 0.28 | 655.15 | 11.93 | 28279.71 | 1 | Fan Energy
VAV_POD_3 FAN | Fan:VariableVolume | 0.28 | 655.15 | 12.23 | 28998.82 | 1 | Fan Energy
VAV_OTHER FAN | Fan:VariableVolume | 0.28 | 655.15 | 16.55 | 39221.98 | 1 | Fan Energy
PSZ-AC_2:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.39 | 4842.94 | 1 | General
PSZ-AC_1:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.43 | 4904.69 | 1 | General
PSZ-AC_2:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.6 | 5143.94 | 1 | General
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00218 | 100245.88 | 3549.14
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006951 | 319588.97 | 11314.83
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001753 | 80616.17 | 2854.16
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002041 | 93851.58 | 3322.75
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005637 | 259207.81 | 9177.08
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002157 | 99174.56 | 3511.21
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006817 | 313429.88 | 11096.77
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001742 | 80096.27 | 2835.75
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002042 | 93913.2 | 3324.93
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005642 | 259425.46 | 9184.78
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002159 | 99277.69 | 3514.86
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006845 | 314730.7 | 11142.83
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001764 | 81113.84 | 2871.78
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002064 | 94896.95 | 3359.76
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003824 | 175837.21 | 6225.4
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00241 | 110796.65 | 3922.68
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004231 | 194553.02 | 6888.02
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002141 | 98436.75 | 3485.09
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001938 | 89094.75 | 3154.34
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002059 | 94690.45 | 3352.45
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005123 | 235564.93 | 8340.02
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004626 | 212712.64 | 7530.95
VAV_POD_1_HEATC | 0.001662 | 76432.68 | 1193.08
VAV_POD_2_HEATC | 0.001442 | 66283.69 | 1021.01
VAV_POD_3_HEATC | 0.001326 | 60961.73 | 952.54
VAV_OTHER_HEATC | 0.001104 | 50772.7 | 821.8
Nominal Capacity [W]
PSZ-AC_2:5_UNITARY_PACKAGE_HEATCOIL | 65732.64
PSZ-AC_1:6_UNITARY_PACKAGE_HEATCOIL | 144829.08
PSZ-AC_2:7_UNITARY_PACKAGE_HEATCOIL | 138734.54
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 94432.6499 | 156.9038 | 393.4624 | 0 | 0.0016 | 24462.1495 | 39192.4728
February | 76498.5519 | 131.5859 | 343.477 | 0 | 0.0014 | 21356.3786 | 32158.9383
March | 76842.6689 | 140.6354 | 391.7208 | 0 | 0.0016 | 24359.3679 | 33076.9316
April | 66760.5358 | 127.2823 | 368.4793 | 0 | 0.0015 | 22915.8505 | 29203.3096
May | 76297.8905 | 148.3586 | 437.093 | 0 | 0.0018 | 27183.8898 | 33639.7848
June | 84631.3559 | 166.6349 | 496.2751 | 0 | 0.002 | 30865.2061 | 37503.4865
July | 71355.3616 | 139.4611 | 412.716 | 0 | 0.0017 | 25668.041 | 31525.8268
August | 77606.1976 | 151.3117 | 446.8471 | 0 | 0.0018 | 27790.6471 | 34254.0289
September | 74480.788 | 145.6214 | 431.0789 | 0 | 0.0017 | 26810.1017 | 32911.4148
October | 73994.2112 | 141.7389 | 412.0782 | 0 | 0.0017 | 25627.4919 | 32428.3912
November | 73982.1868 | 136.4619 | 383.0014 | 0 | 0.0016 | 23817.5125 | 31942.7186
December | 82822.7532 | 142.128 | 370.0157 | 0 | 0.0015 | 23006.3434 | 34786.7962
Annual Sum or Average | 929705.1513 | 1728.124 | 4886.2448 | 0 | 0.0199 | 303862.98 | 402624.1002
Minimum of Months | 66760.5358 | 127.2823 | 343.477 | 0 | 0.0014 | 21356.3786 | 29203.3096
Maximum of Months | 94432.6499 | 166.6349 | 496.2751 | 0 | 0.002 | 30865.2061 | 39192.4728
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 387882000000 | 322669.415 | 09-JAN-11:50 | 84768.624 | 81262.495 | 70397.074 | 0 | 82417.442 | 0 | 39.009 | 0 | 0 | 0 | 0 | 0 | 3784.771 | 0 | 0
February | 338635000000 | 303903.861 | 15-FEB-12:00 | 84768.624 | 81262.495 | 70397.074 | 0 | 64929.795 | 0 | 31.533 | 0 | 0 | 0 | 0 | 0 | 2514.341 | 0 | 0
March | 386252000000 | 376359.317 | 09-MAR-13:00 | 84768.624 | 77263.149 | 70397.074 | 0 | 141320.831 | 0 | 4.049 | 0 | 0 | 0 | 0 | 0 | 2605.589 | 0 | 0
April | 363363000000 | 367208.615 | 04-APR-11:00 | 84768.624 | 81262.495 | 70397.074 | 0 | 128167.28 | 0 | 3.309 | 0 | 0 | 0 | 0 | 0 | 2609.834 | 0 | 0
May | 431039000000 | 426737.837 | 16-MAY-10:39 | 84768.624 | 81262.495 | 70397.074 | 0 | 186468.064 | 0 | 0.134 | 0 | 0 | 0 | 0 | 0 | 3841.446 | 0 | 0
June | 489411000000 | 486354.71 | 30-JUN-13:00 | 84768.624 | 77263.149 | 70397.074 | 0 | 251311.729 | 0 | 0.011 | 0 | 0 | 0 | 0 | 0 | 2614.122 | 0 | 0
July | 407003000000 | 438070.347 | 25-JUL-11:00 | 47093.68 | 47274.638 | 70397.074 | 0 | 270815.457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2489.498 | 0 | 0
August | 440660000000 | 436547.343 | 09-AUG-14:00 | 47093.68 | 41275.62 | 70397.074 | 0 | 275289.081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2491.888 | 0 | 0
September | 425112000000 | 426447.174 | 05-SEP-10:39 | 84768.624 | 80410.298 | 70397.074 | 0 | 187025.815 | 0 | 3.873 | 0 | 0 | 0 | 0 | 0 | 3841.49 | 0 | 0
October | 406360000000 | 414651.577 | 03-OCT-10:39 | 84768.624 | 80410.298 | 70397.074 | 0 | 175233.642 | 0 | 0.464 | 0 | 0 | 0 | 0 | 0 | 3841.474 | 0 | 0
November | 377660000000 | 384839.54 | 03-NOV-11:50 | 84768.624 | 80410.298 | 70397.074 | 0 | 145418.652 | 0 | 3.432 | 0 | 0 | 0 | 0 | 0 | 3841.461 | 0 | 0
December | 364798000000 | 284074.021 | 08-DEC-10:09 | 84768.624 | 80410.298 | 70397.074 | 0 | 45905.559 | 0 | 66.135 | 0 | 0 | 0 | 0 | 0 | 2526.332 | 0 | 0
Annual Sum or Average | 4818170000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 338635000000 | 284074.021 |  | 47093.68 | 41275.62 | 70397.074 | 0 | 45905.559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2489.498 | 0 | 0
Maximum of Months | 489411000000 | 486354.71 |  | 84768.624 | 81262.495 | 70397.074 | 0 | 275289.081 | 0 | 66.135 | 0 | 0 | 0 | 0 | 0 | 3841.49 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 105207.57 | 22541.26 | 0 | 127748.83
Cost per Total Building Area ($/m2) | 15.31 | 3.28 | 0 | 18.59
Cost per Net Conditioned Building Area ($/m2) | 15.31 | 3.28 | 0 | 18.59
9-albuquerque
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 6262.99 | 911.51 | 911.51
Net Site Energy | 6262.99 | 911.51 | 911.51
Total Source Energy | 17313.71 | 2519.82 | 2519.82
Net Source Energy | 17313.71 | 2519.82 | 2519.82
Area (m2)
Total Building Area | 6871
Net Conditioned Building Area | 6871
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 1112.3 | 0 | 0 | 0 | 0
Cooling | 843.2 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1297.99 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 61.68 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1256.13 | 361.03 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1165.75 | 0 | 0 | 0 | 0 | 0
Pumps | 0.94 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 84.12 | 0 | 0 | 0 | 589.92
Refrigeration | 79.86 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 4705.54 | 1557.45 | 0 | 0 | 0 | 589.92
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 4705.54 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 4705.54 | 100
Total On-Site and Utility Electric Sources | 4705.54 | 100
Total Electricity End Uses | 4705.54 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 162 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 546 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 171 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 252 | 90 | 0
BATH_ZN_1_FLR_1_WALL_5 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 190 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 441 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 168 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 399 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 49 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 25.2 | 3.24 | 0.39 | 0.495 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 26.6 | 3.24 | 0.39 | 0.495 | No | LOBBY_ZN_1_FLR_1_WALL_1
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 14 | 3.24 | 0.39 | 0.495 | No | BATH_ZN_1_FLR_1_WALL_5
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 29.4 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_1
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 29.4 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_2
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 23.8 | 3.24 | 0.39 | 0.495 | No | GYM_ZN_1_FLR_1_WALL_2
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 11.2 | 3.24 | 0.39 | 0.495 | No | KITCHEN_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 21 | 3.24 | 0.39 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 29.4 | 3.24 | 0.39 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_3
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 29.4 | 3.24 | 0.39 | 0.495 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 26.6 | 3.24 | 0.39 | 0.495 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
HEATSYS1 BOILER | Boiler:HotWater | 3512411.75 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 289942.84 | 3
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 227007.44 | 3
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 232213.91 | 3
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 315759.67 | 3
PSZ-AC_2:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 65786.86 | 3.69
PSZ-AC_1:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 66884.91 | 3.69
PSZ-AC_2:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 70877.62 | 3.69
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.67 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.02 | 0 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 2.26 | 0 | 1 | Zone Exhaust Fans
VAV_POD_1 FAN | Fan:VariableVolume | 0.28 | 655.15 | 17.52 | 41517.07 | 1 | Fan Energy
VAV_POD_2 FAN | Fan:VariableVolume | 0.28 | 655.15 | 13.71 | 32505.31 | 1 | Fan Energy
VAV_POD_3 FAN | Fan:VariableVolume | 0.28 | 655.15 | 14.03 | 33250.83 | 1 | Fan Energy
VAV_OTHER FAN | Fan:VariableVolume | 0.28 | 655.15 | 19.08 | 45213.79 | 1 | Fan Energy
PSZ-AC_2:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.97 | 5677.41 | 1 | General
PSZ-AC_1:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 4.04 | 5772.17 | 1 | General
PSZ-AC_2:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 4.28 | 6116.74 | 1 | General
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002088 | 95983.47 | 3398.23
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006314 | 290300.09 | 10277.88
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001672 | 76896.53 | 2722.47
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002042 | 93880.16 | 3323.76
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005542 | 254817.02 | 9021.63
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002064 | 94881.39 | 3359.21
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00619 | 284593.84 | 10075.85
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001661 | 76372.62 | 2703.92
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002043 | 93939.67 | 3325.87
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005547 | 255030.23 | 9029.17
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002066 | 94986.65 | 3362.94
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006217 | 285876.63 | 10121.27
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001684 | 77413.12 | 2740.76
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002064 | 94910.43 | 3360.24
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003763 | 173032.11 | 6126.09
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00238 | 109413.09 | 3873.7
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00404 | 185772.22 | 6577.14
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001914 | 87985.75 | 3115.08
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001849 | 85019.06 | 3010.04
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001996 | 91763.78 | 3248.84
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004777 | 219653.3 | 7776.68
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004521 | 207890.26 | 7360.22
VAV_POD_1_HEATC | 0.001198 | 55088.13 | 885.33
VAV_POD_2_HEATC | 0.001047 | 48143.62 | 767.06
VAV_POD_3_HEATC | 0.000956 | 43978.63 | 706.87
VAV_OTHER_HEATC | 0.000757 | 34789.94 | 568.15
Nominal Capacity [W]
PSZ-AC_2:5_UNITARY_PACKAGE_HEATCOIL | 52228.2
PSZ-AC_1:6_UNITARY_PACKAGE_HEATCOIL | 115074.66
PSZ-AC_2:7_UNITARY_PACKAGE_HEATCOIL | 110232.22
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 114969.6698 | 188.8558 | 457.831 | 0 | 0.0018 | 475992.3749 | 48079.433
February | 96872.0649 | 161.4574 | 398.3729 | 0 | 0.0016 | 414192.6196 | 40739.6809
March | 109043.631 | 184.1641 | 461.5262 | 0 | 0.0018 | 479870.8659 | 46095.8476
April | 98659.6485 | 169.3609 | 432.3758 | 0 | 0.0017 | 449580.5285 | 41974.4539
May | 120234.8085 | 208.6188 | 538.9534 | 0 | 0.0021 | 560413.6442 | 51371.4577
June | 126507.3848 | 220.0808 | 570.2014 | 0 | 0.0022 | 592909.6206 | 54108.2197
July | 105016.5514 | 182.1103 | 470.1777 | 0 | 0.0018 | 488898.7799 | 44859.17
August | 112061.6817 | 193.7032 | 498.3418 | 0 | 0.0019 | 518180.2243 | 47807.3654
September | 115711.7565 | 200.8475 | 519.0935 | 0 | 0.002 | 539763.5312 | 49446.4581
October | 107093.6868 | 183.8939 | 469.6354 | 0 | 0.0018 | 488323.0755 | 45568.0804
November | 105184.8617 | 176.8387 | 440.819 | 0 | 0.0017 | 458335.1048 | 44385.3498
December | 113932.0184 | 186.6358 | 450.9089 | 0 | 0.0018 | 468791.9631 | 47594.9336
Annual Sum or Average | 1325287.764 | 2256.5672 | 5708.2369 | 0 | 0.0224 | 5935252.3325 | 562030.4502
Minimum of Months | 96872.0649 | 161.4574 | 398.3729 | 0 | 0.0016 | 414192.6196 | 40739.6809
Maximum of Months | 126507.3848 | 220.0808 | 570.2014 | 0 | 0.0022 | 592909.6206 | 54108.2197
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 377372000000 | 301987.236 | 25-JAN-14:00 | 84768.624 | 77263.149 | 81397.338 | 0 | 56014.266 | 0 | 4.032 | 0 | 0 | 0 | 0 | 0 | 2539.827 | 0 | 0
February | 328377000000 | 332015.211 | 14-FEB-14:00 | 84768.624 | 77263.149 | 81469.319 | 0 | 85983.132 | 0 | 1.386 | 0 | 0 | 0 | 0 | 0 | 2529.6 | 0 | 0
March | 380447000000 | 338881.057 | 02-MAR-14:00 | 84768.624 | 77263.149 | 81430.512 | 0 | 92883.346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2535.426 | 0 | 0
April | 356433000000 | 361676.863 | 21-APR-13:00 | 84768.624 | 77263.149 | 81691.047 | 0 | 115421.892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2532.151 | 0 | 0
May | 444303000000 | 387408.249 | 30-MAY-13:00 | 84768.624 | 77263.149 | 81411.191 | 0 | 141371.217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2594.067 | 0 | 0
June | 470066000000 | 418214.966 | 29-JUN-13:00 | 84768.624 | 77263.149 | 81416.375 | 0 | 172201.092 | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 | 2565.72 | 0 | 0
July | 387605000000 | 349091.224 | 03-JUL-14:00 | 47093.68 | 41275.62 | 81397.338 | 0 | 176856.461 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 2468.123 | 0 | 0
August | 410820000000 | 361789.307 | 01-AUG-13:00 | 47093.68 | 43275.293 | 81397.338 | 0 | 187548.369 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 2474.624 | 0 | 0
September | 427931000000 | 405052.872 | 05-SEP-11:30 | 84768.624 | 80410.298 | 81397.338 | 0 | 155865.659 | 0 | 2.7 | 0 | 0 | 0 | 0 | 0 | 2608.252 | 0 | 0
October | 387148000000 | 373569.813 | 03-OCT-11:00 | 84768.624 | 80410.298 | 81397.338 | 0 | 124394.108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2599.445 | 0 | 0
November | 363374000000 | 328991.201 | 08-NOV-14:00 | 84768.624 | 76410.953 | 81398.454 | 0 | 83867.146 | 0 | 0.945 | 0 | 0 | 0 | 0 | 0 | 2545.08 | 0 | 0
December | 371664000000 | 293986.145 | 08-DEC-14:00 | 84768.624 | 76410.953 | 81397.338 | 0 | 48865.923 | 0 | 4.762 | 0 | 0 | 0 | 0 | 0 | 2538.546 | 0 | 0
Annual Sum or Average | 4705540000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 328377000000 | 293986.145 |  | 47093.68 | 41275.62 | 81397.338 | 0 | 48865.923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2468.123 | 0 | 0
Maximum of Months | 470066000000 | 418214.966 |  | 84768.624 | 80410.298 | 81691.047 | 0 | 187548.369 | 0 | 4.762 | 0 | 0 | 0 | 0 | 0 | 2608.252 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 48460.65 | 10918.71 | 0 | 59379.36
Cost per Total Building Area ($/m2) | 7.05 | 1.59 | 0 | 8.64
Cost per Net Conditioned Building Area ($/m2) | 7.05 | 1.59 | 0 | 8.64
10-seattle
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 5998.06 | 872.95 | 872.95
Net Site Energy | 5998.06 | 872.95 | 872.95
Total Source Energy | 9159.64 | 1333.09 | 1333.09
Net Source Energy | 9159.64 | 1333.09 | 1333.09
Area (m2)
Total Building Area | 6871
Net Conditioned Building Area | 6871
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 1532.22 | 0 | 0 | 0 | 0
Cooling | 428.61 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1297.99 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 61.55 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1256.13 | 361.03 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 889.83 | 0 | 0 | 0 | 0 | 0
Pumps | 1.28 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 89.8 | 0 | 0 | 0 | 589.92
Refrigeration | 79.62 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 4015.01 | 1983.05 | 0 | 0 | 0 | 589.92
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 4015.01 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 4015.01 | 100
Total On-Site and Utility Electric Sources | 4015.01 | 100
Total Electricity End Uses | 4015.01 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 162 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 546 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 171 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 252 | 90 | 0
BATH_ZN_1_FLR_1_WALL_5 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 190 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 441 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 168 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 399 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 49 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 25.2 | 3.24 | 0.39 | 0.495 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 26.6 | 3.24 | 0.39 | 0.495 | No | LOBBY_ZN_1_FLR_1_WALL_1
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 14 | 3.24 | 0.39 | 0.495 | No | BATH_ZN_1_FLR_1_WALL_5
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 29.4 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_1
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 29.4 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_2
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 23.8 | 3.24 | 0.39 | 0.495 | No | GYM_ZN_1_FLR_1_WALL_2
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 11.2 | 3.24 | 0.39 | 0.495 | No | KITCHEN_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 21 | 3.24 | 0.39 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 29.4 | 3.24 | 0.39 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_3
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 29.4 | 3.24 | 0.39 | 0.495 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 26.6 | 3.24 | 0.39 | 0.495 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
HEATSYS1 BOILER | Boiler:HotWater | 3440753.89 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 240818 | 3
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 184396.53 | 3
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 194841.96 | 3
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 247545.86 | 3
PSZ-AC_2:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 48738.73 | 3.69
PSZ-AC_1:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 54683.21 | 3.69
PSZ-AC_2:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 50760.34 | 3.69
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.67 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.02 | 0 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 2.26 | 0 | 1 | Zone Exhaust Fans
VAV_POD_1 FAN | Fan:VariableVolume | 0.28 | 655.15 | 14.55 | 34482.85 | 1 | Fan Energy
VAV_POD_2 FAN | Fan:VariableVolume | 0.28 | 655.15 | 11.14 | 26403.83 | 1 | Fan Energy
VAV_POD_3 FAN | Fan:VariableVolume | 0.28 | 655.15 | 11.77 | 27899.52 | 1 | Fan Energy
VAV_OTHER FAN | Fan:VariableVolume | 0.28 | 655.15 | 14.95 | 35446.22 | 1 | Fan Energy
PSZ-AC_2:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 2.94 | 4206.15 | 1 | General
PSZ-AC_1:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.3 | 4719.16 | 1 | General
PSZ-AC_2:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.07 | 4380.62 | 1 | General
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002228 | 102446.42 | 3627.05
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.007365 | 338659.32 | 11990.01
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001576 | 72444.93 | 2564.86
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00176 | 80904.72 | 2864.38
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004497 | 206759.46 | 7320.18
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002205 | 101397.11 | 3589.9
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.007204 | 331231.84 | 11727.04
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001564 | 71925.6 | 2546.48
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001761 | 80963 | 2866.44
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004502 | 207017.73 | 7329.32
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002207 | 101498.31 | 3593.48
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00723 | 332445.72 | 11770.02
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001586 | 72920.38 | 2581.7
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001781 | 81912.06 | 2900.04
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003078 | 141512.31 | 5010.15
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002063 | 94848.34 | 3358.04
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003619 | 166380.75 | 5890.6
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002286 | 105113.69 | 3721.48
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001695 | 77921.97 | 2758.77
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001757 | 80765.08 | 2859.43
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004862 | 223551.65 | 7914.7
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003898 | 179247.23 | 6346.13
VAV_POD_1_HEATC | 0.001232 | 56639.06 | 909.26
VAV_POD_2_HEATC | 0.001084 | 49837.4 | 788.3
VAV_POD_3_HEATC | 0.000979 | 45034.96 | 723.42
VAV_OTHER_HEATC | 0.000813 | 37374.84 | 608.33
Nominal Capacity [W]
PSZ-AC_2:5_UNITARY_PACKAGE_HEATCOIL | 56846.24
PSZ-AC_1:6_UNITARY_PACKAGE_HEATCOIL | 125249.63
PSZ-AC_2:7_UNITARY_PACKAGE_HEATCOIL | 119979.01
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 32271.7445 | 40.4957 | 71.6579 | 0 | 0.0003 | 946100.4702 | 12369.0367
February | 24581.3846 | 32.1082 | 62.644 | 0 | 0.0003 | 827337.0169 | 9556.7315
March | 27796.5007 | 36.792 | 73.9291 | 0 | 0.0003 | 976461.5652 | 10858.5611
April | 22113.5496 | 30.5536 | 67.0101 | 0 | 0.0003 | 885285.442 | 8776.0231
May | 22256.8866 | 32.4581 | 78.3398 | 0 | 0.0003 | 1035209.2725 | 9015.6697
June | 22100.6925 | 32.9073 | 82.1127 | 0 | 0.0003 | 1085148.6437 | 9024.9086
July | 19487.8867 | 27.9892 | 65.8436 | 0 | 0.0003 | 870026.6023 | 7847.8943
August | 22086.8148 | 31.315 | 72.0267 | 0 | 0.0003 | 951674.8488 | 8850.9213
September | 21793.1054 | 31.9078 | 77.5124 | 0 | 0.0003 | 1024290.5398 | 8841.307
October | 23299.2916 | 32.6653 | 73.6256 | 0 | 0.0003 | 972751.8057 | 9297.2966
November | 27266.3913 | 35.4994 | 68.7457 | 0 | 0.0003 | 907903.0068 | 10588.18
December | 31224.2784 | 39.146 | 69.1069 | 0 | 0.0003 | 912413.1393 | 11963.7903
Annual Sum or Average | 296278.5267 | 403.8376 | 862.5544 | 0 | 0.0036 | 11394600 | 116990.3202
Minimum of Months | 19487.8867 | 27.9892 | 62.644 | 0 | 0.0003 | 827337.0169 | 7847.8943
Maximum of Months | 32271.7445 | 40.4957 | 82.1127 | 0 | 0.0003 | 1085148.6437 | 12369.0367
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 333369000000 | 249179.119 | 27-JAN-12:00 | 84768.624 | 81262.495 | 65324.175 | 0 | 15247.595 | 0 | 56.992 | 0 | 0 | 0 | 0 | 0 | 2519.239 | 0 | 0
February | 291521000000 | 289596.353 | 21-FEB-13:00 | 84768.624 | 77263.149 | 65324.175 | 0 | 59686.311 | 0 | 7.758 | 0 | 0 | 0 | 0 | 0 | 2546.335 | 0 | 0
March | 344067000000 | 304743.914 | 29-MAR-13:00 | 84768.624 | 77263.149 | 65324.175 | 0 | 74817.237 | 0 | 0.198 | 0 | 0 | 0 | 0 | 0 | 2570.532 | 0 | 0
April | 311940000000 | 294290.485 | 14-APR-13:00 | 84768.624 | 77263.149 | 65324.175 | 0 | 64375.84 | 0 | 0.762 | 0 | 0 | 0 | 0 | 0 | 2557.934 | 0 | 0
May | 364767000000 | 347702.828 | 05-MAY-13:00 | 84768.624 | 77263.149 | 65324.175 | 0 | 117742.729 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 2604.148 | 0 | 0
June | 382364000000 | 352451.92 | 28-JUN-12:00 | 84768.624 | 77263.149 | 65324.175 | 0 | 122510.744 | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 | 2585.223 | 0 | 0
July | 306563000000 | 296923.045 | 24-JUL-14:00 | 47093.68 | 41275.62 | 65324.175 | 0 | 140754.458 | 0 | 0.006 | 0 | 0 | 0 | 0 | 0 | 2475.106 | 0 | 0
August | 335333000000 | 282669.251 | 07-AUG-14:00 | 47093.68 | 41275.62 | 65324.175 | 0 | 126500.354 | 0 | 0.009 | 0 | 0 | 0 | 0 | 0 | 2475.413 | 0 | 0
September | 360920000000 | 354657.86 | 13-SEP-15:00 | 84768.624 | 75197.923 | 65324.175 | 0 | 126890.348 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 2476.78 | 0 | 0
October | 342760000000 | 317786.713 | 17-OCT-12:00 | 84768.624 | 76410.953 | 65324.175 | 0 | 88721.275 | 0 | 1.693 | 0 | 0 | 0 | 0 | 0 | 2559.993 | 0 | 0
November | 319909000000 | 304519.897 | 03-NOV-12:00 | 84768.624 | 80410.298 | 65324.175 | 0 | 71431.563 | 0 | 18.817 | 0 | 0 | 0 | 0 | 0 | 2566.421 | 0 | 0
December | 321499000000 | 237727.434 | 13-DEC-11:50 | 84768.624 | 80410.298 | 65324.175 | 0 | 3302.792 | 0 | 158.77 | 0 | 0 | 0 | 0 | 0 | 3762.775 | 0 | 0
Annual Sum or Average | 4015010000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 291521000000 | 237727.434 |  | 47093.68 | 41275.62 | 65324.175 | 0 | 3302.792 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 2475.106 | 0 | 0
Maximum of Months | 382364000000 | 354657.86 |  | 84768.624 | 81262.495 | 65324.175 | 0 | 140754.458 | 0 | 158.77 | 0 | 0 | 0 | 0 | 0 | 3762.775 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 85249.45 | 16601.82 | 0 | 101851.27
Cost per Total Building Area ($/m2) | 12.41 | 2.42 | 0 | 14.82
Cost per Net Conditioned Building Area ($/m2) | 12.41 | 2.42 | 0 | 14.82
11-chicago
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 7693.21 | 1119.66 | 1119.66
Net Site Energy | 7693.21 | 1119.66 | 1119.66
Total Source Energy | 19587.26 | 2850.72 | 2850.72
Net Source Energy | 19587.26 | 2850.72 | 2850.72
Area (m2)
Total Building Area | 6871
Net Conditioned Building Area | 6871
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 2678.88 | 0 | 0 | 0 | 0
Cooling | 789.86 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1297.99 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 61.66 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1256.13 | 361.03 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1071.47 | 0 | 0 | 0 | 0 | 0
Pumps | 2.16 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 94.91 | 0 | 0 | 0 | 589.92
Refrigeration | 79.12 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 4558.39 | 3134.82 | 0 | 0 | 0 | 589.92
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 4558.39 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 4558.39 | 100
Total On-Site and Utility Electric Sources | 4558.39 | 100
Total Electricity End Uses | 4558.39 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 162 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 546 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 171 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 252 | 90 | 0
BATH_ZN_1_FLR_1_WALL_5 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 190 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 441 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 168 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 399 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 49 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 25.2 | 3.24 | 0.39 | 0.495 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 26.6 | 3.24 | 0.39 | 0.495 | No | LOBBY_ZN_1_FLR_1_WALL_1
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 14 | 3.24 | 0.39 | 0.495 | No | BATH_ZN_1_FLR_1_WALL_5
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 29.4 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_1
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 29.4 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_2
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 23.8 | 3.24 | 0.39 | 0.495 | No | GYM_ZN_1_FLR_1_WALL_2
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 11.2 | 3.24 | 0.39 | 0.495 | No | KITCHEN_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 21 | 3.24 | 0.39 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 29.4 | 3.24 | 0.39 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_3
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 29.4 | 3.24 | 0.39 | 0.495 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 26.6 | 3.24 | 0.39 | 0.495 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
HEATSYS1 BOILER | Boiler:HotWater | 3700326.27 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 244796.35 | 3
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 191765.36 | 3
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 196949.51 | 3
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 266767.71 | 3
PSZ-AC_2:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 65828.28 | 3.69
PSZ-AC_1:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 85129.69 | 3.69
PSZ-AC_2:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 86992.13 | 3.69
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.67 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.02 | 0 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 2.26 | 0 | 1 | Zone Exhaust Fans
VAV_POD_1 FAN | Fan:VariableVolume | 0.28 | 655.15 | 14.79 | 35052.52 | 1 | Fan Energy
VAV_POD_2 FAN | Fan:VariableVolume | 0.28 | 655.15 | 11.58 | 27458.98 | 1 | Fan Energy
VAV_POD_3 FAN | Fan:VariableVolume | 0.28 | 655.15 | 11.9 | 28201.3 | 1 | Fan Energy
VAV_OTHER FAN | Fan:VariableVolume | 0.28 | 655.15 | 16.12 | 38198.61 | 1 | Fan Energy
PSZ-AC_2:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.33 | 4759.39 | 1 | General
PSZ-AC_1:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.43 | 4897.39 | 1 | General
PSZ-AC_2:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.5 | 5004.53 | 1 | General
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002082 | 95741.55 | 3389.67
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00675 | 310371.15 | 10988.48
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001675 | 77022.64 | 2726.93
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001911 | 87886.19 | 3111.55
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005316 | 244439.81 | 8654.23
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002059 | 94668.55 | 3351.68
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006609 | 303874.29 | 10758.47
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001664 | 76495.35 | 2708.27
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001913 | 87945.6 | 3113.65
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005321 | 244650.38 | 8661.68
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002061 | 94771.74 | 3355.33
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006636 | 305130.64 | 10802.95
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001686 | 77504.56 | 2744
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001934 | 88909.69 | 3147.79
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003609 | 165923.2 | 5874.4
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002299 | 105722.49 | 3743.03
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004059 | 186650.26 | 6608.23
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002069 | 95124.75 | 3367.83
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001883 | 86580.76 | 3065.33
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001941 | 89241.85 | 3159.55
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004925 | 226432.8 | 8016.7
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004395 | 202064.43 | 7153.96
VAV_POD_1_HEATC | 0.00229 | 105311.96 | 1560.34
VAV_POD_2_HEATC | 0.001973 | 90706.88 | 1323.26
VAV_POD_3_HEATC | 0.001828 | 84028.86 | 1246.62
VAV_OTHER_HEATC | 0.00159 | 73125.91 | 1153.52
Nominal Capacity [W]
PSZ-AC_2:5_UNITARY_PACKAGE_HEATCOIL | 76789.29
PSZ-AC_1:6_UNITARY_PACKAGE_HEATCOIL | 169190.26
PSZ-AC_2:7_UNITARY_PACKAGE_HEATCOIL | 162070.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 170141.075 | 273.9562 | 717.1877 | 0 | 0.0022 | 165058.2232 | 70313.3321
February | 142034.2427 | 233.9552 | 630.2172 | 0 | 0.002 | 145051.1358 | 59200.273
March | 144714.6172 | 246.2674 | 689.4514 | 0 | 0.0021 | 158697.165 | 61072.5107
April | 119203.4956 | 210.5298 | 613.9258 | 0 | 0.0019 | 141324.2147 | 51040.1947
May | 142387.4341 | 255.6447 | 758.3196 | 0 | 0.0023 | 174569.0455 | 61365.6086
June | 163220.8743 | 295.0448 | 881.2349 | 0 | 0.0027 | 202867.4509 | 70535.106
July | 133752.0483 | 240.8915 | 716.8311 | 0 | 0.0022 | 165019.1873 | 57715.7555
August | 141575.0107 | 253.8927 | 752.234 | 0 | 0.0023 | 173167.7345 | 60987.4226
September | 142043.19 | 255.6387 | 760.1556 | 0 | 0.0023 | 174992.5168 | 61275.7704
October | 131241.5101 | 233.3027 | 684.9886 | 0 | 0.0021 | 157684.7805 | 56339.1617
November | 132509.2416 | 227.3064 | 642.1496 | 0 | 0.002 | 147811.9834 | 56094.5973
December | 158102.2761 | 258.0755 | 687.4457 | 0 | 0.0021 | 158219.1141 | 65673.1237
Annual Sum or Average | 1720925.0158 | 2984.5055 | 8534.1412 | 0 | 0.0261 | 1964462.5516 | 731612.8563
Minimum of Months | 119203.4956 | 210.5298 | 613.9258 | 0 | 0.0019 | 141324.2147 | 51040.1947
Maximum of Months | 170141.075 | 295.0448 | 881.2349 | 0 | 0.0027 | 202867.4509 | 70535.106
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 383005000000 | 251577.33 | 17-JAN-12:00 | 84768.624 | 81262.495 | 68635.759 | 0 | 14364.722 | 0 | 32.653 | 0 | 0 | 0 | 0 | 0 | 2513.078 | 0 | 0
February | 336580000000 | 251316.197 | 28-FEB-11:09 | 84768.624 | 81262.495 | 68635.759 | 0 | 13033.204 | 0 | 28.217 | 0 | 0 | 0 | 0 | 0 | 3587.9 | 0 | 0
March | 368245000000 | 323018.171 | 31-MAR-14:00 | 84768.624 | 75263.477 | 68635.759 | 0 | 91806.255 | 0 | 1.456 | 0 | 0 | 0 | 0 | 0 | 2542.599 | 0 | 0
April | 327932000000 | 350204.299 | 03-APR-13:00 | 84768.624 | 77263.149 | 68635.759 | 0 | 116920.828 | 0 | 8.501 | 0 | 0 | 0 | 0 | 0 | 2607.438 | 0 | 0
May | 405074000000 | 408956.257 | 30-MAY-15:00 | 84768.624 | 75263.477 | 68635.759 | 0 | 177679.154 | 0 | 0.008 | 0 | 0 | 0 | 0 | 0 | 2609.235 | 0 | 0
June | 470739000000 | 490911.712 | 08-JUN-12:00 | 84768.624 | 77263.149 | 68712.934 | 0 | 257551.821 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 2615.183 | 0 | 0
July | 382915000000 | 398354.348 | 14-JUL-10:50 | 47093.68 | 47274.638 | 68635.759 | 0 | 231669.722 | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 | 3680.545 | 0 | 0
August | 401823000000 | 396862.342 | 04-AUG-15:00 | 47093.68 | 41275.62 | 68635.759 | 0 | 237365.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2492.172 | 0 | 0
September | 406057000000 | 409939.453 | 06-SEP-10:00 | 84768.624 | 80410.298 | 68635.759 | 0 | 173438.067 | 0 | 0.269 | 0 | 0 | 0 | 0 | 0 | 2686.437 | 0 | 0
October | 365896000000 | 389193.117 | 30-OCT-11:20 | 84768.624 | 80410.298 | 68635.759 | 0 | 151708.831 | 0 | 3.402 | 0 | 0 | 0 | 0 | 0 | 3666.204 | 0 | 0
November | 342987000000 | 385193.17 | 02-NOV-11:50 | 84768.624 | 80410.298 | 68635.759 | 0 | 147534.526 | 0 | 2.533 | 0 | 0 | 0 | 0 | 0 | 3841.431 | 0 | 0
December | 367136000000 | 252410.948 | 12-DEC-12:00 | 84768.624 | 80410.298 | 68635.759 | 0 | 16017.061 | 0 | 46.046 | 0 | 0 | 0 | 0 | 0 | 2533.161 | 0 | 0
Annual Sum or Average | 4558390000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 327932000000 | 251316.197 |  | 47093.68 | 41275.62 | 68635.759 | 0 | 13033.204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2492.172 | 0 | 0
Maximum of Months | 470739000000 | 490911.712 |  | 84768.624 | 81262.495 | 68712.934 | 0 | 257551.821 | 0 | 46.046 | 0 | 0 | 0 | 0 | 0 | 3841.431 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 110995.26 | 26409.54 | 0 | 137404.8
Cost per Total Building Area ($/m2) | 16.15 | 3.84 | 0 | 20
Cost per Net Conditioned Building Area ($/m2) | 16.15 | 3.84 | 0 | 20
12-boulder
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 6794.83 | 988.91 | 988.91
Net Site Energy | 6794.83 | 988.91 | 988.91
Total Source Energy | 17504.3 | 2547.56 | 2547.56
Net Source Energy | 17504.3 | 2547.56 | 2547.56
Area (m2)
Total Building Area | 6871
Net Conditioned Building Area | 6871
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 1809.45 | 0 | 0 | 0 | 0
Cooling | 659.92 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1297.99 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 61.63 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1256.13 | 361.03 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1173.99 | 0 | 0 | 0 | 0 | 0
Pumps | 1.47 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 94.1 | 0 | 0 | 0 | 589.92
Refrigeration | 79.14 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 4530.25 | 2264.58 | 0 | 0 | 0 | 589.92
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 4530.25 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 4530.25 | 100
Total On-Site and Utility Electric Sources | 4530.25 | 100
Total Electricity End Uses | 4530.25 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 162 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 546 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 171 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 252 | 90 | 0
BATH_ZN_1_FLR_1_WALL_5 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 190 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 441 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 168 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 399 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 49 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 25.2 | 3.24 | 0.39 | 0.495 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 26.6 | 3.24 | 0.39 | 0.495 | No | LOBBY_ZN_1_FLR_1_WALL_1
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 14 | 3.24 | 0.39 | 0.495 | No | BATH_ZN_1_FLR_1_WALL_5
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 29.4 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_1
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 29.4 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_2
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 23.8 | 3.24 | 0.39 | 0.495 | No | GYM_ZN_1_FLR_1_WALL_2
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 11.2 | 3.24 | 0.39 | 0.495 | No | KITCHEN_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 21 | 3.24 | 0.39 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 29.4 | 3.24 | 0.39 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_3
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 29.4 | 3.24 | 0.39 | 0.495 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 26.6 | 3.24 | 0.39 | 0.495 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
HEATSYS1 BOILER | Boiler:HotWater | 3485933.57 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 279528.87 | 3
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 218547.83 | 3
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 224591.13 | 3
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 303873.51 | 3
PSZ-AC_2:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 63488.62 | 3.69
PSZ-AC_1:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 65713.38 | 3.69
PSZ-AC_2:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 67449.81 | 3.69
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.67 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.02 | 0 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 2.26 | 0 | 1 | Zone Exhaust Fans
VAV_POD_1 FAN | Fan:VariableVolume | 0.28 | 655.15 | 16.89 | 40025.88 | 1 | Fan Energy
VAV_POD_2 FAN | Fan:VariableVolume | 0.28 | 655.15 | 13.2 | 31293.98 | 1 | Fan Energy
VAV_POD_3 FAN | Fan:VariableVolume | 0.28 | 655.15 | 13.57 | 32159.32 | 1 | Fan Energy
VAV_OTHER FAN | Fan:VariableVolume | 0.28 | 655.15 | 18.36 | 43511.81 | 1 | Fan Energy
PSZ-AC_2:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.84 | 5479.07 | 1 | General
PSZ-AC_1:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.97 | 5671.06 | 1 | General
PSZ-AC_2:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 4.07 | 5820.92 | 1 | General
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00201 | 92412.64 | 3271.81
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006374 | 293075.45 | 10376.14
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001605 | 73787.24 | 2612.39
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001872 | 86093.2 | 3048.07
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00513 | 235877.93 | 8351.1
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001986 | 91331.45 | 3233.53
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006236 | 286743.14 | 10151.95
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001593 | 73250.61 | 2593.39
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001874 | 86150.48 | 3050.1
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005134 | 236075.14 | 8358.08
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001989 | 91435.64 | 3237.22
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006263 | 287995.36 | 10196.28
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001616 | 74290.2 | 2630.19
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001895 | 87118.52 | 3084.37
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003485 | 160244.45 | 5673.35
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002237 | 102837.48 | 3640.89
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003865 | 177718.77 | 6292.01
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001934 | 88931.63 | 3148.56
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001798 | 82692.8 | 2927.68
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001875 | 86227.44 | 3052.82
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004675 | 214955.95 | 7610.37
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004245 | 195208.14 | 6911.21
VAV_POD_1_HEATC | 0.001831 | 84186.04 | 1281.73
VAV_POD_2_HEATC | 0.001583 | 72774.47 | 1091.83
VAV_POD_3_HEATC | 0.001461 | 67176.08 | 1023.75
VAV_OTHER_HEATC | 0.001247 | 57343.3 | 921.72
Nominal Capacity [W]
PSZ-AC_2:5_UNITARY_PACKAGE_HEATCOIL | 63834.94
PSZ-AC_1:6_UNITARY_PACKAGE_HEATCOIL | 140647.85
PSZ-AC_2:7_UNITARY_PACKAGE_HEATCOIL | 134729.27
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 126212.93 | 201.9022 | 473.255 | 0 | 0.0019 | 491988.7752 | 52249.3981
February | 104725.8518 | 170.1261 | 406.7405 | 0 | 0.0016 | 422861.3734 | 43608.9252
March | 113497.5398 | 188.7003 | 464.2157 | 0 | 0.0018 | 482646.8842 | 47685.7499
April | 98014.155 | 166.9815 | 422.6657 | 0 | 0.0017 | 439475.6594 | 41575.1242
May | 108340.2443 | 186.2086 | 476.0449 | 0 | 0.0019 | 494988.7982 | 46115.5776
June | 116824.3994 | 202.3096 | 521.5456 | 0 | 0.002 | 542310.2202 | 49875.8979
July | 100478.3992 | 173.4606 | 445.638 | 0 | 0.0017 | 463376.8964 | 42844.1326
August | 105686.0929 | 181.9243 | 465.8848 | 0 | 0.0018 | 484426.1872 | 45013.0478
September | 105804.7306 | 182.5672 | 468.7821 | 0 | 0.0018 | 487441.7045 | 45106.6067
October | 105148.9558 | 179.7166 | 456.5722 | 0 | 0.0018 | 474734.5103 | 44658.4153
November | 107637.7987 | 177.8999 | 434.5221 | 0 | 0.0017 | 451766.806 | 45120.0081
December | 123412.6286 | 196.9023 | 459.9386 | 0 | 0.0018 | 478141.1771 | 51039.0957
Annual Sum or Average | 1315783.7263 | 2208.6994 | 5495.8051 | 0 | 0.0216 | 5714158.992 | 554891.9791
Minimum of Months | 98014.155 | 166.9815 | 406.7405 | 0 | 0.0016 | 422861.3734 | 41575.1242
Maximum of Months | 126212.93 | 202.3096 | 521.5456 | 0 | 0.002 | 542310.2202 | 52249.3981
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 390055000000 | 315668.701 | 27-JAN-11:50 | 84768.624 | 81262.495 | 78504.282 | 0 | 67369.541 | 0 | 16.456 | 0 | 0 | 0 | 0 | 0 | 3747.303 | 0 | 0
February | 335250000000 | 290445.408 | 07-FEB-14:00 | 84768.624 | 77263.149 | 78504.282 | 0 | 47376.12 | 0 | 4.129 | 0 | 0 | 0 | 0 | 0 | 2529.105 | 0 | 0
March | 382648000000 | 335463.63 | 30-MAR-13:00 | 84768.624 | 77263.149 | 78504.282 | 0 | 92402.225 | 0 | 0.121 | 0 | 0 | 0 | 0 | 0 | 2525.228 | 0 | 0
April | 348422000000 | 355865.985 | 25-APR-13:00 | 84768.624 | 77263.149 | 78504.282 | 0 | 112768.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2561.73 | 0 | 0
May | 392433000000 | 375442.397 | 24-MAY-13:00 | 84768.624 | 77263.149 | 78504.282 | 0 | 132324.995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2581.347 | 0 | 0
June | 429950000000 | 400465.949 | 28-JUN-11:00 | 84768.624 | 81262.495 | 78504.282 | 0 | 153338.834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2591.714 | 0 | 0
July | 367371000000 | 339580.983 | 19-JUL-12:00 | 47093.68 | 43275.293 | 78504.282 | 0 | 168292.299 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 2415.429 | 0 | 0
August | 384059000000 | 340492.998 | 30-AUG-13:00 | 47093.68 | 43275.293 | 78504.282 | 0 | 169211.588 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 2408.155 | 0 | 0
September | 386450000000 | 378246.823 | 05-SEP-13:00 | 84768.624 | 76410.953 | 78504.282 | 0 | 136018.177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2544.787 | 0 | 0
October | 376375000000 | 361030.529 | 05-OCT-13:00 | 84768.624 | 76410.953 | 79090.39 | 0 | 118220.265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2540.297 | 0 | 0
November | 358166000000 | 329686.152 | 10-NOV-13:00 | 84768.624 | 76410.953 | 78504.282 | 0 | 87479.867 | 0 | 3.315 | 0 | 0 | 0 | 0 | 0 | 2519.112 | 0 | 0
December | 379076000000 | 287188.503 | 21-DEC-14:00 | 84768.624 | 76410.953 | 78504.282 | 0 | 44950.172 | 0 | 8.379 | 0 | 0 | 0 | 0 | 0 | 2546.094 | 0 | 0
Annual Sum or Average | 4530250000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 335250000000 | 287188.503 |  | 47093.68 | 43275.293 | 78504.282 | 0 | 44950.172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2408.155 | 0 | 0
Maximum of Months | 429950000000 | 400465.949 |  | 84768.624 | 81262.495 | 79090.39 | 0 | 169211.588 | 0 | 16.456 | 0 | 0 | 0 | 0 | 0 | 3747.303 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 46662.63 | 15833.2 | 0 | 62495.82
Cost per Total Building Area ($/m2) | 6.79 | 2.3 | 0 | 9.1
Cost per Net Conditioned Building Area ($/m2) | 6.79 | 2.3 | 0 | 9.1
13-minneapolis
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 8969.63 | 1305.43 | 1305.43
Net Site Energy | 8969.63 | 1305.43 | 1305.43
Total Source Energy | 20441.52 | 2975.04 | 2975.04
Net Source Energy | 20441.52 | 2975.04 | 2975.04
Area (m2)
Total Building Area | 6871
Net Conditioned Building Area | 6871
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 3965.69 | 0 | 0 | 0 | 0
Cooling | 702.84 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1297.99 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 61.62 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1256.13 | 361.03 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1139.77 | 0 | 0 | 0 | 0 | 0
Pumps | 3.34 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 102.75 | 0 | 0 | 0 | 589.92
Refrigeration | 78.47 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 4540.16 | 4429.46 | 0 | 0 | 0 | 589.92
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 4540.16 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 4540.16 | 100
Total On-Site and Utility Electric Sources | 4540.16 | 100
Total Electricity End Uses | 4540.16 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 162 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 546 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 171 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 252 | 90 | 0
BATH_ZN_1_FLR_1_WALL_5 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 190 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 441 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 168 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 399 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 49 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 25.2 | 3.24 | 0.39 | 0.495 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 26.6 | 3.24 | 0.39 | 0.495 | No | LOBBY_ZN_1_FLR_1_WALL_1
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 14 | 3.24 | 0.39 | 0.495 | No | BATH_ZN_1_FLR_1_WALL_5
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 29.4 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_1
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 29.4 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_2
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 23.8 | 3.24 | 0.39 | 0.495 | No | GYM_ZN_1_FLR_1_WALL_2
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 11.2 | 3.24 | 0.39 | 0.495 | No | KITCHEN_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 21 | 3.24 | 0.39 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 29.4 | 3.24 | 0.39 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_3
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 29.4 | 3.24 | 0.39 | 0.495 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 26.6 | 3.24 | 0.39 | 0.495 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
HEATSYS1 BOILER | Boiler:HotWater | 3728147 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 245889.5 | 3
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 191704.75 | 3
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 198011.96 | 3
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 264725.69 | 3
PSZ-AC_2:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 61330.97 | 3.69
PSZ-AC_1:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 85612.68 | 3.69
PSZ-AC_2:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 86135.16 | 3.69
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.67 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.02 | 0 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 2.26 | 0 | 1 | Zone Exhaust Fans
VAV_POD_1 FAN | Fan:VariableVolume | 0.28 | 655.15 | 14.85 | 35209.05 | 1 | Fan Energy
VAV_POD_2 FAN | Fan:VariableVolume | 0.28 | 655.15 | 11.58 | 27450.3 | 1 | Fan Energy
VAV_POD_3 FAN | Fan:VariableVolume | 0.28 | 655.15 | 11.96 | 28353.44 | 1 | Fan Energy
VAV_OTHER FAN | Fan:VariableVolume | 0.28 | 655.15 | 15.99 | 37906.21 | 1 | Fan Energy
PSZ-AC_2:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.3 | 4712.63 | 1 | General
PSZ-AC_1:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.45 | 4925.18 | 1 | General
PSZ-AC_2:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.47 | 4955.23 | 1 | General
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002108 | 96940.44 | 3432.11
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006909 | 317691.96 | 11247.67
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001642 | 75516.54 | 2673.61
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001845 | 84854 | 3004.2
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005139 | 236290.2 | 8365.7
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002085 | 95847.6 | 3393.42
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00676 | 310847.54 | 11005.35
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001631 | 74979.65 | 2654.6
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001847 | 84918.23 | 3006.47
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005143 | 236495.76 | 8372.97
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002087 | 95952.73 | 3397.14
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006788 | 312127.55 | 11050.67
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001653 | 76008.25 | 2691.02
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001869 | 85948.24 | 3042.94
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00349 | 160473.11 | 5681.44
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002237 | 102859 | 3641.65
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00392 | 180259.02 | 6381.95
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002124 | 97665.56 | 3457.78
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001828 | 84038.46 | 2975.33
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001882 | 86539.27 | 3063.86
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004947 | 227442.29 | 8052.44
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004302 | 197827.98 | 7003.97
VAV_POD_1_HEATC | 0.002629 | 120870.81 | 1749.37
VAV_POD_2_HEATC | 0.002261 | 103973.08 | 1478.87
VAV_POD_3_HEATC | 0.002098 | 96445.26 | 1398.06
VAV_OTHER_HEATC | 0.001856 | 85334.48 | 1317.09
Nominal Capacity [W]
PSZ-AC_2:5_UNITARY_PACKAGE_HEATCOIL | 82986.65
PSZ-AC_1:6_UNITARY_PACKAGE_HEATCOIL | 182844.93
PSZ-AC_2:7_UNITARY_PACKAGE_HEATCOIL | 175150.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 147490.0538 | 214.6904 | 263.8198 | 0 | 0.002 | 173219.9197 | 58771.1957
February | 118613.862 | 178.5463 | 231.3432 | 0 | 0.0018 | 151932.612 | 47827.6335
March | 105686.0783 | 170.8844 | 244.5451 | 0 | 0.0018 | 160669.5551 | 43742.6049
April | 79477.4953 | 137.6909 | 213.8036 | 0 | 0.0016 | 140515.731 | 33772.8803
May | 92730.8066 | 165.3404 | 264.7243 | 0 | 0.0019 | 174000.9687 | 39852.8884
June | 101569.3117 | 183.035 | 296.2579 | 0 | 0.0022 | 194735.2475 | 43836.4044
July | 84269.7027 | 150.8044 | 242.3616 | 0 | 0.0018 | 159304.3065 | 36269.1608
August | 91258.3274 | 162.8836 | 261.0699 | 0 | 0.0019 | 171599.6223 | 39236.1833
September | 86344.0443 | 153.9369 | 246.44 | 0 | 0.0018 | 161982.8192 | 37106.5374
October | 83647.7196 | 144.3173 | 223.074 | 0 | 0.0016 | 146605.9576 | 35487.776
November | 100207.1734 | 162.1894 | 232.401 | 0 | 0.0017 | 152691.4883 | 41490.5901
December | 134684.6613 | 201.2604 | 257.8787 | 0 | 0.002 | 169351.206 | 54166.5555
Annual Sum or Average | 1225979.2366 | 2025.5796 | 2977.7191 | 0 | 0.0222 | 1956609.4337 | 511560.4102
Minimum of Months | 79477.4953 | 137.6909 | 213.8036 | 0 | 0.0016 | 140515.731 | 33772.8803
Maximum of Months | 147490.0538 | 214.6904 | 296.2579 | 0 | 0.0022 | 194735.2475 | 58771.1957
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 401944000000 | 242015.343 | 30-JAN-10:20 | 84768.624 | 81262.495 | 68570.664 | 0 | 4735.118 | 0 | 185.795 | 0 | 0 | 0 | 0 | 0 | 2492.647 | 0 | 0
February | 352548000000 | 242472.987 | 27-FEB-11:20 | 84768.624 | 81262.495 | 68570.664 | 0 | 4158.213 | 0 | 162.032 | 0 | 0 | 0 | 0 | 0 | 3550.96 | 0 | 0
March | 372822000000 | 294198.727 | 23-MAR-15:50 | 84768.624 | 75263.477 | 68570.664 | 0 | 63152.555 | 0 | 2.809 | 0 | 0 | 0 | 0 | 0 | 2440.599 | 0 | 0
April | 326056000000 | 326894.161 | 27-APR-13:00 | 84768.624 | 77263.149 | 68570.664 | 0 | 93708.551 | 0 | 2.983 | 0 | 0 | 0 | 0 | 0 | 2580.189 | 0 | 0
May | 403756000000 | 410921.214 | 31-MAY-11:00 | 84768.624 | 81262.495 | 68570.664 | 0 | 173711.047 | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 | 2608.38 | 0 | 0
June | 451868000000 | 452399.619 | 29-JUN-13:00 | 84768.624 | 77263.149 | 68573.506 | 0 | 219181.423 | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 | 2612.911 | 0 | 0
July | 369654000000 | 381784.147 | 13-JUL-15:00 | 47093.68 | 41275.62 | 68570.664 | 0 | 222354.836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2489.347 | 0 | 0
August | 398184000000 | 371686.198 | 25-AUG-15:00 | 47093.68 | 41275.62 | 68570.664 | 0 | 212258.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2487.884 | 0 | 0
September | 375869000000 | 398389.447 | 22-SEP-13:30 | 84768.624 | 76410.953 | 68570.664 | 0 | 166021.706 | 0 | 2.81 | 0 | 0 | 0 | 0 | 0 | 2614.69 | 0 | 0
October | 340188000000 | 329734.007 | 06-OCT-14:00 | 84768.624 | 74411.28 | 68570.664 | 0 | 99432.28 | 0 | 0.675 | 0 | 0 | 0 | 0 | 0 | 2550.484 | 0 | 0
November | 354309000000 | 311424.731 | 02-NOV-14:00 | 84768.624 | 76410.953 | 68570.664 | 0 | 79101.822 | 0 | 3.301 | 0 | 0 | 0 | 0 | 0 | 2569.367 | 0 | 0
December | 392967000000 | 240877.48 | 26-DEC-11:50 | 84768.624 | 80410.298 | 68570.664 | 0 | 3201.734 | 0 | 171.341 | 0 | 0 | 0 | 0 | 0 | 3754.819 | 0 | 0
Annual Sum or Average | 4540160000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 326056000000 | 240877.48 |  | 47093.68 | 41275.62 | 68570.664 | 0 | 3201.734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2440.599 | 0 | 0
Maximum of Months | 451868000000 | 452399.619 |  | 84768.624 | 81262.495 | 68573.506 | 0 | 222354.836 | 0 | 185.795 | 0 | 0 | 0 | 0 | 0 | 3754.819 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 76768.29 | 35079.32 | 0 | 111847.61
Cost per Total Building Area ($/m2) | 11.17 | 5.11 | 0 | 16.28
Cost per Net Conditioned Building Area ($/m2) | 11.17 | 5.11 | 0 | 16.28
14-helena
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 7824.86 | 1138.82 | 1138.82
Net Site Energy | 7824.86 | 1138.82 | 1138.82
Total Source Energy | 18934.35 | 2755.69 | 2755.69
Net Source Energy | 18934.35 | 2755.69 | 2755.69
Area (m2)
Total Building Area | 6871
Net Conditioned Building Area | 6871
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 3002.29 | 0 | 0 | 0 | 0
Cooling | 491.37 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1297.99 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 61.61 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1256.13 | 361.03 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1170.11 | 0 | 0 | 0 | 0 | 0
Pumps | 2.56 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 103.49 | 0 | 0 | 0 | 589.92
Refrigeration | 78.3 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 4358.05 | 3466.81 | 0 | 0 | 0 | 589.92
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 4358.05 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 4358.05 | 100
Total On-Site and Utility Electric Sources | 4358.05 | 100
Total Electricity End Uses | 4358.05 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 162 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 546 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 171 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 252 | 90 | 0
BATH_ZN_1_FLR_1_WALL_5 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 190 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 441 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 168 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 399 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 49 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 25.2 | 3.24 | 0.39 | 0.495 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 26.6 | 3.24 | 0.39 | 0.495 | No | LOBBY_ZN_1_FLR_1_WALL_1
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 14 | 3.24 | 0.39 | 0.495 | No | BATH_ZN_1_FLR_1_WALL_5
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 29.4 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_1
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 29.4 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_2
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 23.8 | 3.24 | 0.39 | 0.495 | No | GYM_ZN_1_FLR_1_WALL_2
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 11.2 | 3.24 | 0.39 | 0.495 | No | KITCHEN_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 21 | 3.24 | 0.39 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 29.4 | 3.24 | 0.39 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_3
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 29.4 | 3.24 | 0.39 | 0.495 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 26.6 | 3.24 | 0.39 | 0.495 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
HEATSYS1 BOILER | Boiler:HotWater | 3556821.38 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 265102.11 | 3
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 205469.46 | 3
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 213589.48 | 3
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 282454.61 | 3
PSZ-AC_2:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 58319 | 3.69
PSZ-AC_1:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 62259.41 | 3.69
PSZ-AC_2:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 61490.69 | 3.69
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.67 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.02 | 0 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 2.26 | 0 | 1 | Zone Exhaust Fans
VAV_POD_1 FAN | Fan:VariableVolume | 0.28 | 655.15 | 16.01 | 37960.11 | 1 | Fan Energy
VAV_POD_2 FAN | Fan:VariableVolume | 0.28 | 655.15 | 12.41 | 29421.28 | 1 | Fan Energy
VAV_POD_3 FAN | Fan:VariableVolume | 0.28 | 655.15 | 12.9 | 30583.99 | 1 | Fan Energy
VAV_OTHER FAN | Fan:VariableVolume | 0.28 | 655.15 | 17.06 | 40444.82 | 1 | Fan Energy
PSZ-AC_2:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.52 | 5032.93 | 1 | General
PSZ-AC_1:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.76 | 5372.99 | 1 | General
PSZ-AC_2:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.71 | 5306.65 | 1 | General
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002071 | 95244.69 | 3372.07
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006756 | 310644.78 | 10998.17
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001561 | 71762.08 | 2540.69
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001761 | 80981.67 | 2867.1
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004811 | 221210.3 | 7831.8
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002048 | 94154.9 | 3333.49
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006605 | 303719.94 | 10753
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001549 | 71219.67 | 2521.48
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001763 | 81046.88 | 2869.41
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004815 | 221412.79 | 7838.97
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00205 | 94261.08 | 3337.25
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006633 | 304996.45 | 10798.19
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001572 | 72291.56 | 2559.43
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001786 | 82098.17 | 2906.63
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003274 | 150522.41 | 5329.14
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002149 | 98825.89 | 3498.86
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003677 | 169087.04 | 5986.41
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002068 | 95099.75 | 3366.94
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001727 | 79389.79 | 2810.74
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001783 | 81995.12 | 2902.98
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004756 | 218684.72 | 7742.39
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004091 | 188124.47 | 6660.42
VAV_POD_1_HEATC | 0.002392 | 109989.35 | 1607.27
VAV_POD_2_HEATC | 0.002062 | 94793.65 | 1360.23
VAV_POD_3_HEATC | 0.001908 | 87746.59 | 1284.33
VAV_OTHER_HEATC | 0.001686 | 77517.65 | 1204.13
Nominal Capacity [W]
PSZ-AC_2:5_UNITARY_PACKAGE_HEATCOIL | 75620.95
PSZ-AC_1:6_UNITARY_PACKAGE_HEATCOIL | 166616.05
PSZ-AC_2:7_UNITARY_PACKAGE_HEATCOIL | 159604.69
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 134764.8933 | 203.7066 | 294.9233 | 0 | 0.0021 | 6991566.84 | 54508.8099
February | 112051.7757 | 173.018 | 258.395 | 0 | 0.0019 | 6126350.7001 | 45674.1823
March | 107269.524 | 175.2729 | 282.2272 | 0 | 0.002 | 6693241.9561 | 44656.6192
April | 84705.4549 | 142.5932 | 238.0097 | 0 | 0.0017 | 5645291.5689 | 35668.0346
May | 92472.1235 | 159.798 | 274.7704 | 0 | 0.0019 | 6517859.4502 | 39337.7059
June | 99485.4642 | 173.4164 | 301.0306 | 0 | 0.0021 | 7141002.6038 | 42466.0763
July | 82409.8805 | 143.2867 | 248.0429 | 0 | 0.0017 | 5883984.7369 | 35141.9861
August | 87220.8016 | 150.0251 | 256.6415 | 0 | 0.0018 | 6087718.6411 | 37036.296
September | 89800.6988 | 155.6026 | 268.3552 | 0 | 0.0019 | 6365745.2659 | 38241.9765
October | 91021.3069 | 154.4313 | 260.1178 | 0 | 0.0018 | 6169857.345 | 38444.1091
November | 102561.8676 | 166.6608 | 266.5138 | 0 | 0.0019 | 6320429.7414 | 42607.8665
December | 125793.4068 | 192.6287 | 284.2701 | 0 | 0.002 | 6739520.6941 | 51120.1129
Annual Sum or Average | 1209557.1979 | 1990.4403 | 3233.2975 | 0 | 0.0228 | 76682600 | 504903.7753
Minimum of Months | 82409.8805 | 142.5932 | 238.0097 | 0 | 0.0017 | 5645291.5689 | 35141.9861
Maximum of Months | 134764.8933 | 203.7066 | 301.0306 | 0 | 0.0021 | 7141002.6038 | 54508.8099
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 397347000000 | 248796.822 | 30-JAN-11:50 | 84768.624 | 81262.495 | 73658.304 | 0 | 5231.861 | 0 | 126.475 | 0 | 0 | 0 | 0 | 0 | 3749.063 | 0 | 0
February | 348175000000 | 311480.629 | 02-FEB-14:00 | 84768.624 | 77263.149 | 73658.304 | 0 | 73214.014 | 0 | 8.949 | 0 | 0 | 0 | 0 | 0 | 2567.589 | 0 | 0
March | 380393000000 | 319805.128 | 30-MAR-13:00 | 84768.624 | 77263.149 | 73658.304 | 0 | 81568.629 | 0 | 2.466 | 0 | 0 | 0 | 0 | 0 | 2543.955 | 0 | 0
April | 320835000000 | 310845.206 | 06-APR-13:00 | 84768.624 | 77263.149 | 73658.304 | 0 | 72614.127 | 0 | 3.125 | 0 | 0 | 0 | 0 | 0 | 2537.876 | 0 | 0
May | 370426000000 | 343390.582 | 17-MAY-13:00 | 84768.624 | 77263.149 | 73658.304 | 0 | 105134.155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2566.349 | 0 | 0
June | 405840000000 | 417593.107 | 30-JUN-12:00 | 84768.624 | 77263.149 | 73658.304 | 0 | 179314.338 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 2588.687 | 0 | 0
July | 334401000000 | 312314.918 | 19-JUL-13:00 | 47093.68 | 43275.293 | 73658.304 | 0 | 145873.689 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 2413.942 | 0 | 0
August | 345980000000 | 301270.65 | 09-AUG-15:00 | 47093.68 | 41275.62 | 73658.304 | 0 | 136949.793 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 2293.248 | 0 | 0
September | 361781000000 | 367094.001 | 12-SEP-13:00 | 84768.624 | 76410.953 | 73658.304 | 0 | 129651.833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2604.287 | 0 | 0
October | 350648000000 | 335563.462 | 06-OCT-13:00 | 84768.624 | 76410.953 | 73658.304 | 0 | 98154.785 | 0 | 0.832 | 0 | 0 | 0 | 0 | 0 | 2569.965 | 0 | 0
November | 359205000000 | 284241.553 | 21-NOV-11:50 | 84768.624 | 80410.298 | 73658.304 | 0 | 41631.322 | 0 | 27.765 | 0 | 0 | 0 | 0 | 0 | 3745.24 | 0 | 0
December | 383023000000 | 248685.55 | 06-DEC-11:50 | 84768.624 | 80410.298 | 73658.304 | 0 | 5984.492 | 0 | 114.402 | 0 | 0 | 0 | 0 | 0 | 3749.43 | 0 | 0
Annual Sum or Average | 4358050000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 320835000000 | 248685.55 |  | 47093.68 | 41275.62 | 73658.304 | 0 | 5231.861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2293.248 | 0 | 0
Maximum of Months | 405840000000 | 417593.107 |  | 84768.624 | 81262.495 | 73658.304 | 0 | 179314.338 | 0 | 126.475 | 0 | 0 | 0 | 0 | 0 | 3749.43 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 93044.39 | 28432.94 | 0 | 121477.34
Cost per Total Building Area ($/m2) | 13.54 | 4.14 | 0 | 17.68
Cost per Net Conditioned Building Area ($/m2) | 13.54 | 4.14 | 0 | 17.68
15-duluth
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 9628.24 | 1401.29 | 1401.29
Net Site Energy | 9628.24 | 1401.29 | 1401.29
Total Source Energy | 20570.96 | 2993.88 | 2993.88
Net Source Energy | 20570.96 | 2993.88 | 2993.88
Area (m2)
Total Building Area | 6871
Net Conditioned Building Area | 6871
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 4864.03 | 0 | 0 | 0 | 0
Cooling | 434.4 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1297.99 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 61.57 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1256.13 | 361.03 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1156.91 | 0 | 0 | 0 | 0 | 0
Pumps | 4.18 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 114.51 | 0 | 0 | 0 | 589.92
Refrigeration | 77.49 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 4288.67 | 5339.57 | 0 | 0 | 0 | 589.92
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 4288.67 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 4288.67 | 100
Total On-Site and Utility Electric Sources | 4288.67 | 100
Total Electricity End Uses | 4288.67 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 162 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 546 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 171 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 252 | 90 | 0
BATH_ZN_1_FLR_1_WALL_5 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 190 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 441 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 168 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 399 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 15.4 | 3.24 | 0.49 | 0.49 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 3.24 | 0.49 | 0.49 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 74.2 | 3.24 | 0.49 | 0.49 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 4.2 | 3.24 | 0.49 | 0.49 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_NORTH | 15.4 | 3.24 | 0.49 | 0.49 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 3.24 | 0.49 | 0.49 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_NORTH | 74.2 | 3.24 | 0.49 | 0.49 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 15.4 | 3.24 | 0.49 | 0.49 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 3.24 | 0.49 | 0.49 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 74.2 | 3.24 | 0.49 | 0.49 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 4.2 | 3.24 | 0.49 | 0.49 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_NORTH | 15.4 | 3.24 | 0.49 | 0.49 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 3.24 | 0.49 | 0.49 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_NORTH | 74.2 | 3.24 | 0.49 | 0.49 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 15.4 | 3.24 | 0.49 | 0.49 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 3.24 | 0.49 | 0.49 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 74.2 | 3.24 | 0.49 | 0.49 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 4.2 | 3.24 | 0.49 | 0.49 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_NORTH | 15.4 | 3.24 | 0.49 | 0.49 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 3.24 | 0.49 | 0.49 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_NORTH | 49 | 3.24 | 0.49 | 0.49 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_NORTH | 25.2 | 3.24 | 0.49 | 0.49 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 3.24 | 0.49 | 0.49 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 26.6 | 3.24 | 0.49 | 0.49 | No | LOBBY_ZN_1_FLR_1_WALL_1
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 14 | 3.24 | 0.49 | 0.49 | No | BATH_ZN_1_FLR_1_WALL_5
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 29.4 | 3.24 | 0.49 | 0.49 | No | OFFICES_ZN_1_FLR_1_WALL_1
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 29.4 | 3.24 | 0.49 | 0.49 | No | OFFICES_ZN_1_FLR_1_WALL_2
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 23.8 | 3.24 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_1_WALL_2
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_1_CEILING
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 11.2 | 3.24 | 0.49 | 0.49 | No | KITCHEN_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 21 | 3.24 | 0.49 | 0.49 | No | CAFETERIA_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_NORTH | 29.4 | 3.24 | 0.49 | 0.49 | No | CAFETERIA_ZN_1_FLR_1_WALL_3
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 29.4 | 3.24 | 0.49 | 0.49 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_NORTH | 26.6 | 3.24 | 0.49 | 0.49 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
HEATSYS1 BOILER | Boiler:HotWater | 3617436.01 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 242814.34 | 3
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 187095.8 | 3
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 195637.33 | 3
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 256829.05 | 3
PSZ-AC_2:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 52705.76 | 3.69
PSZ-AC_1:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 73079.07 | 3.69
PSZ-AC_2:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 67492.6 | 3.69
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.67 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.02 | 0 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 2.26 | 0 | 1 | Zone Exhaust Fans
VAV_POD_1 FAN | Fan:VariableVolume | 0.28 | 655.15 | 14.67 | 34768.71 | 1 | Fan Energy
VAV_POD_2 FAN | Fan:VariableVolume | 0.28 | 655.15 | 11.3 | 26790.34 | 1 | Fan Energy
VAV_POD_3 FAN | Fan:VariableVolume | 0.28 | 655.15 | 11.82 | 28013.41 | 1 | Fan Energy
VAV_OTHER FAN | Fan:VariableVolume | 0.28 | 655.15 | 15.52 | 36775.49 | 1 | Fan Energy
PSZ-AC_2:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.18 | 4548.51 | 1 | General
PSZ-AC_1:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.43 | 4906.12 | 1 | General
PSZ-AC_2:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.32 | 4748.27 | 1 | General
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002108 | 96934.63 | 3431.91
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00678 | 311722.09 | 11036.31
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001574 | 72355.11 | 2561.68
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00182 | 83678.78 | 2962.59
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004715 | 216793.64 | 7675.43
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002078 | 95565.09 | 3383.42
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006596 | 303288.36 | 10737.72
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001559 | 71698.67 | 2538.44
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001822 | 83757.83 | 2965.39
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00472 | 217048.19 | 7684.45
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002081 | 95693.42 | 3387.96
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006627 | 304703.9 | 10787.84
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001585 | 72868.28 | 2579.85
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001849 | 85034.89 | 3010.6
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003226 | 148344.74 | 5252.05
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.0021 | 96560.17 | 3418.65
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00371 | 170586.26 | 6039.49
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002078 | 95528.85 | 3382.13
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001712 | 78732.6 | 2787.47
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001851 | 85104 | 3013.05
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004725 | 217237.96 | 7691.16
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004 | 183920.85 | 6511.59
VAV_POD_1_HEATC | 0.002775 | 127575.48 | 1817.95
VAV_POD_2_HEATC | 0.002388 | 109802.96 | 1532.69
VAV_POD_3_HEATC | 0.002214 | 101798.34 | 1453.17
VAV_OTHER_HEATC | 0.001981 | 91100.93 | 1383.41
Nominal Capacity [W]
PSZ-AC_2:5_UNITARY_PACKAGE_HEATCOIL | 84943.16
PSZ-AC_1:6_UNITARY_PACKAGE_HEATCOIL | 187155.71
PSZ-AC_2:7_UNITARY_PACKAGE_HEATCOIL | 179280.03
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 149230.7952 | 216.4379 | 264.3729 | 0 | 0.0021 | 173578.2086 | 59389.6695
February | 125223.4669 | 184.7476 | 232.0305 | 0 | 0.0018 | 152362.8022 | 50134.511
March | 116610.2298 | 182.3654 | 249.6914 | 0 | 0.0019 | 164021.2854 | 47673.0672
April | 82701.2434 | 139.1111 | 208.9148 | 0 | 0.0015 | 137285.6458 | 34744.6749
May | 82964.7382 | 144.9025 | 226.9951 | 0 | 0.0017 | 149190.2102 | 35366.5929
June | 89919.6616 | 160.9947 | 258.8695 | 0 | 0.0019 | 170155.2249 | 38708.455
July | 79442.7244 | 141.0028 | 224.6904 | 0 | 0.0016 | 147684.5411 | 34080.4384
August | 79161.4726 | 138.3818 | 216.9859 | 0 | 0.0016 | 142612.2486 | 33756.9642
September | 79402.0101 | 139.4801 | 219.8523 | 0 | 0.0016 | 144498.9473 | 33924.3294
October | 83742.4731 | 142.5752 | 217.1218 | 0 | 0.0016 | 142686.2506 | 35345.8272
November | 108788.659 | 170.6639 | 234.6711 | 0 | 0.0018 | 154157.2151 | 44526.1351
December | 141079.6367 | 207.3649 | 258.8842 | 0 | 0.002 | 169991.6216 | 56408.5181
Annual Sum or Average | 1218267.111 | 1968.0278 | 2813.0798 | 0 | 0.0211 | 1848224.2012 | 504059.183
Minimum of Months | 79161.4726 | 138.3818 | 208.9148 | 0 | 0.0015 | 137285.6458 | 33756.9642
Maximum of Months | 149230.7952 | 216.4379 | 264.3729 | 0 | 0.0021 | 173578.2086 | 59389.6695
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 402775000000 | 240593.7 | 13-JAN-11:50 | 84768.624 | 81262.495 | 67105.607 | 0 | 3563.682 | 0 | 140.915 | 0 | 0 | 0 | 0 | 0 | 3752.377 | 0 | 0
February | 353546000000 | 241236.619 | 24-FEB-11:50 | 84768.624 | 81262.495 | 67105.607 | 0 | 4224.332 | 0 | 119.231 | 0 | 0 | 0 | 0 | 0 | 3756.331 | 0 | 0
March | 380599000000 | 241880.261 | 16-MAR-10:50 | 84768.624 | 81262.495 | 67105.607 | 0 | 4879.183 | 0 | 108.044 | 0 | 0 | 0 | 0 | 0 | 3756.309 | 0 | 0
April | 318561000000 | 290076.21 | 04-APR-14:00 | 84768.624 | 75263.477 | 67105.607 | 0 | 60400.988 | 0 | 1.331 | 0 | 0 | 0 | 0 | 0 | 2536.183 | 0 | 0
May | 346185000000 | 325633.866 | 31-MAY-13:00 | 84768.624 | 77263.149 | 67105.607 | 0 | 93934.181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2562.304 | 0 | 0
June | 394832000000 | 407822.42 | 14-JUN-14:00 | 84768.624 | 75263.477 | 67219.718 | 0 | 177959.329 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 2611.271 | 0 | 0
July | 342691000000 | 332746.606 | 07-JUL-11:00 | 47093.68 | 47274.638 | 67105.607 | 0 | 168786.612 | 0 | 0.498 | 0 | 0 | 0 | 0 | 0 | 2485.571 | 0 | 0
August | 330921000000 | 324792.093 | 11-AUG-14:00 | 47093.68 | 41275.62 | 67105.607 | 0 | 166852.816 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 2464.366 | 0 | 0
September | 335299000000 | 393450.15 | 08-SEP-12:20 | 84768.624 | 76410.953 | 67105.607 | 0 | 162547.52 | 0 | 2.836 | 0 | 0 | 0 | 0 | 0 | 2614.611 | 0 | 0
October | 331093000000 | 304097.89 | 27-OCT-11:00 | 84768.624 | 80410.298 | 67105.607 | 0 | 69280.584 | 0 | 10.1 | 0 | 0 | 0 | 0 | 0 | 2522.678 | 0 | 0
November | 357710000000 | 273267.198 | 09-NOV-11:50 | 84768.624 | 80410.298 | 67105.607 | 0 | 37150.797 | 0 | 31.86 | 0 | 0 | 0 | 0 | 0 | 3800.013 | 0 | 0
December | 394453000000 | 240085.379 | 26-DEC-11:50 | 84768.624 | 80410.298 | 67105.607 | 0 | 3887.656 | 0 | 152.412 | 0 | 0 | 0 | 0 | 0 | 3760.782 | 0 | 0
Annual Sum or Average | 4288670000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 318561000000 | 240085.379 |  | 47093.68 | 41275.62 | 67105.607 | 0 | 3563.682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2464.366 | 0 | 0
Maximum of Months | 402775000000 | 407822.42 |  | 84768.624 | 81262.495 | 67219.718 | 0 | 177959.329 | 0 | 152.412 | 0 | 0 | 0 | 0 | 0 | 3800.013 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 71072.03 | 42180.46 | 0 | 113252.49
Cost per Total Building Area ($/m2) | 10.34 | 6.14 | 0 | 16.48
Cost per Net Conditioned Building Area ($/m2) | 10.34 | 6.14 | 0 | 16.48
16-fairbanks
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 13185.38 | 1918.99 | 1918.99
Net Site Energy | 13185.38 | 1918.99 | 1918.99
Total Source Energy | 24617.69 | 3582.84 | 3582.84
Net Source Energy | 24617.69 | 3582.84 | 3582.84
Area (m2)
Total Building Area | 6871
Net Conditioned Building Area | 6871
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 8575.26 | 0 | 0 | 0 | 0
Cooling | 291.57 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1297.99 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 61.19 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1256.13 | 361.03 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1129.54 | 0 | 0 | 0 | 0 | 0
Pumps | 8.42 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 128.43 | 0 | 0 | 0 | 589.92
Refrigeration | 75.82 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 4120.66 | 9064.72 | 0 | 0 | 0 | 589.92
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 4120.66 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 4120.66 | 100
Total On-Site and Utility Electric Sources | 4120.66 | 100
Total Electricity End Uses | 4120.66 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 192 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 192 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 192 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 162 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 546 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 171 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 252 | 90 | 0
BATH_ZN_1_FLR_1_WALL_5 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 190 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 441 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 168 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 315 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 399 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 15.4 | 2.62 | 0.49 | 0.49 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 2.62 | 0.49 | 0.49 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 74.2 | 2.62 | 0.49 | 0.49 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 4.2 | 2.62 | 0.49 | 0.49 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_NORTH | 15.4 | 2.62 | 0.49 | 0.49 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 2.62 | 0.49 | 0.49 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_NORTH | 74.2 | 2.62 | 0.49 | 0.49 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 15.4 | 2.62 | 0.49 | 0.49 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 2.62 | 0.49 | 0.49 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 74.2 | 2.62 | 0.49 | 0.49 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 4.2 | 2.62 | 0.49 | 0.49 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_NORTH | 15.4 | 2.62 | 0.49 | 0.49 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 2.62 | 0.49 | 0.49 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_NORTH | 74.2 | 2.62 | 0.49 | 0.49 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 15.4 | 2.62 | 0.49 | 0.49 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 2.62 | 0.49 | 0.49 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 74.2 | 2.62 | 0.49 | 0.49 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 4.2 | 2.62 | 0.49 | 0.49 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_NORTH | 15.4 | 2.62 | 0.49 | 0.49 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 2.62 | 0.49 | 0.49 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_NORTH | 49 | 2.62 | 0.49 | 0.49 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_NORTH | 25.2 | 2.62 | 0.49 | 0.49 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 2.62 | 0.49 | 0.49 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 26.6 | 2.62 | 0.49 | 0.49 | No | LOBBY_ZN_1_FLR_1_WALL_1
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 14 | 2.62 | 0.49 | 0.49 | No | BATH_ZN_1_FLR_1_WALL_5
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 29.4 | 2.62 | 0.49 | 0.49 | No | OFFICES_ZN_1_FLR_1_WALL_1
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 29.4 | 2.62 | 0.49 | 0.49 | No | OFFICES_ZN_1_FLR_1_WALL_2
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 23.8 | 2.62 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_1_WALL_2
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_1_CEILING
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_1_CEILING
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 11.2 | 2.62 | 0.49 | 0.49 | No | KITCHEN_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 21 | 2.62 | 0.49 | 0.49 | No | CAFETERIA_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_NORTH | 29.4 | 2.62 | 0.49 | 0.49 | No | CAFETERIA_ZN_1_FLR_1_WALL_3
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 29.4 | 2.62 | 0.49 | 0.49 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_NORTH | 26.6 | 2.62 | 0.49 | 0.49 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
HEATSYS1 BOILER | Boiler:HotWater | 3572763.5 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 225587.26 | 3
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 170124.46 | 3
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 182427.1 | 3
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 217553.94 | 3
PSZ-AC_2:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 45090.88 | 3.69
PSZ-AC_1:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 54937.85 | 3.69
PSZ-AC_2:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 45790.13 | 3.69
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.67 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 0.02 | 0 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 2.26 | 0 | 1 | Zone Exhaust Fans
VAV_POD_1 FAN | Fan:VariableVolume | 0.28 | 655.15 | 13.63 | 32301.96 | 1 | Fan Energy
VAV_POD_2 FAN | Fan:VariableVolume | 0.28 | 655.15 | 10.28 | 24360.21 | 1 | Fan Energy
VAV_POD_3 FAN | Fan:VariableVolume | 0.28 | 655.15 | 11.02 | 26121.83 | 1 | Fan Energy
VAV_OTHER FAN | Fan:VariableVolume | 0.28 | 655.15 | 13.14 | 31151.66 | 1 | Fan Energy
PSZ-AC_2:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 2.72 | 3891.34 | 1 | General
PSZ-AC_1:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.32 | 4741.14 | 1 | General
PSZ-AC_2:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 2.77 | 3951.69 | 1 | General
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002148 | 98758.99 | 3496.5
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00732 | 336579.52 | 11916.37
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001315 | 60465.69 | 2140.75
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001565 | 71967.27 | 2547.95
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00389 | 178882.74 | 6333.22
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002115 | 97264.18 | 3443.57
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.007079 | 325473.97 | 11523.19
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001299 | 59750.64 | 2115.43
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001567 | 72036.29 | 2550.4
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003897 | 179172 | 6343.46
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002119 | 97409.37 | 3448.71
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.007113 | 327062.14 | 11579.42
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001328 | 61082.78 | 2162.59
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001591 | 73152 | 2589.9
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002691 | 123750.6 | 4381.31
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001825 | 83900.61 | 2970.44
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002831 | 130185.64 | 4609.14
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002268 | 104286.24 | 3692.18
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001341 | 61655.05 | 2182.86
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001488 | 68423.64 | 2422.49
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004542 | 208853.39 | 7394.31
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003405 | 156561.28 | 5542.95
VAV_POD_1_HEATC | 0.003816 | 175481.89 | 2326.11
VAV_POD_2_HEATC | 0.003277 | 150686.32 | 1938.25
VAV_POD_3_HEATC | 0.003045 | 140022.64 | 1861.59
VAV_OTHER_HEATC | 0.002825 | 129898.62 | 1818.91
Nominal Capacity [W]
PSZ-AC_2:5_UNITARY_PACKAGE_HEATCOIL | 107679.68
PSZ-AC_1:6_UNITARY_PACKAGE_HEATCOIL | 231763.01
PSZ-AC_2:7_UNITARY_PACKAGE_HEATCOIL | 222010.22
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 171228.2439 | 181.6539 | 549.0342 | 0 | 0.0021 | 110096.7597 | 63297.0474
February | 148618.424 | 158.8232 | 500.717 | 0 | 0.0019 | 100415.5962 | 55116.8511
March | 133276.961 | 147.2744 | 550.4139 | 0 | 0.002 | 110413.0919 | 50173.0335
April | 85293.1394 | 98.8601 | 448.6753 | 0 | 0.0016 | 90028.4361 | 32818.4696
May | 70315.0249 | 86.1711 | 467.6175 | 0 | 0.0016 | 93848.4567 | 27774.181
June | 74866.3683 | 92.6804 | 517.3761 | 0 | 0.0018 | 103837.7906 | 29715.3106
July | 59726.4288 | 73.261 | 398.5859 | 0 | 0.0014 | 79994.3914 | 23601.9187
August | 62791.2176 | 75.829 | 394.1154 | 0 | 0.0013 | 79093.3131 | 24629.696
September | 68107.2455 | 82.0749 | 423.843 | 0 | 0.0015 | 85058.6177 | 26688.1277
October | 100769.6084 | 115.1066 | 494.6949 | 0 | 0.0017 | 99255.5042 | 38513.0592
November | 143283.7444 | 155.702 | 536.7164 | 0 | 0.002 | 107651.6069 | 53535.4237
December | 160821.5723 | 172.1237 | 547.2597 | 0 | 0.002 | 109751.1169 | 59682.4593
Annual Sum or Average | 1279097.9785 | 1439.5602 | 5829.0494 | 0 | 0.0207 | 1169444.6814 | 485545.5778
Minimum of Months | 59726.4288 | 73.261 | 394.1154 | 0 | 0.0013 | 79093.3131 | 23601.9187
Maximum of Months | 171228.2439 | 181.6539 | 550.4139 | 0 | 0.0021 | 110413.0919 | 63297.0474
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 387938000000 | 236074.035 | 13-JAN-10:09 | 84768.624 | 81262.495 | 60297.5 | 0 | 0 | 3925 | 3517.925 | 0 | 0 | 0 | 0 | 0 | 2302.492 | 0 | 0
February | 353825000000 | 232003.736 | 03-FEB-11:50 | 84768.624 | 81262.495 | 60297.5 | 0 | 0 | 0 | 2114.775 | 0 | 0 | 0 | 0 | 0 | 3560.343 | 0 | 0
March | 389052000000 | 230984.868 | 31-MAR-10:50 | 84768.624 | 81262.495 | 60297.5 | 0 | 825.065 | 0 | 74.035 | 0 | 0 | 0 | 0 | 0 | 3757.149 | 0 | 0
April | 317225000000 | 231860.144 | 24-APR-10:39 | 84768.624 | 81262.495 | 60297.5 | 0 | 1756.652 | 0 | 16.706 | 0 | 0 | 0 | 0 | 0 | 3758.169 | 0 | 0
May | 330685000000 | 294950.72 | 30-MAY-11:00 | 84768.624 | 81262.495 | 60297.5 | 0 | 66111.357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2510.744 | 0 | 0
June | 365884000000 | 334388.095 | 21-JUN-13:00 | 84768.624 | 77263.149 | 60297.5 | 0 | 109452.757 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 2606.062 | 0 | 0
July | 281869000000 | 264245.699 | 03-JUL-15:00 | 47093.68 | 41275.62 | 60297.5 | 0 | 113100.49 | 0 | 1.247 | 0 | 0 | 0 | 0 | 0 | 2477.162 | 0 | 0
August | 278694000000 | 251206.723 | 15-AUG-15:00 | 47093.68 | 41275.62 | 60297.5 | 0 | 100071.384 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 2468.537 | 0 | 0
September | 299713000000 | 268479.246 | 07-SEP-15:00 | 84768.624 | 75197.923 | 60297.5 | 0 | 45795.2 | 0 | 1.214 | 0 | 0 | 0 | 0 | 0 | 2418.784 | 0 | 0
October | 349738000000 | 241950.252 | 03-OCT-14:00 | 84768.624 | 74411.28 | 60297.5 | 0 | 19952.565 | 0 | 4.523 | 0 | 0 | 0 | 0 | 0 | 2515.761 | 0 | 0
November | 379322000000 | 232309.471 | 30-NOV-10:20 | 84768.624 | 80410.298 | 60297.5 | 0 | 0 | 3925 | 559.851 | 0 | 0 | 0 | 0 | 0 | 2348.198 | 0 | 0
December | 386720000000 | 234510.116 | 29-DEC-11:09 | 84768.624 | 80410.298 | 60297.5 | 0 | 0 | 3925 | 1636.389 | 0 | 0 | 0 | 0 | 0 | 3472.305 | 0 | 0
Annual Sum or Average | 4120660000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 278694000000 | 230984.868 |  | 47093.68 | 41275.62 | 60297.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2302.492 | 0 | 0
Maximum of Months | 389052000000 | 334388.095 |  | 84768.624 | 81262.495 | 60297.5 | 0 | 113100.49 | 3925 | 3517.925 | 0 | 0 | 0 | 0 | 0 | 3758.169 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 107742.83 | 37313.08 | 0 | 145055.91
Cost per Total Building Area ($/m2) | 15.68 | 5.43 | 0 | 21.11
Cost per Net Conditioned Building Area ($/m2) | 15.68 | 5.43 | 0 | 21.11
Refresh All Data

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago-O'hare | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7A | 8A
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 45.6 | 310.9 | 58.3 | 331.2 | 294.4 | 45 | 13.5 | 725.5 | 19.8 | 78.2 | 849.9 | 131.1 | 146 | 19 | 32.3 | 3.69
Fabric
Exterior walls
| Construction Type | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed
| R-value (m2·K / W) | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 2.0964 | 2.0964 | 2.0964 | 2.0964 | 2.7473 | 2.7473
Roof
| Construction Type | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck
| R-value (m2·K / W) | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 3.663
Window
| U-Factor (W / m2·K) | 6.88 | 6.88 | 6.88 | 3.24 | 3.24 | 3.24 | 6.88 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 2.62
| SHGC | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.34 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.49 | 0.49
| Visible transmittance | 0.25 | 0.25 | 0.25 | 0.318 | 0.318 | 0.318 | 0.34 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.49 | 0.49
Skylights/TDD
| U-Factor (W / m2·K) | 6.92 | 6.92 | 6.92 | 6.92 | 6.92 | 6.92 | 6.92 | 3.92 | 3.92 | 3.92 | 3.92 | 3.92 | 3.92 | 3.92 | 3.92 | 3.3
| SHGC | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.61 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49
| Visible transmittance | 0.457 | 0.457 | 0.457 | 0.457 | 0.457 | 0.457 | 0.775 | 0.622 | 0.622 | 0.622 | 0.622 | 0.622 | 0.622 | 0.622 | 0.49 | 0.49
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 10 cm slab-on-grade | 10 cm slab-on-grade | 10 cm slab-on-grade | 10 cm slab-on-grade | 10 cm slab-on-grade | 10 cm slab-on-grade | 10 cm slab-on-grade | 10 cm slab-on-grade | 10 cm slab-on-grade | 10 cm slab-on-grade | 10 cm slab-on-grade | 10 cm slab-on-grade | 10 cm slab-on-grade | 10 cm slab-on-grade | 10 cm slab-on-grade | 10 cm slab-on-grade
| R-value (m2·K / W) | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463
HVAC
HVAC Sizing
Air Conditioning (kW)
| VAV_POD_1_COOLC DXCOIL | 247.7967 | 250.492 | 299.1291 | 235.2048 | 208.0929 | 280.9178 | 342.5829 | 251.9231 | 289.9428 | 240.818 | 244.7963 | 279.5289 | 245.8895 | 265.1021 | 242.8143 | 225.5873
| VAV_POD_2_COOLC DXCOIL | 199.3052 | 200.4229 | 238.5466 | 187.8712 | 163.5129 | 224.2162 | 272.8031 | 197.4971 | 227.0074 | 184.3965 | 191.7654 | 218.5478 | 191.7047 | 205.4695 | 187.0958 | 170.1245
| VAV_POD_3_COOLC DXCOIL | 197.8784 | 200.6898 | 239.8328 | 189.2338 | 168.0087 | 225.4786 | 276.7619 | 202.5191 | 232.2139 | 194.842 | 196.9495 | 224.5911 | 198.012 | 213.5895 | 195.6373 | 182.4271
| VAV_OTHER_COOLC DXCOIL | 287.8612 | 282.3993 | 324.8522 | 264.55 | 230.4491 | 310.6903 | 316.8964 | 273.9146 | 315.7597 | 247.5459 | 266.7677 | 303.8735 | 264.7257 | 282.4546 | 256.829 | 217.5539
| PSZ-AC_2:5_UNITARY_PACKAGE_COOLCOIL | 73.9669 | 72.5489 | 64.18 | 65.4039 | 46.4423 | 61.3139 | 67.2115 | 67.0216 | 65.7869 | 48.7387 | 65.8283 | 63.4886 | 61.331 | 58.319 | 52.7058 | 45.0909
| PSZ-AC_1:6_UNITARY_PACKAGE_COOLCOIL | 87.6259 | 85.9902 | 85.2133 | 86.9703 | 53.4857 | 71.6567 | 65.3849 | 85.2565 | 66.8849 | 54.6832 | 85.1297 | 65.7134 | 85.6127 | 62.2594 | 73.0791 | 54.9378
| PSZ-AC_2:7_UNITARY_PACKAGE_COOLCOIL | 97.0392 | 96.3779 | 88.1586 | 90.6972 | 50.0684 | 71.886 | 91.1907 | 89.4153 | 70.8776 | 50.7603 | 86.9921 | 67.4498 | 86.1352 | 61.4907 | 67.4926 | 45.7901
Heating (kW)
| HEATSYS1 BOILER | 3597.9842 | 3700.1743 | 4112.8634 | 3424.5316 | 2998.7872 | 3792.0591 | 4671.8465 | 3755.7062 | 3512.4118 | 3440.7539 | 3700.3263 | 3485.9336 | 3728.147 | 3556.8214 | 3617.436 | 3572.7635
| PSZ-AC_2:5_UNITARY_PACKAGE_HEATCOIL | 41.4648 | 54.7392 | 46.1832 | 59.0495 | 43.1251 | 49.9252 | 47.6675 | 65.7326 | 52.2282 | 56.8462 | 76.7893 | 63.8349 | 82.9866 | 75.6209 | 84.9432 | 107.6797
| PSZ-AC_1:6_UNITARY_PACKAGE_HEATCOIL | 91.3595 | 120.6071 | 101.7557 | 130.104 | 95.0178 | 110.0005 | 105.0261 | 144.8291 | 115.0747 | 125.2496 | 169.1903 | 140.6479 | 182.8449 | 166.6161 | 187.1557 | 231.763
| PSZ-AC_2:7_UNITARY_PACKAGE_HEATCOIL | 87.5151 | 115.5319 | 97.4737 | 124.6291 | 91.0194 | 105.3716 | 100.6065 | 138.7345 | 110.2322 | 119.979 | 162.0706 | 134.7293 | 175.1507 | 159.6047 | 179.28 | 222.0102
HVAC Efficiency
Air Conditioning (COP)
| VAV_POD_1_COOLC DXCOIL | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| VAV_POD_2_COOLC DXCOIL | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| VAV_POD_3_COOLC DXCOIL | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| VAV_OTHER_COOLC DXCOIL | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| PSZ-AC_2:5_UNITARY_PACKAGE_COOLCOIL | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69
| PSZ-AC_1:6_UNITARY_PACKAGE_COOLCOIL | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69
| PSZ-AC_2:7_UNITARY_PACKAGE_COOLCOIL | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69
| Heating Efficiency (%) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
HVAC Control
| Economizer | None | None | Fixed Dry Bulb | None | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | None | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb
Fan Max Flow Rate (m3/s )
| BATH_ZN_1_FLR_1 EXHAUST FAN | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28
| KITCHEN_ZN_1_FLR_1 EXHAUST FAN | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
| CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | 2.26 | 2.26 | 2.26 | 2.26 | 2.26 | 2.26 | 2.26 | 2.26 | 2.26 | 2.26 | 2.26 | 2.26 | 2.26 | 2.26 | 2.26 | 2.26
| VAV_POD_1 FAN | 14.97 | 15.13 | 18.07 | 14.21 | 12.57 | 16.97 | 20.7 | 15.22 | 17.52 | 14.55 | 14.79 | 16.89 | 14.85 | 16.01 | 14.67 | 13.63
| VAV_POD_2 FAN | 12.04 | 12.11 | 14.41 | 11.35 | 9.88 | 13.54 | 16.48 | 11.93 | 13.71 | 11.14 | 11.58 | 13.2 | 11.58 | 12.41 | 11.3 | 10.28
| VAV_POD_3 FAN | 11.95 | 12.12 | 14.49 | 11.43 | 10.15 | 13.62 | 16.72 | 12.23 | 14.03 | 11.77 | 11.9 | 13.57 | 11.96 | 12.9 | 11.82 | 11.02
| VAV_OTHER FAN | 17.39 | 17.06 | 19.62 | 15.98 | 13.92 | 18.77 | 19.14 | 16.55 | 19.08 | 14.95 | 16.12 | 18.36 | 15.99 | 17.06 | 15.52 | 13.14
| PSZ-AC_2:5_UNITARY_PACKAGE_FAN | 3.48 | 3.42 | 3.8 | 3.26 | 2.81 | 3.7 | 4.06 | 3.39 | 3.97 | 2.94 | 3.33 | 3.84 | 3.3 | 3.52 | 3.18 | 2.72
| PSZ-AC_1:6_UNITARY_PACKAGE_FAN | 3.53 | 3.46 | 3.7 | 3.5 | 3.23 | 3.72 | 3.95 | 3.43 | 4.04 | 3.3 | 3.43 | 3.97 | 3.45 | 3.76 | 3.43 | 3.32
| PSZ-AC_2:7_UNITARY_PACKAGE_FAN | 3.91 | 3.88 | 4.43 | 3.65 | 3.02 | 4.15 | 5.51 | 3.6 | 4.28 | 3.07 | 3.5 | 4.07 | 3.47 | 3.71 | 3.32 | 2.77
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.089288 | 0.11939 | 0.088959 | 0.097495 | 0.12896 | 0.099237 | 0.14966 | 0.078608 | 0.037075 | 0.076438 | 0.087659 | 0.037081 | 0.060871 | 0.07686 | 0.059659 | 0.094129
| Total Cost ($/m2) | 21.27 | 21.27 | 21.27 | 21.27 | 21.27 | 21.27 | 21.27 | 21.27 | 21.27 | 21.27 | 21.27 | 21.27 | 21.27 | 21.27 | 21.27 | 21.27
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011454 | 0.004862 | 0.0051374 | 0.0037789 | 0.0070292 | 0.0050848 | 0.0024185 | 0.002398 | 0.0035395 | 0.0027798 | 0.0017585 | 0.0024342 | 0.0012445 | 0.0015901 | 0.0010324 | 0.00060813
| Total Cost ($/m2) | 0.8 | 1.34 | 1.31 | 2.14 | 0.97 | 1.25 | 2.81 | 3.28 | 1.59 | 2.42 | 3.84 | 2.3 | 5.11 | 4.14 | 6.14 | 5.43
Total Utility Costs
| Cost Intensity ($/m2) | 22.07 | 27.73 | 21 | 21.19 | 23.69 | 21.26 | 31.22 | 18.59 | 8.64 | 14.82 | 20 | 9.1 | 16.28 | 17.68 | 16.48 | 21.11
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 620188.8889 | 500205.5556 | 459780.5556 | 335277.7778 | 250825 | 340888.8889 | 222044.4444 | 301711.1111 | 234222.2222 | 119058.3333 | 219405.5556 | 183311.1111 | 195233.3333 | 136491.6667 | 120666.6667 | 80991.6667
| Interior Lighting | 360552.7778 | 360552.7778 | 360552.7778 | 360552.7778 | 360552.7778 | 360552.7778 | 360552.7778 | 360552.7778 | 360552.7778 | 360552.7778 | 360552.7778 | 360552.7778 | 360552.7778 | 360552.7778 | 360552.7778 | 360552.7778
| Exterior Lighting | 17155.5556 | 17150 | 17147.2222 | 17144.4444 | 17130.5556 | 17127.7778 | 17136.1111 | 17125 | 17133.3333 | 17097.2222 | 17127.7778 | 17119.4444 | 17116.6667 | 17113.8889 | 17102.7778 | 16997.2222
| Interior Equipment | 348925 | 348925 | 348925 | 348925 | 348925 | 348925 | 348925 | 348925 | 348925 | 348925 | 348925 | 348925 | 348925 | 348925 | 348925 | 348925
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 267027.7778 | 268872.2222 | 311841.6667 | 258219.4444 | 210708.3333 | 295808.3333 | 332716.6667 | 287441.6667 | 323819.4444 | 247175 | 297630.5556 | 326108.3333 | 316602.7778 | 325030.5556 | 321363.8889 | 313761.1111
| Pumps | 19.4444 | 175 | 175 | 241.6667 | 97.2222 | 175 | 494.4444 | 419.4444 | 261.1111 | 355.5556 | 600 | 408.3333 | 927.7778 | 711.1111 | 1161.1111 | 2338.8889
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 23086.1111 | 22827.7778 | 22511.1111 | 22505.5556 | 22697.2222 | 22305.5556 | 22313.8889 | 22208.3333 | 22183.3333 | 22116.6667 | 21977.7778 | 21983.3333 | 21797.2222 | 21750 | 21525 | 21061.1111
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1636955.5556 | 1518708.3333 | 1520930.5556 | 1342866.6667 | 1210936.1111 | 1385780.5556 | 1304183.3333 | 1338380.5556 | 1307094.4445 | 1115280.5556 | 1266219.4445 | 1258402.7778 | 1261155.5556 | 1210569.4445 | 1191297.2222 | 1144627.7778
Gas (MJ)
| Heating | 72080 | 710010 | 655960 | 1021990 | 351810 | 657500 | 1835830 | 1851720 | 1112300 | 1532220 | 2678880 | 1809450 | 3965690 | 3002290 | 4864030 | 8575260
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 361030 | 361030 | 361030 | 361030 | 361030 | 361030 | 361030 | 361030 | 361030 | 361030 | 361030 | 361030 | 361030 | 361030 | 361030 | 361030
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 48150 | 62750 | 56030 | 75750 | 71400 | 65580 | 82430 | 86090 | 84120 | 89800 | 94910 | 94100 | 102750 | 103490 | 114510 | 128430
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 481260 | 1133790 | 1073020 | 1458780 | 784230 | 1084110 | 2279290 | 2298850 | 1557450 | 1983050 | 3134820 | 2264580 | 4429460 | 3466810 | 5339570 | 9064720
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 6374300 | 6601140 | 6548370 | 6293090 | 5143600 | 6072930 | 6974350 | 7117020 | 6262990 | 5998060 | 7693210 | 6794830 | 8969630 | 7824860 | 9628240 | 13185380
| On-Site Production (MJ) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 324.9425 | 262.0783 | 240.898 | 175.6658 | 131.4176 | 178.6057 | 116.3382 | 158.0789 | 122.7187 | 62.3796 | 114.9556 | 96.0442 | 102.2908 | 71.5136 | 63.2222 | 42.4349
| Interior Lighting (elec) | 188.9085 | 188.9085 | 188.9085 | 188.9085 | 188.9085 | 188.9085 | 188.9085 | 188.9085 | 188.9085 | 188.9085 | 188.9085 | 188.9085 | 188.9085 | 188.9085 | 188.9085 | 188.9085
| Exterior Lighting (elec) | 8.9885 | 8.9856 | 8.9841 | 8.9827 | 8.9754 | 8.9739 | 8.9783 | 8.9725 | 8.9769 | 8.9579 | 8.9739 | 8.9696 | 8.9681 | 8.9667 | 8.9608 | 8.9055
| Interior Equipment (elec) | 182.8162 | 182.8162 | 182.8162 | 182.8162 | 182.8162 | 182.8162 | 182.8162 | 182.8162 | 182.8162 | 182.8162 | 182.8162 | 182.8162 | 182.8162 | 182.8162 | 182.8162 | 182.8162
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 139.9069 | 140.8732 | 163.3867 | 135.2918 | 110.3988 | 154.9862 | 174.324 | 150.6025 | 169.6623 | 129.5052 | 155.9409 | 170.8616 | 165.8812 | 170.2969 | 168.3758 | 164.3924
| Pumps (elec) | 0.010188 | 0.09169 | 0.09169 | 0.12662 | 0.050939 | 0.09169 | 0.25906 | 0.21976 | 0.13681 | 0.18629 | 0.31436 | 0.21394 | 0.4861 | 0.37258 | 0.60835 | 1.2254
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 12.0958 | 11.9604 | 11.7945 | 11.7916 | 11.892 | 11.6868 | 11.6912 | 11.6359 | 11.6228 | 11.5878 | 11.5151 | 11.518 | 11.4205 | 11.3957 | 11.2778 | 11.0348
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 857.6685 | 795.7139 | 796.8782 | 703.5832 | 634.4593 | 726.0675 | 683.3154 | 701.2327 | 684.8406 | 584.3414 | 663.4245 | 659.3291 | 660.7714 | 634.2672 | 624.1697 | 599.7177
Gas (MJ/m2)
| Heating (gas) | 10.4905 | 103.3343 | 95.4679 | 148.7396 | 51.2022 | 95.692 | 267.1853 | 269.4979 | 161.8833 | 222.9981 | 389.8821 | 263.3459 | 577.1634 | 436.951 | 707.9071 | 1248.0367
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 52.544 | 52.544 | 52.544 | 52.544 | 52.544 | 52.544 | 52.544 | 52.544 | 52.544 | 52.544 | 52.544 | 52.544 | 52.544 | 52.544 | 52.544 | 52.544
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 7.0077 | 9.1326 | 8.1546 | 11.0246 | 10.3915 | 9.5445 | 11.9968 | 12.5295 | 12.2428 | 13.0694 | 13.8131 | 13.6952 | 14.9542 | 15.0619 | 16.6657 | 18.6916
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 70.0422 | 165.0109 | 156.1665 | 212.3097 | 114.1362 | 157.7805 | 331.7261 | 334.5728 | 226.6701 | 288.6116 | 456.2393 | 329.5852 | 644.6602 | 504.5568 | 777.1169 | 1319.2723
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 927.7107 | 960.7248 | 953.0447 | 915.8914 | 748.5955 | 883.8495 | 1015.0415 | 1035.8056 | 911.5107 | 872.953 | 1119.6638 | 988.9143 | 1305.433 | 1138.824 | 1401.2866 | 1918.99
| On-Site Production (MJ/m2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 438.9723 | 426.9924 | 358.4213 | 317.0102 | 325.7471 | 329.2137 | 335.4902 | 322.6694 | 301.9872 | 249.1791 | 251.5773 | 315.6687 | 242.0153 | 248.7968 | 240.5937 | 236.074
| Feb | 444.2025 | 397.3915 | 368.4923 | 322.4534 | 323.8522 | 336.372 | 389.9357 | 303.9039 | 332.0152 | 289.5964 | 251.3162 | 290.4454 | 242.473 | 311.4806 | 241.2366 | 232.0037
| Mar | 449.8295 | 417.1589 | 403.7054 | 344.3927 | 317.7363 | 351.4635 | 373.2258 | 376.3593 | 338.8811 | 304.7439 | 323.0182 | 335.4636 | 294.1987 | 319.8051 | 241.8803 | 230.9849
| Apr | 457.674 | 432.9837 | 416.3544 | 383.5066 | 343.119 | 399.5775 | 388.7307 | 367.2086 | 361.6769 | 294.2905 | 350.2043 | 355.866 | 326.8942 | 310.8452 | 290.0762 | 231.8601
| May | 498.5224 | 489.9998 | 458.7562 | 414.636 | 366.493 | 429.3134 | 426.8663 | 426.7378 | 387.4082 | 347.7028 | 408.9563 | 375.4424 | 410.9212 | 343.3906 | 325.6339 | 294.9507
| Jun | 507.7561 | 479.062 | 556.4514 | 438.1963 | 352.2837 | 512.06 | 410.1026 | 486.3547 | 418.215 | 352.4519 | 490.9117 | 400.4659 | 452.3996 | 417.5931 | 407.8224 | 334.3881
| Jul | 415.2866 | 451.9444 | 482.717 | 403.5697 | 284.1144 | 417.279 | 352.7827 | 438.0703 | 349.0912 | 296.923 | 398.3543 | 339.581 | 381.7841 | 312.3149 | 332.7466 | 264.2457
| Aug | 431.3134 | 424.4806 | 470.2562 | 379.8795 | 309.2571 | 416.5737 | 350.4899 | 436.5473 | 361.7893 | 282.6693 | 396.8623 | 340.493 | 371.6862 | 301.2706 | 324.7921 | 251.2067
| Sep | 486.2108 | 500.9618 | 508.0366 | 426.8817 | 368.3654 | 433.1345 | 448.3796 | 426.4472 | 405.0529 | 354.6579 | 409.9395 | 378.2468 | 398.3894 | 367.094 | 393.4502 | 268.4792
| Oct | 479.5012 | 460.9671 | 443.3213 | 390.9072 | 353.3747 | 412.0483 | 409.1741 | 414.6516 | 373.5698 | 317.7867 | 389.1931 | 361.0305 | 329.734 | 335.5635 | 304.0979 | 241.9503
| Nov | 455.1365 | 436.5753 | 392.2354 | 346.6665 | 336.5433 | 344.5373 | 369.8142 | 384.8395 | 328.9912 | 304.5199 | 385.1932 | 329.6862 | 311.4247 | 284.2416 | 273.2672 | 232.3095
| Dec | 423.1101 | 409.4548 | 376.1508 | 336.8267 | 327.4812 | 339.5202 | 336.3673 | 284.074 | 293.9861 | 237.7274 | 252.4109 | 287.1885 | 240.8775 | 248.6856 | 240.0854 | 234.5101
Time of Peak Electrical Demand
| Jan | 06-JAN-11:50 | 03-JAN-11:50 | 27-JAN-14:00 | 24-JAN-14:00 | 26-JAN-12:00 | 18-JAN-14:00 | 06-JAN-15:00 | 09-JAN-11:50 | 25-JAN-14:00 | 27-JAN-12:00 | 17-JAN-12:00 | 27-JAN-11:50 | 30-JAN-10:20 | 30-JAN-11:50 | 13-JAN-11:50 | 13-JAN-10:09
| Feb | 23-FEB-11:50 | 21-FEB-11:39 | 28-FEB-14:00 | 21-FEB-14:09 | 13-FEB-11:50 | 08-FEB-14:00 | 15-FEB-14:00 | 15-FEB-12:00 | 14-FEB-14:00 | 21-FEB-13:00 | 28-FEB-11:09 | 07-FEB-14:00 | 27-FEB-11:20 | 02-FEB-14:00 | 24-FEB-11:50 | 03-FEB-11:50
| Mar | 14-MAR-10:39 | 24-MAR-11:00 | 17-MAR-15:09 | 28-MAR-11:00 | 31-MAR-10:50 | 31-MAR-13:00 | 01-MAR-12:00 | 09-MAR-13:00 | 02-MAR-14:00 | 29-MAR-13:00 | 31-MAR-14:00 | 30-MAR-13:00 | 23-MAR-15:50 | 30-MAR-13:00 | 16-MAR-10:50 | 31-MAR-10:50
| Apr | 03-APR-13:00 | 10-APR-11:00 | 26-APR-13:00 | 13-APR-13:00 | 11-APR-13:50 | 21-APR-14:00 | 28-APR-11:39 | 04-APR-11:00 | 21-APR-13:00 | 14-APR-13:00 | 03-APR-13:00 | 25-APR-13:00 | 27-APR-13:00 | 06-APR-13:00 | 04-APR-14:00 | 24-APR-10:39
| May | 22-MAY-06:10 | 18-MAY-13:00 | 30-MAY-13:00 | 22-MAY-13:00 | 30-MAY-12:00 | 31-MAY-15:00 | 25-MAY-11:00 | 16-MAY-10:39 | 30-MAY-13:00 | 05-MAY-13:00 | 30-MAY-15:00 | 24-MAY-13:00 | 31-MAY-11:00 | 17-MAY-13:00 | 31-MAY-13:00 | 30-MAY-11:00
| Jun | 26-JUN-10:00 | 13-JUN-14:00 | 08-JUN-14:00 | 08-JUN-14:00 | 23-JUN-10:50 | 27-JUN-15:00 | 15-JUN-12:00 | 30-JUN-13:00 | 29-JUN-13:00 | 28-JUN-12:00 | 08-JUN-12:00 | 28-JUN-11:00 | 29-JUN-13:00 | 30-JUN-12:00 | 14-JUN-14:00 | 21-JUN-13:00
| Jul | 13-JUL-11:00 | 18-JUL-11:00 | 11-JUL-15:00 | 03-JUL-11:00 | 10-JUL-09:00 | 24-JUL-15:00 | 03-JUL-11:00 | 25-JUL-11:00 | 03-JUL-14:00 | 24-JUL-14:00 | 14-JUL-10:50 | 19-JUL-12:00 | 13-JUL-15:00 | 19-JUL-13:00 | 07-JUL-11:00 | 03-JUL-15:00
| Aug | 21-AUG-13:00 | 31-AUG-10:00 | 01-AUG-15:00 | 17-AUG-11:00 | 08-AUG-09:00 | 03-AUG-11:00 | 15-AUG-11:00 | 09-AUG-14:00 | 01-AUG-13:00 | 07-AUG-14:00 | 04-AUG-15:00 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-14:00 | 15-AUG-15:00
| Sep | 18-SEP-11:00 | 15-SEP-13:00 | 25-SEP-13:00 | 11-SEP-13:00 | 25-SEP-14:00 | 21-SEP-13:00 | 28-SEP-15:09 | 05-SEP-10:39 | 05-SEP-11:30 | 13-SEP-15:00 | 06-SEP-10:00 | 05-SEP-13:00 | 22-SEP-13:30 | 12-SEP-13:00 | 08-SEP-12:20 | 07-SEP-15:00
| Oct | 06-OCT-13:00 | 30-OCT-12:00 | 03-OCT-09:30 | 12-OCT-15:00 | 05-OCT-10:50 | 06-OCT-12:00 | 17-OCT-11:39 | 03-OCT-10:39 | 03-OCT-11:00 | 17-OCT-12:00 | 30-OCT-11:20 | 05-OCT-13:00 | 06-OCT-14:00 | 06-OCT-13:00 | 27-OCT-11:00 | 03-OCT-14:00
| Nov | 01-NOV-11:50 | 27-NOV-12:00 | 13-NOV-14:00 | 22-NOV-12:00 | 07-NOV-12:00 | 10-NOV-12:00 | 16-NOV-15:00 | 03-NOV-11:50 | 08-NOV-14:00 | 03-NOV-12:00 | 02-NOV-11:50 | 10-NOV-13:00 | 02-NOV-14:00 | 21-NOV-11:50 | 09-NOV-11:50 | 30-NOV-10:20
| Dec | 15-DEC-14:00 | 20-DEC-11:50 | 13-DEC-12:39 | 26-DEC-14:00 | 19-DEC-12:00 | 05-DEC-12:00 | 07-DEC-14:00 | 08-DEC-10:09 | 08-DEC-14:00 | 13-DEC-11:50 | 12-DEC-12:00 | 21-DEC-14:00 | 26-DEC-11:50 | 06-DEC-11:50 | 26-DEC-11:50 | 29-DEC-11:09
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 589.92 | 589.92 | 589.92 | 589.92 | 589.92 | 589.92 | 589.92 | 589.92 | 589.92 | 589.92 | 589.92 | 589.92 | 589.92 | 589.92 | 589.92 | 589.92
| Total Building | 589.92 | 589.92 | 589.92 | 589.92 | 589.92 | 589.92 | 589.92 | 589.92 | 589.92 | 589.92 | 589.92 | 589.92 | 589.92 | 589.92 | 589.92 | 589.92
Emissions
| Carbon Equivalent (kg) | 457612.7398 | 527026.9938 | 478480.8822 | 439957.5677 | 155658.8502 | 486939.0714 | 193516.0939 | 402624.1002 | 562030.4502 | 116990.3202 | 731612.8563 | 554891.9791 | 511560.4102 | 504903.7753 | 504059.183 | 485545.5778
| CO2 (kg) | 1064605.2202 | 1330229.0811 | 1135642.9183 | 1014826.5161 | 418685.0698 | 1163500.1894 | 525671.502 | 929705.1513 | 1325287.764 | 296278.5267 | 1720925.0158 | 1315783.7263 | 1225979.2366 | 1209557.1979 | 1218267.111 | 1279097.9785
| NOX (kg) | 1856.087 | 1724.4501 | 1875.6873 | 1881.8689 | 360.4286 | 1866.7081 | 456.0427 | 1728.124 | 2256.5672 | 403.8376 | 2984.5055 | 2208.6994 | 2025.5796 | 1990.4403 | 1968.0278 | 1439.5602
| SO2 (kg) | 7006.948 | 7244.5413 | 6116.2513 | 4713.8497 | 3523.8882 | 7623.1989 | 3795.6253 | 4886.2448 | 5708.2369 | 862.5544 | 8534.1412 | 5495.8051 | 2977.7191 | 3233.2975 | 2813.0798 | 5829.0494
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.032 | 0.0205 | 0.0167 | 0.0174 | 0.0017 | 0.0144 | 0.0019 | 0.0199 | 0.0224 | 0.0036 | 0.0261 | 0.0216 | 0.0222 | 0.0228 | 0.0211 | 0.0207
| Water Environmental Factors (m3) | 867.1896 | 2471.116 | 45178.3 | 8384.315 | 21261.3 | 38017.5 | 22898.5 | 303.863 | 5935.2523 | 11394.6 | 1964.4626 | 5714.159 | 1956.6094 | 76682.6 | 1848.2242 | 1169.4447

## Picture
DOE Commercial Building Benchmark - Primary School

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | HoursPerDay | HoursPerWeek | HoursPerYear
BLDG_LIGHT_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | 14.37 | 80.38 | 3909.96
|  |  | WE, WinterDesign, Hol, Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
|  | Through 9/1 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 8.13 | 49.15
|  |  | WE, WinterDesign, Hol, Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
|  | Through 12/31 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | 14.37 | 80.38
|  |  | WE, WinterDesign, Hol, Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
BLDG_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 13.8 | 85.8 | 4180.91
|  |  | WE, WinterDesign, Hol, Other | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
|  | Through 9/1 | WD, SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 8.25 | 53.25
|  |  | WE, WinterDesign, Hol, Other | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  | Through 12/31 | WD, SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 13.8 | 85.8
|  |  | WE, WinterDesign, Hol, Other | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
KITCHEN_ELEC_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 20.05 | 1045.46
|  |  | WE, WinterDesign, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
|  | Through 9/1 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 20.05
|  |  | WE, WinterDesign, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
|  | Through 12/31 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 20.05
|  |  | WE, WinterDesign, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
KITCHEN_GAS_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 8.16 | 425.49
|  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
|  | Through 9/1 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 8.16
|  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
|  | Through 12/31 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 8.16
|  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
BLDG_OCC_SCH | Fraction | Through 6/15 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 8.35 | 41.75 | 1756.39
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/15 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 1.95 | 9.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 8.35 | 41.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Extend | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 12.35 | 61.75 | 2956.57
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 6.5 | 32.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 12.35 | 61.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Offices | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 9.15 | 45.75 | 2203.29
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 5.1 | 25.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 9.15 | 45.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Gym | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75 | 1833.39
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 4.55 | 22.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Cafeteria | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 7.45 | 37.25 | 1692.57
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | 1.9 | 9.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 7.45 | 37.25
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INFIL_SCH | Fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 17 | 119 | 6205
BLDG_SWH_SCH | Fraction | Through 6/15 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 6.91 | 36.19 | 1599.88
|  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
|  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
|  | Through 9/15 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 2.54 | 14.34
|  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
|  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
|  | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 6.91 | 36.19
|  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
|  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 1 to 24 24
ALWAYS_OFF | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 26.4 | 184.8 | 7800
|  | Through 09/30 | All | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 14.4 | 100.8
|  | Through 12/31 | All | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 26.4 | 184.8
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PlantOnSched | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 1 to 24 24
FAN_SCH | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 1 to 24 24
ReheatCoilAvailSched | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 1 to 24 24
CoolingCoilAvailSched | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 1 to 24 24
Humidity Setpoint Schedule | Humidity | Through 12/31 | All | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1560 | 10920 | 569400
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 03/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 09/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 1608 | 11256 | 586920
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
Kitchen_Exhaust_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 45 | 2137.86
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 7.15 | 35.75
|  |  | WE, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75
|  |  | WE, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 70 | 3650
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 70 | 3650
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HTGSETP_SCH | Temperature | Through 12/31 | SummerDesign | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 3038 | 158410
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | WD | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 454
|  |  | WE, Hol, Other | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
HTGSETP_SCH_Setback | Temperature | Through 12/31 | SummerDesign | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | WD | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
|  |  | WE, Hol, Other | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
CLGSETP_SCH | Temperature | Through 12/31 | SummerDesign | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456 | 4788 | 249660
|  |  | WinterDesign | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WE | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WD, Hol, Other | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 31 | 31 | 31 | 660
CLGSETP_SCH_Setup | Temperature | Through 12/31 | SummerDesign | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456 | 5208 | 271560
|  |  | WinterDesign | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WE | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WD, Hol, Other | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
MinOA_Sched | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 118 | 6152.86
|  |  | WE, WinterDesign, Hol, Other | [24 empty] | 24 | bar: 1 1 to 24 24
MinOA_MotorizedDamper_Sched | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 70 | 3650
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MinOA_Kitchen_Sched | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42 | 2.1 | 109.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
Bath_ZN_1_FLR_1 SHW_default Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Bath_ZN_1_FLR_1 SHW_default Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Bath_ZN_1_FLR_1 SHW_default Temp Sched | Temperature | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
Bath_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_ZN_1_FLR_1 SHW_default Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Kitchen_ZN_1_FLR_1 SHW_default Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Kitchen_ZN_1_FLR_1 SHW_default Temp Sched | Temperature | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
Kitchen_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
SHWSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SHWSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SHWSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720