## BuildingSummary
Building Summary Small Office new construction version 1.0_3.0
|  | Value | Data Source
Program
| Building Name | Benchmark Small Office
| Available Fuel Types | gas, electricity
| Principal Building Activity | Office
Form
| Total Floor Area (m2) | 511 | 2003 CBECS, ASHRAE Small Office 30% Advanced Energy Design Guide
| Building Shape | Rectangle
| Aspect Ratio | 1.5
| Number of Floors | 1
Window Fraction (Window to Wall Ratio)
| South | 0.244
| East | 0.198
| North | 0.198
| West | 0.198
| Total | 0.212
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | core zone with four perimeter zones
| Floor to Ceiling Height (m) | 3.05
| Roof type | Attic | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Mass wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 281.5
| Net Dimensions - Total Area (m2) | 222
| Wall to Skin Ratio | 0.32
Roof
| Construction Type | Attic | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 598.76
| Net Dimensions - Total Area (m2) | 598.76
| Roof to Skin Ratio | 0.68
Window Dimensions (m2)
| South | 16.73
| East | 11.16
| North | 16.73
| West | 11.16
| Total Area (m2) | 55.78
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 10 cm slab-on-grade
| Dimensions - Total Area (m2) | 511
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 0
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 1022.46
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.45 | See Benchmark Technical Report
HVAC
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | Unitary DX | 2003 CBECS
| Fan Control | Constant volume | 2003 CBECS
Service Water Heating
| SWH Type | gas water heater
| Fuel | gas
| Thermal Efficiency (%) | 80
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 17.65

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Core_ZN | Yes | 1 | 149.66 | 456.46 | 3.05 | 0 | 0 | 18.5806 | 8.0546 | 10.76 | 8.07 | 0 | 11.3562 | 10 | 0 | 80.5463 | 0 | 0
Perimeter_ZN_1 | Yes | 1 | 113.45 | 346.02 | 3.05 | 84.45 | 20.64 | 18.5806 | 6.1058 | 10.76 | 8.07 | 0 | 0 | 10 | 0 | 61.0582 | 0 | 0.62247
Perimeter_ZN_2 | Yes | 1 | 67.3 | 205.26 | 3.0499 | 56.3 | 11.16 | 18.5806 | 3.6221 | 10.76 | 8.07 | 0 | 0 | 10 | 0 | 36.2205 | 0 | 0.65537
Perimeter_ZN_3 | Yes | 1 | 113.45 | 346.02 | 3.05 | 84.45 | 16.73 | 18.5806 | 6.1058 | 10.76 | 8.07 | 0 | 0 | 10 | 0 | 61.0582 | 0 | 0.62247
Perimeter_ZN_4 | Yes | 1 | 67.3 | 205.26 | 3.0499 | 56.3 | 11.16 | 18.5806 | 3.6221 | 10.76 | 8.07 | 0 | 0 | 10 | 0 | 36.2205 | 0 | 0.65537
Attic | No | 1 | 567.98 | 720.19 | 1.268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
Total Conditioned Zones |  |  | 511.16 | 1559.02 |  | 281.5 | 59.69 |  | 27.5104
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report

## Query (hidden)
1-miami
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 319.31 | 295.89 | 624.67
Net Site Energy | 319.31 | 295.89 | 624.67
Total Source Energy | 1034.67 | 958.79 | 2024.16
Net Source Energy | 1034.67 | 958.79 | 2024.16
Area (m2)
Total Building Area | 1079.13
Net Conditioned Building Area | 511.16
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 0.3 | 0 | 0 | 0 | 0
Cooling | 96.7 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.83 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 65.3 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 10.69 | 0 | 0 | 0 | 17.65
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 308.31 | 11 | 0 | 0 | 0 | 17.65
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 308.31 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 308.31 | 100
Total On-Site and Utility Electric Sources | 308.31 | 100
Total Electricity End Uses | 308.31 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 90 | 180
ATTIC_SOFFIT_WEST | EXPOSED-FLOOR | 0.3 | 1.627 | 2.69 | 11.44 | 270 | 180
ATTIC_SOFFIT_SOUTH | EXPOSED-FLOOR | 0.3 | 1.627 | 2.69 | 16.97 | 225 | 180
ATTIC_SOFFIT_EAST | EXPOSED-FLOOR | 0.3 | 1.627 | 2.69 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | EXPOSED-FLOOR | 0.3 | 1.627 | 2.69 | 16.97 | 315 | 180
ATTIC_ROOF_NORTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 0 | 18.45
ATTIC_ROOF_WEST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 270 | 18.45
ATTIC_ROOF_EAST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 90 | 18.45
ATTIC_ROOF_SOUTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 180 | 18.45
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW_SOUTH | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW_SOUTH | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW_SOUTH | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW_SOUTH | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW_SOUTH | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW_SOUTH | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW_SOUTH | 3.91 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW_EAST | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW_EAST | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW_EAST | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW_EAST | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW_NORTH | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW_NORTH | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW_NORTH | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW_NORTH | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW_NORTH | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW_NORTH | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW_WEST | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW_WEST | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW_WEST | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW_WEST | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8873.05 | 3.05
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7788.87 | 3.05
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6479.22 | 3.05
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8310.36 | 3.05
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7304.77 | 3.05
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.46 | 870.61 | 1 | Fan Energy
PSZ-AC:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.4 | 753.08 | 1 | Fan Energy
PSZ-AC:3 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.35 | 670.3 | 1 | Fan Energy
PSZ-AC:4 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.44 | 826.59 | 1 | Fan Energy
PSZ-AC:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.41 | 782.57 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
Nominal Capacity [W]
PSZ-AC:1_HEATC | 4446.67
PSZ-AC:2_HEATC | 3723.35
PSZ-AC:3_HEATC | 3036.87
PSZ-AC:4_HEATC | 3995.32
PSZ-AC:5_HEATC | 3452.7
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 4013.7363 | 7.0249 | 26.6313 | 0 | 0.0001 | 3295.9458 | 1727.9988
February | 3761.1783 | 6.5956 | 25.0556 | 0 | 0.0001 | 3100.9412 | 1620.5404
March | 4457.5376 | 7.8195 | 29.716 | 0 | 0.0001 | 3677.7245 | 1920.8474
April | 4389.6997 | 7.7025 | 29.2793 | 0 | 0.0001 | 3623.6881 | 1891.8133
May | 4899.6724 | 8.6008 | 32.7085 | 0 | 0.0001 | 4048.0965 | 2111.9467
June | 5090.197 | 8.9384 | 34.0055 | 0 | 0.0002 | 4208.6197 | 2194.39
July | 5031.7818 | 8.8348 | 33.6068 | 0 | 0.0002 | 4159.2678 | 2169.0988
August | 5450.0296 | 9.5718 | 36.4209 | 0 | 0.0002 | 4507.5533 | 2349.6603
September | 4808.1829 | 8.4412 | 32.1052 | 0 | 0.0001 | 3973.4307 | 2072.606
October | 4733.7486 | 8.3081 | 31.5893 | 0 | 0.0001 | 3909.5772 | 2040.2798
November | 4340.7573 | 7.6158 | 28.9464 | 0 | 0.0001 | 3582.4803 | 1870.638
December | 3981.9337 | 6.9814 | 26.516 | 0 | 0.0001 | 3281.6814 | 1715.5251
Annual Sum or Average | 54958.455 | 96.4347 | 366.5807 | 0 | 0.0017 | 45369.0065 | 23685.3447
Minimum of Months | 3761.1783 | 6.5956 | 25.0556 | 0 | 0.0001 | 3100.9412 | 1620.5404
Maximum of Months | 5450.0296 | 9.5718 | 36.4209 | 0 | 0.0002 | 4507.5533 | 2349.6603
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 22397800000 | 19867.156 | 23-JAN-15:00 | 4950.048 | 3712.536 | 3903.152 | 0 | 7301.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 21072600000 | 20509.96 | 22-FEB-15:00 | 4950.048 | 3712.536 | 3903.152 | 0 | 7944.224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 24992200000 | 20432.603 | 13-MAR-15:50 | 4950.048 | 3712.536 | 3903.152 | 0 | 7866.867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 24625000000 | 21580.236 | 03-APR-14:30 | 4950.048 | 3712.536 | 3903.152 | 0 | 9014.499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 27509100000 | 22143.844 | 19-MAY-14:00 | 4950.048 | 3712.536 | 3903.152 | 0 | 9578.108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 28599900000 | 23559.484 | 28-JUN-14:00 | 4950.048 | 3712.536 | 3903.152 | 0 | 10993.747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 28264500000 | 23115.654 | 13-JUL-14:00 | 4950.048 | 3712.536 | 3903.152 | 0 | 10549.917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 30631300000 | 23361.205 | 21-AUG-14:00 | 4950.048 | 3712.536 | 3903.152 | 0 | 10795.468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 27001700000 | 22765.171 | 11-SEP-14:00 | 4950.048 | 3712.536 | 3903.152 | 0 | 10199.434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 26567700000 | 22020.487 | 06-OCT-15:00 | 4950.048 | 3712.536 | 3903.152 | 0 | 9454.751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 24344900000 | 20699.313 | 07-NOV-15:09 | 4950.048 | 3712.536 | 3903.152 | 0 | 8133.576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 22300800000 | 19647.316 | 15-DEC-15:39 | 4950.048 | 3712.536 | 3903.152 | 0 | 7081.579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 308308000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 21072600000 | 19647.316 |  | 4950.048 | 3712.536 | 3903.152 | 0 | 7081.579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 30631300000 | 23559.484 |  | 4950.048 | 3712.536 | 3903.152 | 0 | 10993.747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 8757.2 | 126.12 | 0 | 8883.31
Cost per Total Building Area ($/m2) | 8.12 | 0.12 | 0 | 8.23
Cost per Net Conditioned Building Area ($/m2) | 17.13 | 0.25 | 0 | 17.38
2-houston
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 320.68 | 297.16 | 627.36
Net Site Energy | 320.68 | 297.16 | 627.36
Total Source Energy | 37.53 | 34.78 | 73.42
Net Source Energy | 37.53 | 34.78 | 73.42
Area (m2)
Total Building Area | 1079.13
Net Conditioned Building Area | 511.16
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 23.28 | 0 | 0 | 0 | 0
Cooling | 63.95 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.82 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 76.06 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.09 | 0 | 0 | 0 | 17.65
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 286.31 | 34.37 | 0 | 0 | 0 | 17.65
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 286.31 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 286.31 | 100
Total On-Site and Utility Electric Sources | 286.31 | 100
Total Electricity End Uses | 286.31 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 90 | 180
ATTIC_SOFFIT_WEST | EXPOSED-FLOOR | 0.3 | 0.778 | 0.96 | 11.44 | 270 | 180
ATTIC_SOFFIT_SOUTH | EXPOSED-FLOOR | 0.3 | 0.778 | 0.96 | 16.97 | 225 | 180
ATTIC_SOFFIT_EAST | EXPOSED-FLOOR | 0.3 | 0.778 | 0.96 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | EXPOSED-FLOOR | 0.3 | 0.778 | 0.96 | 16.97 | 315 | 180
ATTIC_ROOF_NORTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 0 | 18.45
ATTIC_ROOF_WEST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 270 | 18.45
ATTIC_ROOF_EAST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 90 | 18.45
ATTIC_ROOF_SOUTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 180 | 18.45
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW_SOUTH | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW_SOUTH | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW_SOUTH | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW_SOUTH | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW_SOUTH | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW_SOUTH | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW_SOUTH | 3.91 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW_EAST | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW_EAST | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW_EAST | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW_EAST | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW_NORTH | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW_NORTH | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW_NORTH | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW_NORTH | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW_NORTH | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW_NORTH | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW_WEST | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW_WEST | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW_WEST | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW_WEST | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7570.38 | 3.05
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11560.39 | 3.05
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6931.48 | 3.05
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11063.92 | 3.05
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7131.37 | 3.05
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.4 | 757.41 | 1 | Fan Energy
PSZ-AC:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.58 | 1107.14 | 1 | Fan Energy
PSZ-AC:3 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.37 | 704.97 | 1 | Fan Energy
PSZ-AC:4 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.58 | 1091.58 | 1 | Fan Energy
PSZ-AC:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.41 | 775.42 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
Nominal Capacity [W]
PSZ-AC:1_HEATC | 5033.73
PSZ-AC:2_HEATC | 5769
PSZ-AC:3_HEATC | 3599.72
PSZ-AC:4_HEATC | 5711.63
PSZ-AC:5_HEATC | 3858.54
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 5134.5212 | 6.5621 | 26.6462 | 0 | 0.0001 | 9088.6065 | 2022.1402
February | 4607.6205 | 5.8806 | 23.7982 | 0 | 0.0001 | 8117.1633 | 1813.5844
March | 5120.6266 | 6.6858 | 28.5545 | 0 | 0.0001 | 9740.161 | 2034.8944
April | 5076.3818 | 6.652 | 28.6432 | 0 | 0.0001 | 9770.5255 | 2020.399
May | 6114.3773 | 8.017 | 34.5685 | 0 | 0.0001 | 11791.7527 | 2434.1516
June | 6764.9129 | 8.873 | 38.289 | 0 | 0.0001 | 13060.8698 | 2693.5237
July | 6808.7124 | 8.9305 | 38.537 | 0 | 0.0001 | 13145.456 | 2710.9636
August | 7156.3609 | 9.3871 | 40.513 | 0 | 0.0001 | 13819.501 | 2849.4604
September | 6150.4662 | 8.0655 | 34.7889 | 0 | 0.0001 | 11866.9382 | 2448.6693
October | 5581.7141 | 7.3158 | 31.5178 | 0 | 0.0001 | 10751.0839 | 2221.7353
November | 4919.5148 | 6.4328 | 27.5677 | 0 | 0.0001 | 9403.6007 | 1956.2137
December | 4923.0533 | 6.3205 | 25.9495 | 0 | 0.0001 | 8851.1207 | 1942.5458
Annual Sum or Average | 68358.262 | 89.1228 | 379.3736 | 0 | 0.0011 | 129406.7793 | 27148.2815
Minimum of Months | 4607.6205 | 5.8806 | 23.7982 | 0 | 0.0001 | 8117.1633 | 1813.5844
Maximum of Months | 7156.3609 | 9.3871 | 40.513 | 0 | 0.0001 | 13819.501 | 2849.4604
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 20108600000 | 17795.332 | 20-JAN-16:49 | 4950.048 | 3712.536 | 4436.517 | 0 | 4696.231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 17959200000 | 18305.372 | 23-FEB-15:30 | 4950.048 | 3712.536 | 4436.517 | 0 | 5206.271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 21550100000 | 18988.989 | 28-MAR-14:00 | 4950.048 | 3712.536 | 4436.517 | 0 | 5889.888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 21617300000 | 20047.6 | 21-APR-15:30 | 4950.048 | 3712.536 | 4436.517 | 0 | 6948.498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 26089300000 | 23246.245 | 18-MAY-15:30 | 4950.048 | 3712.536 | 4436.517 | 0 | 10147.144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 28897200000 | 23368.764 | 13-JUN-14:00 | 4950.048 | 3712.536 | 4436.517 | 0 | 10269.663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 29084300000 | 24887.743 | 31-JUL-13:00 | 4950.048 | 3712.536 | 4436.517 | 0 | 11788.642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 30575700000 | 24509.19 | 31-AUG-15:00 | 4950.048 | 3712.536 | 4436.517 | 0 | 11410.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 26255600000 | 22787.381 | 15-SEP-14:00 | 4950.048 | 3712.536 | 4436.517 | 0 | 9688.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 23786800000 | 21336.821 | 06-OCT-15:00 | 4950.048 | 3712.536 | 4436.517 | 0 | 8237.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 20805500000 | 19169.087 | 03-NOV-14:39 | 4950.048 | 3712.536 | 4436.517 | 0 | 6069.986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 19583100000 | 17721.262 | 20-DEC-11:00 | 4950.048 | 3712.536 | 4436.517 | 0 | 4622.161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 286313000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 17959200000 | 17721.262 |  | 4950.048 | 3712.536 | 4436.517 | 0 | 4622.161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 30575700000 | 24887.743 |  | 4950.048 | 3712.536 | 4436.517 | 0 | 11788.642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 9752.72 | 278.44 | 0 | 10031.16
Cost per Total Building Area ($/m2) | 9.04 | 0.26 | 0 | 9.3
Cost per Net Conditioned Building Area ($/m2) | 19.08 | 0.54 | 0 | 19.62
3-phoenix
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 332.68 | 308.29 | 650.85
Net Site Energy | 332.68 | 308.29 | 650.85
Total Source Energy | 1005.99 | 932.22 | 1968.05
Net Source Energy | 1005.99 | 932.22 | 1968.05
Area (m2)
Total Building Area | 1079.13
Net Conditioned Building Area | 511.16
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 11.49 | 0 | 0 | 0 | 0
Cooling | 77.02 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.81 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 87.01 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 10.86 | 0 | 0 | 0 | 17.65
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 310.33 | 22.35 | 0 | 0 | 0 | 17.65
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 310.33 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 310.33 | 100
Total On-Site and Utility Electric Sources | 310.33 | 100
Total Electricity End Uses | 310.33 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 90 | 180
ATTIC_SOFFIT_WEST | EXPOSED-FLOOR | 0.3 | 0.778 | 0.96 | 11.44 | 270 | 180
ATTIC_SOFFIT_SOUTH | EXPOSED-FLOOR | 0.3 | 0.778 | 0.96 | 16.97 | 225 | 180
ATTIC_SOFFIT_EAST | EXPOSED-FLOOR | 0.3 | 0.778 | 0.96 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | EXPOSED-FLOOR | 0.3 | 0.778 | 0.96 | 16.97 | 315 | 180
ATTIC_ROOF_NORTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 0 | 18.45
ATTIC_ROOF_WEST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 270 | 18.45
ATTIC_ROOF_EAST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 90 | 18.45
ATTIC_ROOF_SOUTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 180 | 18.45
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW_SOUTH | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW_SOUTH | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW_SOUTH | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW_SOUTH | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW_SOUTH | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW_SOUTH | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW_SOUTH | 3.91 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW_EAST | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW_EAST | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW_EAST | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW_EAST | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW_NORTH | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW_NORTH | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW_NORTH | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW_NORTH | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW_NORTH | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW_NORTH | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW_WEST | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW_WEST | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW_WEST | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW_WEST | 2.79 | 6.88 | 0.25 | 0.25 | No | PERIMETER_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7548.45 | 3.05
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11010.23 | 3.05
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7732.3 | 3.05
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9472.17 | 3.05
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8547.76 | 3.05
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.46 | 864.69 | 1 | Fan Energy
PSZ-AC:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.66 | 1253.43 | 1 | Fan Energy
PSZ-AC:3 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.47 | 885.76 | 1 | Fan Energy
PSZ-AC:4 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.57 | 1085.06 | 1 | Fan Energy
PSZ-AC:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.52 | 979.17 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
Nominal Capacity [W]
PSZ-AC:1_HEATC | 4736.89
PSZ-AC:2_HEATC | 5702.41
PSZ-AC:3_HEATC | 3886.42
PSZ-AC:4_HEATC | 5119.67
PSZ-AC:5_HEATC | 4217
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 4236.9006 | 6.9802 | 22.6906 | 0 | 0.0001 | 167605.2563 | 1783.3432
February | 3791.9291 | 6.2876 | 20.6003 | 0 | 0.0001 | 152167.1767 | 1600.1432
March | 4754.492 | 7.9688 | 26.4457 | 0 | 0.0001 | 195349.7521 | 2014.9449
April | 4650.4264 | 7.8232 | 26.0755 | 0 | 0.0001 | 192616.5737 | 1973.7586
May | 5455.6878 | 9.1841 | 30.6358 | 0 | 0.0001 | 226302.9303 | 2316.1618
June | 6548.5295 | 11.0332 | 36.8404 | 0 | 0.0001 | 272136.6266 | 2781.0675
July | 6652.6619 | 11.209 | 37.4287 | 0 | 0.0001 | 276481.8848 | 2825.3248
August | 6873.875 | 11.5823 | 38.6776 | 0 | 0.0001 | 285707.5909 | 2919.3328
September | 5859.656 | 9.8687 | 32.9374 | 0 | 0.0001 | 243305.1161 | 2488.1269
October | 4927.2618 | 8.2906 | 27.6397 | 0 | 0.0001 | 204171.4223 | 2091.422
November | 4279.2841 | 7.1855 | 23.8976 | 0 | 0.0001 | 176528.1131 | 1814.8826
December | 4331.0883 | 7.0774 | 22.7757 | 0 | 0.0001 | 168231.1425 | 1817.1265
Annual Sum or Average | 62361.7924 | 104.4904 | 346.6449 | 0 | 0.0009 | 2560603.5853 | 26425.6348
Minimum of Months | 3791.9291 | 6.2876 | 20.6003 | 0 | 0.0001 | 152167.1767 | 1600.1432
Maximum of Months | 6873.875 | 11.5823 | 38.6776 | 0 | 0.0001 | 285707.5909 | 2919.3328
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 20312800000 | 16943.837 | 27-JAN-16:00 | 4950.048 | 3712.536 | 5068.113 | 0 | 3213.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 18441800000 | 18010.815 | 28-FEB-16:00 | 4950.048 | 3712.536 | 5068.113 | 0 | 4280.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 23675300000 | 20700.932 | 17-MAR-15:00 | 4950.048 | 3712.536 | 5068.113 | 0 | 6970.235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 23344000000 | 21002.431 | 26-APR-15:00 | 4950.048 | 3712.536 | 5068.113 | 0 | 7271.734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 27426600000 | 25179.858 | 30-MAY-15:00 | 4950.048 | 3712.536 | 5068.113 | 0 | 11449.161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 32981400000 | 30096.228 | 28-JUN-15:00 | 4950.048 | 3712.536 | 5068.113 | 0 | 16365.531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 33508000000 | 29571.04 | 11-JUL-15:00 | 4950.048 | 3712.536 | 5068.113 | 0 | 15840.343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 34626100000 | 29175.108 | 01-AUG-15:00 | 4950.048 | 3712.536 | 5068.113 | 0 | 15444.411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 29487200000 | 26746.823 | 11-SEP-15:00 | 4950.048 | 3712.536 | 5068.113 | 0 | 13016.126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 24744400000 | 21822.27 | 02-OCT-15:00 | 4950.048 | 3712.536 | 5068.113 | 0 | 8091.573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 21394200000 | 19374.64 | 13-NOV-16:49 | 4950.048 | 3712.536 | 5068.113 | 0 | 5643.943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 20388600000 | 16298.043 | 13-DEC-16:00 | 4950.048 | 3712.536 | 5068.113 | 0 | 2567.346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 310330000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 18441800000 | 16298.043 |  | 4950.048 | 3712.536 | 5068.113 | 0 | 2567.346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 34626100000 | 30096.228 |  | 4950.048 | 3712.536 | 5068.113 | 0 | 16365.531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 10547.91 | 187.19 | 0 | 10735.1
Cost per Total Building Area ($/m2) | 9.77 | 0.17 | 0 | 9.95
Cost per Net Conditioned Building Area ($/m2) | 20.64 | 0.37 | 0 | 21
4-atlanta
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 293.18 | 271.68 | 573.55
Net Site Energy | 293.18 | 271.68 | 573.55
Total Source Energy | 884.55 | 819.68 | 1730.48
Net Source Energy | 884.55 | 819.68 | 1730.48
Area (m2)
Total Building Area | 1079.13
Net Conditioned Building Area | 511.16
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 33.28 | 0 | 0 | 0 | 0
Cooling | 32.9 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.81 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 69.22 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.48 | 0 | 0 | 0 | 17.65
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 248.42 | 44.76 | 0 | 0 | 0 | 17.65
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 248.42 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 248.42 | 100
Total On-Site and Utility Electric Sources | 248.42 | 100
Total Electricity End Uses | 248.42 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 90 | 180
ATTIC_SOFFIT_WEST | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 11.44 | 270 | 180
ATTIC_SOFFIT_SOUTH | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 16.97 | 225 | 180
ATTIC_SOFFIT_EAST | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 16.97 | 315 | 180
ATTIC_ROOF_NORTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 0 | 18.45
ATTIC_ROOF_WEST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 270 | 18.45
ATTIC_ROOF_EAST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 90 | 18.45
ATTIC_ROOF_SOUTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 180 | 18.45
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW_SOUTH | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW_SOUTH | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW_SOUTH | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW_SOUTH | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW_SOUTH | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW_SOUTH | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW_SOUTH | 3.91 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW_EAST | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW_EAST | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW_EAST | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW_EAST | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW_NORTH | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW_NORTH | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW_NORTH | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW_NORTH | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW_NORTH | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW_NORTH | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW_WEST | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW_WEST | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW_WEST | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW_WEST | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6535.76 | 3.05
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10556.02 | 3.05
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5995.91 | 3.05
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9982.74 | 3.05
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6106.04 | 3.05
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.35 | 659.82 | 1 | Fan Energy
PSZ-AC:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.54 | 1027.52 | 1 | Fan Energy
PSZ-AC:3 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.34 | 641.3 | 1 | Fan Energy
PSZ-AC:4 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.53 | 1007.22 | 1 | Fan Energy
PSZ-AC:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.34 | 643.56 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
Nominal Capacity [W]
PSZ-AC:1_HEATC | 4976.96
PSZ-AC:2_HEATC | 5643.9
PSZ-AC:3_HEATC | 3461.06
PSZ-AC:4_HEATC | 5571.6
PSZ-AC:5_HEATC | 3469.09
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 4406.6693 | 7.8325 | 18.8064 | 0 | 0.0001 | 33446.8625 | 1879.1023
February | 3751.2419 | 6.749 | 16.4089 | 0 | 0.0001 | 29183.8334 | 1607.1434
March | 3928.3567 | 7.4344 | 18.9813 | 0 | 0.0001 | 33762.6343 | 1716.8909
April | 3782.8931 | 7.2169 | 18.5618 | 0 | 0.0001 | 33017.0077 | 1658.6545
May | 4248.1102 | 8.1513 | 21.0739 | 0 | 0.0001 | 37485.8746 | 1866.9561
June | 4706.5033 | 9.0391 | 23.3883 | 0 | 0.0001 | 41602.8179 | 2069.1724
July | 4694.9899 | 9.0167 | 23.3297 | 0 | 0.0001 | 41498.4755 | 2064.0834
August | 5054.1314 | 9.7094 | 25.1291 | 0 | 0.0001 | 44699.3409 | 2222.2546
September | 4391.8811 | 8.4323 | 21.8123 | 0 | 0.0001 | 38799.4001 | 1930.6152
October | 3867.892 | 7.4089 | 19.1253 | 0 | 0.0001 | 34019.5355 | 1698.6812
November | 3685.5551 | 6.9339 | 17.607 | 0 | 0.0001 | 31317.6786 | 1606.9847
December | 4056.0506 | 7.3486 | 17.9929 | 0 | 0.0001 | 32001.4527 | 1742.4542
Annual Sum or Average | 50574.2745 | 95.2729 | 242.2169 | 0 | 0.0009 | 430834.9138 | 22062.9931
Minimum of Months | 3685.5551 | 6.749 | 16.4089 | 0 | 0.0001 | 29183.8334 | 1606.9847
Maximum of Months | 5054.1314 | 9.7094 | 25.1291 | 0 | 0.0001 | 44699.3409 | 2222.2546
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 19285100000 | 13250.165 | 23-JAN-16:40 | 4950.048 | 3712.536 | 3979.412 | 0 | 608.168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 16827100000 | 13552.138 | 22-FEB-15:00 | 4950.048 | 3712.536 | 3979.412 | 0 | 910.141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 19467200000 | 15659.197 | 28-MAR-15:00 | 4950.048 | 3712.536 | 3979.412 | 0 | 3017.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 19037300000 | 17786.163 | 14-APR-15:00 | 4950.048 | 3712.536 | 3979.412 | 0 | 5144.166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 21614000000 | 19453.261 | 15-MAY-14:00 | 4950.048 | 3712.536 | 3979.412 | 0 | 6811.264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 23987800000 | 20549.483 | 19-JUN-14:00 | 4950.048 | 3712.536 | 3979.412 | 0 | 7907.486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 23927600000 | 22437.876 | 03-JUL-14:00 | 4950.048 | 3712.536 | 3979.412 | 0 | 9795.879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 25773200000 | 20742.256 | 17-AUG-15:30 | 4950.048 | 3712.536 | 3979.412 | 0 | 8100.259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 22371400000 | 19640.34 | 11-SEP-13:39 | 4950.048 | 3712.536 | 3979.412 | 0 | 6998.343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 19615300000 | 17865.295 | 02-OCT-13:30 | 4950.048 | 3712.536 | 3979.412 | 0 | 5223.298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 18057500000 | 15338.199 | 22-NOV-14:00 | 4950.048 | 3712.536 | 3979.412 | 0 | 2696.202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 18451700000 | 13114.129 | 05-DEC-14:00 | 4950.048 | 3712.536 | 3979.412 | 0 | 472.132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 248415000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 16827100000 | 13114.129 |  | 4950.048 | 3712.536 | 3979.412 | 0 | 472.132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 25773200000 | 22437.876 |  | 4950.048 | 3712.536 | 3979.412 | 0 | 9795.879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 8073.06 | 437.34 | 0 | 8510.4
Cost per Total Building Area ($/m2) | 7.48 | 0.41 | 0 | 7.89
Cost per Net Conditioned Building Area ($/m2) | 15.79 | 0.86 | 0 | 16.65
5-losangeles
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 220.24 | 204.09 | 430.86
Net Site Energy | 220.24 | 204.09 | 430.86
Total Source Energy | 650.93 | 603.2 | 1273.45
Net Source Energy | 650.93 | 603.2 | 1273.45
Area (m2)
Total Building Area | 1079.13
Net Conditioned Building Area | 511.16
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 3.93 | 0 | 0 | 0 | 0
Cooling | 14.56 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.79 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 44.07 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.4 | 0 | 0 | 0 | 17.65
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 204.91 | 15.33 | 0 | 0 | 0 | 17.65
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 204.91 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 204.91 | 100
Total On-Site and Utility Electric Sources | 204.91 | 100
Total Electricity End Uses | 204.91 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 90 | 180
ATTIC_SOFFIT_WEST | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 11.44 | 270 | 180
ATTIC_SOFFIT_SOUTH | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 16.97 | 225 | 180
ATTIC_SOFFIT_EAST | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 16.97 | 315 | 180
ATTIC_ROOF_NORTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 0 | 18.45
ATTIC_ROOF_WEST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 270 | 18.45
ATTIC_ROOF_EAST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 90 | 18.45
ATTIC_ROOF_SOUTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 180 | 18.45
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW_SOUTH | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW_SOUTH | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW_SOUTH | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW_SOUTH | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW_SOUTH | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW_SOUTH | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW_SOUTH | 3.91 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW_EAST | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW_EAST | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW_EAST | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW_EAST | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW_NORTH | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW_NORTH | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW_NORTH | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW_NORTH | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW_NORTH | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW_NORTH | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW_WEST | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW_WEST | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW_WEST | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW_WEST | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4801.31 | 3.05
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5782.37 | 3.05
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3565.16 | 3.05
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4591.97 | 3.05
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3982.8 | 3.05
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.29 | 550 | 1 | Fan Energy
PSZ-AC:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.35 | 662.39 | 1 | Fan Energy
PSZ-AC:3 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.22 | 408.4 | 1 | Fan Energy
PSZ-AC:4 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.28 | 526.02 | 1 | Fan Energy
PSZ-AC:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.24 | 456.24 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
Nominal Capacity [W]
PSZ-AC:1_HEATC | 3393.2
PSZ-AC:2_HEATC | 3478.39
PSZ-AC:3_HEATC | 2120.53
PSZ-AC:4_HEATC | 2975
PSZ-AC:5_HEATC | 2297.1
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 1559.9083 | 1.3414 | 13.3968 | 0 | 0 | 80830.4095 | 580.76
February | 1378.775 | 1.1845 | 12.0335 | 0 | 0 | 72605.7193 | 513.9102
March | 1574.0579 | 1.351 | 13.9652 | 0 | 0 | 84261.59 | 587.3914
April | 1447.4081 | 1.2416 | 12.9713 | 0 | 0 | 78264.7784 | 540.5252
May | 1544.216 | 1.3242 | 13.9139 | 0 | 0 | 83952.8387 | 576.9066
June | 1554.6212 | 1.3329 | 14.0445 | 0 | 0 | 84740.8296 | 580.9062
July | 1588.0496 | 1.3616 | 14.3509 | 0 | 0 | 86589.5714 | 593.4107
August | 1762.5086 | 1.5109 | 15.9695 | 0 | 0 | 96355.8265 | 658.7295
September | 1581.1588 | 1.3556 | 14.2974 | 0 | 0 | 86266.8922 | 590.8626
October | 1560.3564 | 1.338 | 14.0802 | 0 | 0 | 84956.1228 | 583.0001
November | 1490.949 | 1.279 | 13.3462 | 0 | 0 | 80526.9503 | 556.7387
December | 1516.0962 | 1.3023 | 13.2621 | 0 | 0 | 80018.6571 | 565.1857
Annual Sum or Average | 18558.1049 | 15.9232 | 165.6316 | 0 | 0.0001 | 999370.1859 | 6928.3267
Minimum of Months | 1378.775 | 1.1845 | 12.0335 | 0 | 0 | 72605.7193 | 513.9102
Maximum of Months | 1762.5086 | 1.5109 | 15.9695 | 0 | 0 | 96355.8265 | 658.7295
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 16573300000 | 13930.705 | 26-JAN-13:00 | 4950.048 | 3712.536 | 2603.048 | 0 | 2665.073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 14886900000 | 13339.244 | 13-FEB-11:00 | 4950.048 | 3712.536 | 2603.048 | 0 | 2073.611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 17276800000 | 14098.537 | 31-MAR-14:39 | 4950.048 | 3712.536 | 2603.048 | 0 | 2832.904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 16047200000 | 14582.05 | 11-APR-15:00 | 4950.048 | 3712.536 | 2603.048 | 0 | 3316.417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 17213500000 | 15005.305 | 30-MAY-13:00 | 4950.048 | 3712.536 | 2603.048 | 0 | 3739.673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 17375100000 | 15029.26 | 30-JUN-14:00 | 4950.048 | 3712.536 | 2603.048 | 0 | 3763.628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 17754100000 | 15285.657 | 12-JUL-13:39 | 4950.048 | 3712.536 | 2603.048 | 0 | 4020.025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 19756600000 | 16089.079 | 09-AUG-13:09 | 4950.048 | 3712.536 | 2603.048 | 0 | 4823.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 17688000000 | 15865.068 | 25-SEP-15:20 | 4950.048 | 3712.536 | 2603.048 | 0 | 4599.435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 17419200000 | 14891.731 | 05-OCT-14:20 | 4950.048 | 3712.536 | 2603.048 | 0 | 3626.098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 16511100000 | 14830.283 | 09-NOV-16:00 | 4950.048 | 3712.536 | 2603.048 | 0 | 2050.562 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 16406800000 | 14146.986 | 19-DEC-16:49 | 4950.048 | 3712.536 | 2603.048 | 0 | 1367.264 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 204908000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 14886900000 | 13339.244 |  | 4950.048 | 3712.536 | 2603.048 | 0 | 1367.264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 19756600000 | 16089.079 |  | 4950.048 | 3712.536 | 2603.048 | 0 | 4823.446 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 7300 | 130.77 | 0 | 7430.77
Cost per Total Building Area ($/m2) | 6.76 | 0.12 | 0 | 6.89
Cost per Net Conditioned Building Area ($/m2) | 14.28 | 0.26 | 0 | 14.54
6-lasvegas
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 283.12 | 262.36 | 553.89
Net Site Energy | 283.12 | 262.36 | 553.89
Total Source Energy | 951.62 | 881.84 | 1861.7
Net Source Energy | 951.62 | 881.84 | 1861.7
Area (m2)
Total Building Area | 1079.13
Net Conditioned Building Area | 511.16
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 13.45 | 0 | 0 | 0 | 0
Cooling | 45.19 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.78 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 67.07 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.14 | 0 | 0 | 0 | 17.65
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 258.53 | 24.59 | 0 | 0 | 0 | 17.65
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 258.53 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 258.53 | 100
Total On-Site and Utility Electric Sources | 258.53 | 100
Total Electricity End Uses | 258.53 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 90 | 180
ATTIC_SOFFIT_WEST | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 11.44 | 270 | 180
ATTIC_SOFFIT_SOUTH | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 16.97 | 225 | 180
ATTIC_SOFFIT_EAST | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 16.97 | 315 | 180
ATTIC_ROOF_NORTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 0 | 18.45
ATTIC_ROOF_WEST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 270 | 18.45
ATTIC_ROOF_EAST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 90 | 18.45
ATTIC_ROOF_SOUTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 180 | 18.45
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW_SOUTH | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW_SOUTH | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW_SOUTH | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW_SOUTH | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW_SOUTH | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW_SOUTH | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW_SOUTH | 3.91 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW_EAST | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW_EAST | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW_EAST | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW_EAST | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW_NORTH | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW_NORTH | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW_NORTH | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW_NORTH | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW_NORTH | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW_NORTH | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW_WEST | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW_WEST | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW_WEST | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW_WEST | 2.79 | 3.24 | 0.25 | 0.318 | No | PERIMETER_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6864.13 | 3.05
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8419.19 | 3.05
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5552.28 | 3.05
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7529.09 | 3.05
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6018.48 | 3.05
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.41 | 786.3 | 1 | Fan Energy
PSZ-AC:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.51 | 964.44 | 1 | Fan Energy
PSZ-AC:3 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.34 | 636.03 | 1 | Fan Energy
PSZ-AC:4 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.45 | 862.48 | 1 | Fan Energy
PSZ-AC:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.36 | 689.43 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
Nominal Capacity [W]
PSZ-AC:1_HEATC | 4702.56
PSZ-AC:2_HEATC | 4824.95
PSZ-AC:3_HEATC | 3081.25
PSZ-AC:4_HEATC | 4475.73
PSZ-AC:5_HEATC | 3264.04
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 4467.3892 | 7.0654 | 28.3113 | 0 | 0.0001 | 141187.0743 | 1859.0543
February | 3831.0165 | 6.1954 | 25.561 | 0 | 0 | 127476.5599 | 1608.4177
March | 4460.1545 | 7.2269 | 29.8906 | 0 | 0.0001 | 149069.321 | 1874.0141
April | 4415.3149 | 7.2047 | 30.0641 | 0 | 0.0001 | 149936.4491 | 1860.4156
May | 5025.2417 | 8.2052 | 34.2666 | 0 | 0.0001 | 170895.6319 | 2117.9589
June | 5842.8863 | 9.5484 | 39.9191 | 0 | 0.0001 | 199086.5002 | 2463.4194
July | 5962.8705 | 9.7451 | 40.7448 | 0 | 0.0001 | 203204.39 | 2514.0716
August | 6309.1364 | 10.3124 | 43.124 | 0 | 0.0001 | 215070.0474 | 2660.2097
September | 5267.2739 | 8.6046 | 35.9572 | 0 | 0.0001 | 179327.1182 | 2220.4112
October | 4644.081 | 7.5791 | 31.633 | 0 | 0.0001 | 157761.2104 | 1956.932
November | 4137.5922 | 6.7141 | 27.8218 | 0 | 0.0001 | 138752.3319 | 1739.5114
December | 4286.4492 | 6.8415 | 27.7497 | 0 | 0.0001 | 138388.6299 | 1790.2276
Annual Sum or Average | 58649.4063 | 95.2429 | 395.0431 | 0 | 0.0007 | 1970155.2641 | 24664.6437
Minimum of Months | 3831.0165 | 6.1954 | 25.561 | 0 | 0 | 127476.5599 | 1608.4177
Maximum of Months | 6309.1364 | 10.3124 | 43.124 | 0 | 0.0001 | 215070.0474 | 2660.2097
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 18527100000 | 14382.873 | 30-JAN-16:00 | 4950.048 | 3712.536 | 3938.682 | 0 | 267.518 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 16728000000 | 14112.574 | 08-FEB-15:00 | 4950.048 | 3712.536 | 3938.682 | 0 | 1511.308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 19561500000 | 16003.423 | 31-MAR-15:30 | 4950.048 | 3712.536 | 3938.682 | 0 | 3402.157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 19675300000 | 18307.218 | 21-APR-15:20 | 4950.048 | 3712.536 | 3938.682 | 0 | 5705.952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 22425600000 | 20030.781 | 31-MAY-15:00 | 4950.048 | 3712.536 | 3938.682 | 0 | 7429.515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 26124900000 | 24235.873 | 27-JUN-15:00 | 4950.048 | 3712.536 | 3938.682 | 0 | 11634.607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 26665300000 | 23744.464 | 24-JUL-15:00 | 4950.048 | 3712.536 | 3938.682 | 0 | 11143.198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 28222400000 | 22956.829 | 04-AUG-14:00 | 4950.048 | 3712.536 | 3938.682 | 0 | 10355.563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 23532000000 | 22242.914 | 01-SEP-14:00 | 4950.048 | 3712.536 | 3938.682 | 0 | 9641.648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 20702100000 | 18613.555 | 06-OCT-13:50 | 4950.048 | 3712.536 | 3938.682 | 0 | 6012.289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 18207600000 | 16408.176 | 10-NOV-16:40 | 4950.048 | 3712.536 | 3938.682 | 0 | 2292.821 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 18159900000 | 14911.519 | 06-DEC-16:30 | 4950.048 | 3712.536 | 3938.682 | 0 | 796.164 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 258532000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 16728000000 | 14112.574 |  | 4950.048 | 3712.536 | 3938.682 | 0 | 267.518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 28222400000 | 24235.873 |  | 4950.048 | 3712.536 | 3938.682 | 0 | 11634.607 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 7288.79 | 193.12 | 0 | 7481.91
Cost per Total Building Area ($/m2) | 6.75 | 0.18 | 0 | 6.93
Cost per Net Conditioned Building Area ($/m2) | 14.26 | 0.38 | 0 | 14.64
7-sanfrancisco
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 238.01 | 220.56 | 465.63
Net Site Energy | 238.01 | 220.56 | 465.63
Total Source Energy | 664.35 | 615.63 | 1299.7
Net Source Energy | 664.35 | 615.63 | 1299.7
Area (m2)
Total Building Area | 1079.13
Net Conditioned Building Area | 511.16
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 24.36 | 0 | 0 | 0 | 0
Cooling | 5.82 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.8 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 49.82 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.73 | 0 | 0 | 0 | 17.65
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 201.92 | 36.09 | 0 | 0 | 0 | 17.65
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 201.92 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 201.92 | 100
Total On-Site and Utility Electric Sources | 201.92 | 100
Total Electricity End Uses | 201.92 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 90 | 180
ATTIC_SOFFIT_WEST | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 11.44 | 270 | 180
ATTIC_SOFFIT_SOUTH | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 16.97 | 225 | 180
ATTIC_SOFFIT_EAST | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 16.97 | 315 | 180
ATTIC_ROOF_NORTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 0 | 18.45
ATTIC_ROOF_WEST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 270 | 18.45
ATTIC_ROOF_EAST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 90 | 18.45
ATTIC_ROOF_SOUTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 180 | 18.45
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW_SOUTH | 2.79 | 6.88 | 0.39 | 0.39 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW_SOUTH | 2.79 | 6.88 | 0.39 | 0.39 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW_SOUTH | 2.79 | 6.88 | 0.39 | 0.39 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW_SOUTH | 2.79 | 6.88 | 0.39 | 0.39 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW_SOUTH | 2.79 | 6.88 | 0.39 | 0.39 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW_SOUTH | 2.79 | 6.88 | 0.39 | 0.39 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW_SOUTH | 3.91 | 6.88 | 0.39 | 0.39 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW_EAST | 2.79 | 6.88 | 0.39 | 0.39 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW_EAST | 2.79 | 6.88 | 0.39 | 0.39 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW_EAST | 2.79 | 6.88 | 0.39 | 0.39 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW_EAST | 2.79 | 6.88 | 0.39 | 0.39 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW_NORTH | 2.79 | 6.88 | 0.39 | 0.39 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW_NORTH | 2.79 | 6.88 | 0.39 | 0.39 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW_NORTH | 2.79 | 6.88 | 0.39 | 0.39 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW_NORTH | 2.79 | 6.88 | 0.39 | 0.39 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW_NORTH | 2.79 | 6.88 | 0.39 | 0.39 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW_NORTH | 2.79 | 6.88 | 0.39 | 0.39 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW_WEST | 2.79 | 6.88 | 0.39 | 0.39 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW_WEST | 2.79 | 6.88 | 0.39 | 0.39 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW_WEST | 2.79 | 6.88 | 0.39 | 0.39 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW_WEST | 2.79 | 6.88 | 0.39 | 0.39 | No | PERIMETER_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4130.26 | 3.05
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7337.74 | 3.05
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3700.74 | 3.05
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5764.79 | 3.05
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4220.04 | 3.05
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.25 | 473.13 | 1 | Fan Energy
PSZ-AC:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.44 | 840.56 | 1 | Fan Energy
PSZ-AC:3 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.22 | 423.93 | 1 | Fan Energy
PSZ-AC:4 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.35 | 660.37 | 1 | Fan Energy
PSZ-AC:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.25 | 483.42 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
Nominal Capacity [W]
PSZ-AC:1_HEATC | 3331.51
PSZ-AC:2_HEATC | 4400.25
PSZ-AC:3_HEATC | 2333.77
PSZ-AC:4_HEATC | 3733.21
PSZ-AC:5_HEATC | 2554.03
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 1916.6151 | 1.6634 | 13.7224 | 0 | 0 | 82784.9401 | 705.2102
February | 1502.3579 | 1.2952 | 12.3143 | 0 | 0 | 74297.0206 | 557.5391
March | 1738.6919 | 1.4997 | 14.1076 | 0 | 0 | 85115.8968 | 644.8058
April | 1522.497 | 1.31 | 12.9254 | 0 | 0 | 77985.4004 | 566.3736
May | 1557.1473 | 1.3369 | 13.74 | 0 | 0 | 82902.5617 | 580.8516
June | 1533.2097 | 1.3154 | 13.7008 | 0 | 0 | 82666.466 | 572.447
July | 1499.6755 | 1.2862 | 13.4821 | 0 | 0 | 81346.9081 | 560.1734
August | 1628.7372 | 1.3967 | 14.6696 | 0 | 0 | 88512.1213 | 608.4649
September | 1542.3098 | 1.3227 | 13.8803 | 0 | 0 | 83749.8627 | 576.1442
October | 1562.9691 | 1.3413 | 13.9 | 0 | 0 | 83868.2546 | 583.3546
November | 1568.2315 | 1.3494 | 13.3117 | 0 | 0 | 80316.4363 | 583.3811
December | 1808.3025 | 1.5665 | 13.4667 | 0 | 0 | 81244.8325 | 666.943
Annual Sum or Average | 19380.7444 | 16.6835 | 163.2209 | 0 | 0.0001 | 984790.7011 | 7205.6886
Minimum of Months | 1499.6755 | 1.2862 | 12.3143 | 0 | 0 | 74297.0206 | 557.5391
Maximum of Months | 1916.6151 | 1.6634 | 14.6696 | 0 | 0 | 88512.1213 | 705.2102
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 16974000000 | 13058.081 | 02-JAN-16:00 | 4950.048 | 3712.536 | 2881.407 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 15233700000 | 13098.546 | 15-FEB-15:00 | 4950.048 | 3712.536 | 2881.407 | 0 | 1554.555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 17452000000 | 12265.197 | 01-MAR-13:30 | 4950.048 | 3712.536 | 2881.407 | 0 | 721.205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 15989900000 | 14014.672 | 13-APR-14:00 | 4950.048 | 3712.536 | 2881.407 | 0 | 2470.681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 16998100000 | 14497.096 | 17-MAY-13:00 | 4950.048 | 3712.536 | 2881.407 | 0 | 2953.105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 16949700000 | 15072.685 | 16-JUN-14:00 | 4950.048 | 3712.536 | 2881.407 | 0 | 3528.693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 16679200000 | 16530.639 | 03-JUL-12:00 | 4950.048 | 3712.536 | 2881.407 | 0 | 4986.647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 18148300000 | 15298.316 | 15-AUG-12:09 | 4950.048 | 3712.536 | 2881.407 | 0 | 3754.325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 17171900000 | 17200.477 | 28-SEP-14:00 | 4950.048 | 3712.536 | 2881.407 | 0 | 5656.486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 17196100000 | 14422.109 | 13-OCT-15:30 | 4950.048 | 3712.536 | 2881.407 | 0 | 2878.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 16467900000 | 13287.489 | 14-NOV-16:00 | 4950.048 | 3712.536 | 2881.407 | 0 | 229.409 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 16658200000 | 13058.081 | 01-DEC-16:49 | 4950.048 | 3712.536 | 2881.407 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 201919000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 15233700000 | 12265.197 |  | 4950.048 | 3712.536 | 2881.407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 18148300000 | 17200.477 |  | 4950.048 | 3712.536 | 2881.407 | 0 | 5656.486 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 9099.53 | 312.3 | 0 | 9411.82
Cost per Total Building Area ($/m2) | 8.43 | 0.29 | 0 | 8.72
Cost per Net Conditioned Building Area ($/m2) | 17.8 | 0.61 | 0 | 18.41
8-baltimore
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 328.83 | 304.71 | 643.3
Net Site Energy | 328.83 | 304.71 | 643.3
Total Source Energy | 983.57 | 911.44 | 1924.2
Net Source Energy | 983.57 | 911.44 | 1924.2
Area (m2)
Total Building Area | 1079.13
Net Conditioned Building Area | 511.16
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 65.64 | 0 | 0 | 0 | 0
Cooling | 28.96 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.78 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 76.17 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.78 | 0 | 0 | 0 | 17.65
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 251.41 | 77.42 | 0 | 0 | 0 | 17.65
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 251.41 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 251.41 | 100
Total On-Site and Utility Electric Sources | 251.41 | 100
Total Electricity End Uses | 251.41 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 90 | 180
ATTIC_SOFFIT_WEST | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 11.44 | 270 | 180
ATTIC_SOFFIT_SOUTH | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 16.97 | 225 | 180
ATTIC_SOFFIT_EAST | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 16.97 | 315 | 180
ATTIC_ROOF_NORTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 0 | 18.45
ATTIC_ROOF_WEST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 270 | 18.45
ATTIC_ROOF_EAST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 90 | 18.45
ATTIC_ROOF_SOUTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 180 | 18.45
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW_SOUTH | 3.91 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW_EAST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW_EAST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW_EAST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW_EAST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW_WEST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW_WEST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW_WEST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW_WEST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6477.34 | 3.05
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11087.35 | 3.05
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6242.19 | 3.05
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10697.72 | 3.05
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6460.4 | 3.05
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.34 | 652.19 | 1 | Fan Energy
PSZ-AC:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.58 | 1107.97 | 1 | Fan Energy
PSZ-AC:3 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.36 | 687.94 | 1 | Fan Energy
PSZ-AC:4 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.57 | 1083.64 | 1 | Fan Energy
PSZ-AC:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.36 | 690.41 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
Nominal Capacity [W]
PSZ-AC:1_HEATC | 5469.5
PSZ-AC:2_HEATC | 6394.51
PSZ-AC:3_HEATC | 3906.07
PSZ-AC:4_HEATC | 6305
PSZ-AC:5_HEATC | 3915.18
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 4606.9267 | 7.9241 | 20.6835 | 0 | 0.0001 | 1286.0379 | 1936.6634
February | 3851.171 | 6.7953 | 18.2353 | 0 | 0.0001 | 1133.8852 | 1634.6059
March | 3668.3074 | 6.9366 | 19.9309 | 0 | 0.0001 | 1239.4885 | 1599.4074
April | 3175.0126 | 6.2049 | 18.3612 | 0 | 0.0001 | 1141.9395 | 1402.7184
May | 3503.2171 | 6.9392 | 20.7721 | 0 | 0.0001 | 1291.9054 | 1556.2113
June | 4087.6357 | 8.1188 | 24.3585 | 0 | 0.0001 | 1514.9694 | 1817.8307
July | 4178.7491 | 8.3011 | 24.9089 | 0 | 0.0001 | 1549.1971 | 1858.4722
August | 4538.182 | 9.0189 | 27.0725 | 0 | 0.0001 | 1683.7684 | 2018.6783
September | 3617.1137 | 7.179 | 21.5256 | 0 | 0.0001 | 1338.7741 | 1608.1014
October | 3467.0196 | 6.8045 | 20.2098 | 0 | 0.0001 | 1256.9169 | 1534.3747
November | 3404.1624 | 6.5115 | 18.9067 | 0 | 0.0001 | 1175.8203 | 1491.0445
December | 4197.4613 | 7.4258 | 19.9821 | 0 | 0.0001 | 1242.5076 | 1783.3599
Annual Sum or Average | 46294.9586 | 88.1597 | 254.9471 | 0 | 0.001 | 15855.2102 | 20241.4681
Minimum of Months | 3175.0126 | 6.2049 | 18.2353 | 0 | 0.0001 | 1133.8852 | 1402.7184
Maximum of Months | 4606.9267 | 9.0189 | 27.0725 | 0 | 0.0001 | 1683.7684 | 2018.6783
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 20391900000 | 14398.821 | 02-JAN-16:49 | 4950.048 | 3712.536 | 4222.148 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 17979300000 | 13010.275 | 15-FEB-13:20 | 4950.048 | 3712.536 | 4222.148 | 0 | 125.543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 19653800000 | 15228.583 | 10-MAR-10:00 | 4950.048 | 3712.536 | 4222.148 | 0 | 2343.851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 18107100000 | 16683.442 | 05-APR-15:00 | 4950.048 | 3712.536 | 4222.148 | 0 | 3798.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 20485000000 | 18678.003 | 31-MAY-15:00 | 4950.048 | 3712.536 | 4222.148 | 0 | 5793.271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 24022000000 | 22054.252 | 30-JUN-15:20 | 4950.048 | 3712.536 | 4222.148 | 0 | 9169.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 24564700000 | 23032.756 | 25-JUL-13:30 | 4950.048 | 3712.536 | 4222.148 | 0 | 10148.024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 26698500000 | 22826.805 | 09-AUG-14:39 | 4950.048 | 3712.536 | 4222.148 | 0 | 9942.073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 21228100000 | 19890.317 | 08-SEP-15:09 | 4950.048 | 3712.536 | 4222.148 | 0 | 7005.585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 19930200000 | 18252.849 | 03-OCT-14:00 | 4950.048 | 3712.536 | 4222.148 | 0 | 5368.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 18644300000 | 16628.606 | 03-NOV-13:00 | 4950.048 | 3712.536 | 4222.148 | 0 | 3743.874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 19701700000 | 14398.821 | 01-DEC-16:40 | 4950.048 | 3712.536 | 4222.148 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 251407000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 17979300000 | 13010.275 |  | 4950.048 | 3712.536 | 4222.148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 26698500000 | 23032.756 |  | 4950.048 | 3712.536 | 4222.148 | 0 | 10148.024 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 5233.89 | 752.25 | 0 | 5986.14
Cost per Total Building Area ($/m2) | 4.85 | 0.7 | 0 | 5.55
Cost per Net Conditioned Building Area ($/m2) | 10.24 | 1.47 | 0 | 11.71
9-albuquerque
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 299.46 | 277.5 | 585.86
Net Site Energy | 299.46 | 277.5 | 585.86
Total Source Energy | 896.67 | 830.91 | 1754.19
Net Source Energy | 896.67 | 830.91 | 1754.19
Area (m2)
Total Building Area | 1079.13
Net Conditioned Building Area | 511.16
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 31.83 | 0 | 0 | 0 | 0
Cooling | 29.87 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.79 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 79.76 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.72 | 0 | 0 | 0 | 17.65
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 255.91 | 43.56 | 0 | 0 | 0 | 17.65
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 255.91 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 255.91 | 100
Total On-Site and Utility Electric Sources | 255.91 | 100
Total Electricity End Uses | 255.91 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 90 | 180
ATTIC_SOFFIT_WEST | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 11.44 | 270 | 180
ATTIC_SOFFIT_SOUTH | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 16.97 | 225 | 180
ATTIC_SOFFIT_EAST | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 16.97 | 315 | 180
ATTIC_ROOF_NORTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 0 | 18.45
ATTIC_ROOF_WEST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 270 | 18.45
ATTIC_ROOF_EAST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 90 | 18.45
ATTIC_ROOF_SOUTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 180 | 18.45
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW_SOUTH | 3.91 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW_EAST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW_EAST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW_EAST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW_EAST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW_WEST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW_WEST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW_WEST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW_WEST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6189.52 | 3.05
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10377.11 | 3.05
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6499.8 | 3.05
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10159.25 | 3.05
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6499.8 | 3.05
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.37 | 709.03 | 1 | Fan Energy
PSZ-AC:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.63 | 1188.73 | 1 | Fan Energy
PSZ-AC:3 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.39 | 744.57 | 1 | Fan Energy
PSZ-AC:4 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.61 | 1163.77 | 1 | Fan Energy
PSZ-AC:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.39 | 744.57 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
Nominal Capacity [W]
PSZ-AC:1_HEATC | 4535.7
PSZ-AC:2_HEATC | 5411.87
PSZ-AC:3_HEATC | 3330.24
PSZ-AC:4_HEATC | 5335.89
PSZ-AC:5_HEATC | 3330.24
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 5875.0058 | 9.8553 | 24.5032 | 0 | 0.0001 | 25476.7215 | 2476.9595
February | 4983.5742 | 8.4709 | 21.3861 | 0 | 0.0001 | 22236.4877 | 2112.0111
March | 5604.4762 | 9.6445 | 24.6903 | 0 | 0.0001 | 25672.8883 | 2386.7395
April | 5170.5155 | 9.0088 | 23.3796 | 0 | 0.0001 | 24310.7909 | 2212.8257
May | 5994.6761 | 10.4728 | 27.2581 | 0 | 0.0001 | 28343.9174 | 2568.2937
June | 6391.9424 | 11.1732 | 29.0987 | 0 | 0.0001 | 30257.8656 | 2739.114
July | 6543.7236 | 11.4396 | 29.7957 | 0 | 0.0001 | 30982.7159 | 2804.2668
August | 6932.1199 | 12.1204 | 31.5741 | 0 | 0.0001 | 32831.9357 | 2970.8901
September | 5898.4211 | 10.3082 | 26.8394 | 0 | 0.0001 | 27908.536 | 2527.3988
October | 5454.1916 | 9.5025 | 24.6594 | 0 | 0.0001 | 25641.5024 | 2334.177
November | 5316.4938 | 9.1184 | 23.256 | 0 | 0.0001 | 24181.3774 | 2261.0984
December | 5766.4416 | 9.6618 | 23.9888 | 0 | 0.0001 | 24941.8217 | 2430.0716
Annual Sum or Average | 69931.5818 | 120.7764 | 310.4294 | 0 | 0.0012 | 322786.5605 | 29823.8463
Minimum of Months | 4983.5742 | 8.4709 | 21.3861 | 0 | 0.0001 | 22236.4877 | 2112.0111
Maximum of Months | 6932.1199 | 12.1204 | 31.5741 | 0 | 0.0001 | 32831.9357 | 2970.8901
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 20198300000 | 14243.023 | 27-JAN-15:09 | 4950.048 | 3712.536 | 4550.656 | 0 | 1029.782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 17629400000 | 15006.908 | 14-FEB-15:00 | 4950.048 | 3712.536 | 4550.656 | 0 | 1793.667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 20353800000 | 15705.217 | 21-MAR-15:39 | 4950.048 | 3712.536 | 4550.656 | 0 | 2491.976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 19273900000 | 17901.239 | 21-APR-15:30 | 4950.048 | 3712.536 | 4550.656 | 0 | 4687.998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 22471400000 | 19097.386 | 31-MAY-15:00 | 4950.048 | 3712.536 | 4550.656 | 0 | 5884.146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 23988800000 | 20861.149 | 29-JUN-13:00 | 4950.048 | 3712.536 | 4550.656 | 0 | 7647.908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 24563500000 | 21750.037 | 31-JUL-14:00 | 4950.048 | 3712.536 | 4550.656 | 0 | 8536.797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 26029600000 | 21989.991 | 01-AUG-13:00 | 4950.048 | 3712.536 | 4550.656 | 0 | 8776.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 22126200000 | 19100.267 | 29-SEP-14:30 | 4950.048 | 3712.536 | 4550.656 | 0 | 5887.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 20328900000 | 17960.625 | 03-OCT-14:50 | 4950.048 | 3712.536 | 4550.656 | 0 | 4747.384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 19171300000 | 15194.321 | 10-NOV-14:00 | 4950.048 | 3712.536 | 4550.656 | 0 | 1981.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 19774200000 | 14994.37 | 08-DEC-16:49 | 4950.048 | 3712.536 | 4550.656 | 0 | 267.04 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 255909000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 17629400000 | 14243.023 |  | 4950.048 | 3712.536 | 4550.656 | 0 | 267.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 26029600000 | 21989.991 |  | 4950.048 | 3712.536 | 4550.656 | 0 | 8776.75 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 5340.62 | 301.76 | 0 | 5642.38
Cost per Total Building Area ($/m2) | 4.95 | 0.28 | 0 | 5.23
Cost per Net Conditioned Building Area ($/m2) | 10.45 | 0.59 | 0 | 11.04
10-seattle
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 285.56 | 264.62 | 558.66
Net Site Energy | 285.56 | 264.62 | 558.66
Total Source Energy | 452.32 | 419.15 | 884.89
Net Source Energy | 452.32 | 419.15 | 884.89
Area (m2)
Total Building Area | 1079.13
Net Conditioned Building Area | 511.16
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 57.49 | 0 | 0 | 0 | 0
Cooling | 8.22 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.74 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 61.68 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.94 | 0 | 0 | 0 | 17.65
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 216.13 | 69.43 | 0 | 0 | 0 | 17.65
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 216.13 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 216.13 | 100
Total On-Site and Utility Electric Sources | 216.13 | 100
Total Electricity End Uses | 216.13 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 90 | 180
ATTIC_SOFFIT_WEST | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 11.44 | 270 | 180
ATTIC_SOFFIT_SOUTH | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 16.97 | 225 | 180
ATTIC_SOFFIT_EAST | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 16.97 | 315 | 180
ATTIC_ROOF_NORTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 0 | 18.45
ATTIC_ROOF_WEST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 270 | 18.45
ATTIC_ROOF_EAST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 90 | 18.45
ATTIC_ROOF_SOUTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 180 | 18.45
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW_SOUTH | 3.91 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW_EAST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW_EAST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW_EAST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW_EAST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW_WEST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW_WEST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW_WEST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW_WEST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4699.18 | 3.05
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8037.62 | 3.05
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5040.53 | 3.05
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7853.32 | 3.05
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5026.42 | 3.05
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.28 | 538.3 | 1 | Fan Energy
PSZ-AC:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.49 | 920.73 | 1 | Fan Energy
PSZ-AC:3 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.3 | 577.41 | 1 | Fan Energy
PSZ-AC:4 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.47 | 899.62 | 1 | Fan Energy
PSZ-AC:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.3 | 575.79 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
Nominal Capacity [W]
PSZ-AC:1_HEATC | 4380.94
PSZ-AC:2_HEATC | 5182.55
PSZ-AC:3_HEATC | 3187.94
PSZ-AC:4_HEATC | 5115.79
PSZ-AC:5_HEATC | 3182.06
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 1659.6457 | 2.1299 | 3.9875 | 0 | 0 | 52655.9657 | 641.176
February | 1239.1488 | 1.6666 | 3.4646 | 0 | 0 | 45764.6941 | 486.8998
March | 1350.6414 | 1.8494 | 3.9858 | 0 | 0 | 52655.3281 | 534.2235
April | 1036.4251 | 1.5024 | 3.5904 | 0 | 0 | 47444.0128 | 418.8622
May | 942.8964 | 1.4575 | 3.8454 | 0 | 0 | 50824.5902 | 390.7753
June | 933.2671 | 1.4596 | 3.9141 | 0 | 0 | 51734.268 | 388.5955
July | 947.459 | 1.4859 | 4.0003 | 0 | 0 | 52874.016 | 394.9522
August | 1026.3366 | 1.6125 | 4.3517 | 0 | 0 | 57519.5317 | 428.1415
September | 927.1871 | 1.4426 | 3.8411 | 0 | 0 | 50769.1324 | 385.2678
October | 1005.8214 | 1.507 | 3.7968 | 0 | 0 | 50177.6682 | 411.7347
November | 1297.6446 | 1.7648 | 3.7529 | 0 | 0 | 49575.707 | 511.9768
December | 1638.0972 | 2.0954 | 3.8918 | 0 | 0 | 51391.9773 | 632.1156
Annual Sum or Average | 14004.5705 | 19.9738 | 46.4225 | 0 | 0.0002 | 613386.8914 | 5624.7208
Minimum of Months | 927.1871 | 1.4426 | 3.4646 | 0 | 0 | 45764.6941 | 385.2678
Maximum of Months | 1659.6457 | 2.1299 | 4.3517 | 0 | 0 | 57519.5317 | 641.176
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 18553900000 | 13688.521 | 02-JAN-16:30 | 4950.048 | 3712.536 | 3511.848 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 16125700000 | 12371.493 | 24-FEB-14:30 | 4950.048 | 3712.536 | 3511.848 | 0 | 197.061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 18553700000 | 13719.662 | 29-MAR-15:50 | 4950.048 | 3712.536 | 3511.848 | 0 | 1545.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 16717400000 | 13547.048 | 19-APR-15:30 | 4950.048 | 3712.536 | 3511.848 | 0 | 1372.616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 17908600000 | 15794.301 | 05-MAY-13:39 | 4950.048 | 3712.536 | 3511.848 | 0 | 3619.869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 18229100000 | 16842.51 | 28-JUN-14:00 | 4950.048 | 3712.536 | 3511.848 | 0 | 4668.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 18630700000 | 17717.339 | 24-JUL-14:00 | 4950.048 | 3712.536 | 3511.848 | 0 | 5542.907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 20267600000 | 17544.116 | 07-AUG-14:00 | 4950.048 | 3712.536 | 3511.848 | 0 | 5369.684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 17889100000 | 17013.828 | 01-SEP-15:50 | 4950.048 | 3712.536 | 3511.848 | 0 | 4839.396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 17680600000 | 14186.48 | 03-OCT-15:39 | 4950.048 | 3712.536 | 3511.848 | 0 | 2012.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 17468500000 | 13688.521 | 01-NOV-16:49 | 4950.048 | 3712.536 | 3511.848 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 18108500000 | 13688.521 | 01-DEC-16:19 | 4950.048 | 3712.536 | 3511.848 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 216134000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 16125700000 | 12371.493 |  | 4950.048 | 3712.536 | 3511.848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 20267600000 | 17717.339 |  | 4950.048 | 3712.536 | 3511.848 | 0 | 5542.907 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 4394.28 | 586.24 | 0 | 4980.52
Cost per Total Building Area ($/m2) | 4.07 | 0.54 | 0 | 4.62
Cost per Net Conditioned Building Area ($/m2) | 8.6 | 1.15 | 0 | 9.74
11-chicago
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 376.22 | 348.63 | 736.01
Net Site Energy | 376.22 | 348.63 | 736.01
Total Source Energy | 1069.63 | 991.2 | 2092.57
Net Source Energy | 1069.63 | 991.2 | 2092.57
Area (m2)
Total Building Area | 1079.13
Net Conditioned Building Area | 511.16
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 95.71 | 0 | 0 | 0 | 0
Cooling | 25.81 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.79 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 96.38 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 12.04 | 0 | 0 | 0 | 17.65
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 268.46 | 107.76 | 0 | 0 | 0 | 17.65
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 268.46 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 268.46 | 100
Total On-Site and Utility Electric Sources | 268.46 | 100
Total Electricity End Uses | 268.46 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 90 | 180
ATTIC_SOFFIT_WEST | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 11.44 | 270 | 180
ATTIC_SOFFIT_SOUTH | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 16.97 | 225 | 180
ATTIC_SOFFIT_EAST | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 16.97 | 315 | 180
ATTIC_ROOF_NORTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 0 | 18.45
ATTIC_ROOF_WEST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 270 | 18.45
ATTIC_ROOF_EAST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 90 | 18.45
ATTIC_ROOF_SOUTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 180 | 18.45
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW_SOUTH | 3.91 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW_EAST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW_EAST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW_EAST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW_EAST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW_WEST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW_WEST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW_WEST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW_WEST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7895.11 | 3.05
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13315.36 | 3.05
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7534.79 | 3.05
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13801.68 | 3.05
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7814 | 3.05
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.42 | 794.91 | 1 | Fan Energy
PSZ-AC:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.71 | 1348.36 | 1 | Fan Energy
PSZ-AC:3 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.44 | 832.21 | 1 | Fan Energy
PSZ-AC:4 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.69 | 1316.51 | 1 | Fan Energy
PSZ-AC:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.44 | 836.09 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
Nominal Capacity [W]
PSZ-AC:1_HEATC | 6811.71
PSZ-AC:2_HEATC | 7849.81
PSZ-AC:3_HEATC | 4762.12
PSZ-AC:4_HEATC | 7734.39
PSZ-AC:5_HEATC | 4776.06
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 9372.1392 | 15.6505 | 42.8614 | 0 | 0.0001 | 9865.3436 | 3926.6926
February | 7909.1939 | 13.4417 | 37.5747 | 0 | 0.0001 | 8648.875 | 3336.1437
March | 8089.1676 | 14.1128 | 40.619 | 0 | 0.0001 | 9350.1569 | 3446.9751
April | 6732.122 | 12.1015 | 35.9406 | 0 | 0.0001 | 8273.721 | 2902.7722
May | 7560.1144 | 13.7034 | 41.0414 | 0 | 0.0001 | 9448.1174 | 3270.6409
June | 8642.6111 | 15.6908 | 47.07 | 0 | 0.0001 | 10835.9948 | 3741.3742
July | 8758.8752 | 15.9027 | 47.708 | 0 | 0.0001 | 10982.8729 | 3791.7814
August | 9149.2177 | 16.6128 | 49.8426 | 0 | 0.0002 | 11474.2679 | 3960.8978
September | 7653.52 | 13.8896 | 41.65 | 0 | 0.0001 | 9588.245 | 3312.6692
October | 7153.5672 | 12.909 | 38.4898 | 0 | 0.0001 | 8860.6325 | 3089.265
November | 7400.8746 | 13.0277 | 37.8568 | 0 | 0.0001 | 8714.482 | 3164.7465
December | 8925.7879 | 15.0907 | 41.9327 | 0 | 0.0001 | 9651.8862 | 3757.4282
Annual Sum or Average | 97347.1908 | 172.1331 | 502.5871 | 0 | 0.0015 | 115694.5951 | 41701.3868
Minimum of Months | 6732.122 | 12.1015 | 35.9406 | 0 | 0.0001 | 8273.721 | 2902.7722
Maximum of Months | 9372.1392 | 16.6128 | 49.8426 | 0 | 0.0002 | 11474.2679 | 3960.8978
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 22891800000 | 15304.755 | 02-JAN-16:30 | 4950.048 | 3712.536 | 5128.081 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 20069100000 | 15304.755 | 01-FEB-16:00 | 4950.048 | 3712.536 | 5128.081 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 21696300000 | 15179.607 | 31-MAR-15:50 | 4950.048 | 3712.536 | 5128.081 | 0 | 1388.941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 19198500000 | 16614.406 | 28-APR-15:30 | 4950.048 | 3712.536 | 5128.081 | 0 | 2823.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 21923600000 | 19919.185 | 30-MAY-15:00 | 4950.048 | 3712.536 | 5128.081 | 0 | 6128.519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 25144100000 | 22994.347 | 08-JUN-12:00 | 4950.048 | 3712.536 | 5128.081 | 0 | 9203.681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 25484900000 | 23604.05 | 14-JUL-10:00 | 4950.048 | 3712.536 | 5128.081 | 0 | 9813.384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 26625200000 | 23270.794 | 04-AUG-15:30 | 4950.048 | 3712.536 | 5128.081 | 0 | 9480.129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 22248800000 | 20660.348 | 06-SEP-10:00 | 4950.048 | 3712.536 | 5128.081 | 0 | 6869.682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 20560400000 | 19226.954 | 31-OCT-16:49 | 4950.048 | 3712.536 | 5128.081 | 0 | 3922.199 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 20221300000 | 18824.633 | 02-NOV-16:49 | 4950.048 | 3712.536 | 5128.081 | 0 | 3519.878 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 22396500000 | 15304.755 | 01-DEC-16:19 | 4950.048 | 3712.536 | 5128.081 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 268461000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 19198500000 | 15179.607 |  | 4950.048 | 3712.536 | 5128.081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 26625200000 | 23604.05 |  | 4950.048 | 3712.536 | 5128.081 | 0 | 9813.384 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 4635.62 | 894.54 | 0 | 5530.16
Cost per Total Building Area ($/m2) | 4.3 | 0.83 | 0 | 5.12
Cost per Net Conditioned Building Area ($/m2) | 9.07 | 1.75 | 0 | 10.82
12-boulder
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 333.65 | 309.18 | 652.74
Net Site Energy | 333.65 | 309.18 | 652.74
Total Source Energy | 955.07 | 885.03 | 1868.44
Net Source Energy | 955.07 | 885.03 | 1868.44
Area (m2)
Total Building Area | 1079.13
Net Conditioned Building Area | 511.16
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 56.25 | 0 | 0 | 0 | 0
Cooling | 21.61 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.77 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 97.5 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 12.03 | 0 | 0 | 0 | 17.65
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 265.37 | 68.28 | 0 | 0 | 0 | 17.65
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 265.37 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 265.37 | 100
Total On-Site and Utility Electric Sources | 265.37 | 100
Total Electricity End Uses | 265.37 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 90 | 180
ATTIC_SOFFIT_WEST | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 11.44 | 270 | 180
ATTIC_SOFFIT_SOUTH | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 16.97 | 225 | 180
ATTIC_SOFFIT_EAST | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 16.97 | 315 | 180
ATTIC_ROOF_NORTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 0 | 18.45
ATTIC_ROOF_WEST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 270 | 18.45
ATTIC_ROOF_EAST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 90 | 18.45
ATTIC_ROOF_SOUTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 180 | 18.45
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW_SOUTH | 3.91 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW_EAST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW_EAST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW_EAST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW_EAST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW_WEST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW_WEST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW_WEST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW_WEST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6949.52 | 3.05
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12390.99 | 3.05
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7703.53 | 3.05
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12022.06 | 3.05
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7703.53 | 3.05
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.42 | 796.09 | 1 | Fan Energy
PSZ-AC:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.75 | 1419.42 | 1 | Fan Energy
PSZ-AC:3 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.47 | 882.46 | 1 | Fan Energy
PSZ-AC:4 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.73 | 1377.16 | 1 | Fan Energy
PSZ-AC:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.47 | 882.46 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
Nominal Capacity [W]
PSZ-AC:1_HEATC | 5676.72
PSZ-AC:2_HEATC | 6752.79
PSZ-AC:3_HEATC | 4127.81
PSZ-AC:4_HEATC | 6625.33
PSZ-AC:5_HEATC | 4127.81
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 6781.9899 | 11.1576 | 27.0997 | 0 | 0.0001 | 28174.8306 | 2837.8532
February | 5707.5606 | 9.529 | 23.559 | 0 | 0.0001 | 24494.7104 | 2401.9082
March | 6192.1958 | 10.5418 | 26.6619 | 0 | 0.0001 | 27722.2428 | 2625.8362
April | 5459.586 | 9.465 | 24.4296 | 0 | 0.0001 | 25402.3437 | 2331.8806
May | 5855.465 | 10.2058 | 26.4963 | 0 | 0.0001 | 27551.6155 | 2506.3174
June | 6226.9887 | 10.8805 | 28.3241 | 0 | 0.0001 | 29452.3827 | 2667.9982
July | 6541.5135 | 11.4342 | 29.7774 | 0 | 0.0001 | 30963.6654 | 2803.1702
August | 6940.5418 | 12.1337 | 31.6047 | 0 | 0.0001 | 32863.7238 | 2974.3585
September | 5862.897 | 10.2403 | 26.6463 | 0 | 0.0001 | 27707.7163 | 2511.6072
October | 5718.0103 | 9.9446 | 25.7574 | 0 | 0.0001 | 26783.1476 | 2445.3639
November | 5820.2385 | 9.9019 | 25.0241 | 0 | 0.0001 | 26019.2006 | 2467.4475
December | 6614.8424 | 10.9016 | 26.5347 | 0 | 0.0001 | 27587.5681 | 2769.777
Annual Sum or Average | 73721.8296 | 126.3359 | 321.9152 | 0 | 0.0013 | 334723.1477 | 31343.518
Minimum of Months | 5459.586 | 9.465 | 23.559 | 0 | 0.0001 | 24494.7104 | 2331.8806
Maximum of Months | 6940.5418 | 12.1337 | 31.6047 | 0 | 0.0001 | 32863.7238 | 2974.3585
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 22337300000 | 15534.255 | 02-JAN-16:49 | 4950.048 | 3712.536 | 5357.581 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 19419700000 | 14620.602 | 10-FEB-14:30 | 4950.048 | 3712.536 | 5357.581 | 0 | 600.436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 21978500000 | 16929.308 | 30-MAR-15:00 | 4950.048 | 3712.536 | 5357.581 | 0 | 2909.142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 20139300000 | 18402.538 | 26-APR-15:39 | 4950.048 | 3712.536 | 5357.581 | 0 | 4382.372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 21843300000 | 19585.147 | 24-MAY-15:00 | 4950.048 | 3712.536 | 5357.581 | 0 | 5564.981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 23350200000 | 21050.681 | 28-JUN-13:30 | 4950.048 | 3712.536 | 5357.581 | 0 | 7030.515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 24548400000 | 22158.086 | 18-JUL-13:00 | 4950.048 | 3712.536 | 5357.581 | 0 | 8137.921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 26054800000 | 22143.891 | 30-AUG-13:00 | 4950.048 | 3712.536 | 5357.581 | 0 | 8123.726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 21967000000 | 20001.626 | 01-SEP-12:00 | 4950.048 | 3712.536 | 5357.581 | 0 | 5981.461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 21234000000 | 18881.938 | 05-OCT-14:00 | 4950.048 | 3712.536 | 5357.581 | 0 | 4861.772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 20628300000 | 16131.506 | 01-NOV-16:00 | 4950.048 | 3712.536 | 5357.581 | 0 | 597.251 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 21871800000 | 15600.617 | 22-DEC-16:40 | 4950.048 | 3712.536 | 5357.581 | 0 | 66.362 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 265373000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 19419700000 | 14620.602 |  | 4950.048 | 3712.536 | 5357.581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 26054800000 | 22158.086 |  | 4950.048 | 3712.536 | 5357.581 | 0 | 8137.921 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 5535.04 | 471.08 | 0 | 6006.12
Cost per Total Building Area ($/m2) | 5.13 | 0.44 | 0 | 5.57
Cost per Net Conditioned Building Area ($/m2) | 10.83 | 0.92 | 0 | 11.75
13-minneapolis
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 429.74 | 398.22 | 840.71
Net Site Energy | 429.74 | 398.22 | 840.71
Total Source Energy | 1119.37 | 1037.28 | 2189.87
Net Source Energy | 1119.37 | 1037.28 | 2189.87
Area (m2)
Total Building Area | 1079.13
Net Conditioned Building Area | 511.16
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 140.24 | 0 | 0 | 0 | 0
Cooling | 23.41 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.77 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 107.56 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 12.27 | 0 | 0 | 0 | 17.65
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 277.23 | 152.51 | 0 | 0 | 0 | 17.65
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 277.23 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 277.23 | 100
Total On-Site and Utility Electric Sources | 277.23 | 100
Total Electricity End Uses | 277.23 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 90 | 180
ATTIC_SOFFIT_WEST | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 11.44 | 270 | 180
ATTIC_SOFFIT_SOUTH | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 16.97 | 225 | 180
ATTIC_SOFFIT_EAST | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 16.97 | 315 | 180
ATTIC_ROOF_NORTH | ROOFS | 0.22 | 0.154 | 0.16 | 197.51 | 0 | 18.45
ATTIC_ROOF_WEST | ROOFS | 0.22 | 0.154 | 0.16 | 101.87 | 270 | 18.45
ATTIC_ROOF_EAST | ROOFS | 0.22 | 0.154 | 0.16 | 101.87 | 90 | 18.45
ATTIC_ROOF_SOUTH | ROOFS | 0.22 | 0.154 | 0.16 | 197.51 | 180 | 18.45
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW_SOUTH | 3.91 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW_EAST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW_EAST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW_EAST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW_EAST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW_WEST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW_WEST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW_WEST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW_WEST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8169.36 | 3.05
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13835 | 3.05
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7981.98 | 3.05
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14312.1 | 3.05
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8156.11 | 3.05
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.45 | 845.1 | 1 | Fan Energy
PSZ-AC:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.77 | 1451.16 | 1 | Fan Energy
PSZ-AC:3 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.47 | 897.76 | 1 | Fan Energy
PSZ-AC:4 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.75 | 1421.45 | 1 | Fan Energy
PSZ-AC:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.48 | 901.78 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
Nominal Capacity [W]
PSZ-AC:1_HEATC | 7450.9
PSZ-AC:2_HEATC | 8524.88
PSZ-AC:3_HEATC | 5188.74
PSZ-AC:4_HEATC | 8418.87
PSZ-AC:5_HEATC | 5203.1
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 7727.7672 | 11.9424 | 16.0814 | 0 | 0.0001 | 10563.0651 | 3145.627
February | 6258.1861 | 10.001 | 14.0968 | 0 | 0.0001 | 9261.2624 | 2578.9437
March | 5801.6478 | 9.8384 | 14.9147 | 0 | 0.0001 | 9801.3317 | 2445.0047
April | 4513.4853 | 8.0727 | 12.9665 | 0 | 0.0001 | 8522.8733 | 1942.1543
May | 5034.1224 | 9.1211 | 14.8439 | 0 | 0.0001 | 9757.3329 | 2177.3893
June | 5561.117 | 10.1003 | 16.4771 | 0 | 0.0001 | 10830.9728 | 2407.6553
July | 5622.3307 | 10.2125 | 16.6619 | 0 | 0.0001 | 10952.4417 | 2434.2576
August | 6015.6329 | 10.9295 | 17.8359 | 0 | 0.0001 | 11724.1373 | 2604.7894
September | 4835.8012 | 8.7747 | 14.3014 | 0 | 0.0001 | 9400.7645 | 2092.8507
October | 4728.1397 | 8.455 | 13.5781 | 0 | 0.0001 | 8924.8452 | 2034.3702
November | 5525.6278 | 9.3821 | 14.2433 | 0 | 0.0001 | 9360.2106 | 2329.8038
December | 7089.9462 | 11.2747 | 15.7895 | 0 | 0.0001 | 10373.0531 | 2916.3951
Annual Sum or Average | 68713.8043 | 118.1043 | 181.7905 | 0 | 0.0013 | 119472.2907 | 29109.2412
Minimum of Months | 4513.4853 | 8.0727 | 12.9665 | 0 | 0.0001 | 8522.8733 | 1942.1543
Maximum of Months | 7727.7672 | 11.9424 | 17.8359 | 0 | 0.0001 | 11724.1373 | 3145.627
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 24510800000 | 15693.919 | 02-JAN-16:40 | 4950.048 | 3712.536 | 5517.245 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 21490100000 | 14223.174 | 16-FEB-13:20 | 4950.048 | 3712.536 | 5517.245 | 0 | 43.344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 22743300000 | 14832.106 | 23-MAR-15:30 | 4950.048 | 3712.536 | 5517.245 | 0 | 652.276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 19776700000 | 16600.308 | 27-APR-14:00 | 4950.048 | 3712.536 | 5517.245 | 0 | 2420.478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 22641200000 | 20838.446 | 31-MAY-12:09 | 4950.048 | 3712.536 | 5517.245 | 0 | 6658.617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 25132500000 | 23356.98 | 30-JUN-14:00 | 4950.048 | 3712.536 | 5517.245 | 0 | 9177.151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 25414300000 | 23053.279 | 13-JUL-15:20 | 4950.048 | 3712.536 | 5517.245 | 0 | 8873.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 27205000000 | 22665.548 | 25-AUG-15:00 | 4950.048 | 3712.536 | 5517.245 | 0 | 8485.718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 21813800000 | 20910.491 | 14-SEP-14:00 | 4950.048 | 3712.536 | 5517.245 | 0 | 6730.662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 20709400000 | 16765.882 | 06-OCT-14:00 | 4950.048 | 3712.536 | 5517.245 | 0 | 2586.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 21719700000 | 16110.979 | 02-NOV-16:00 | 4950.048 | 3712.536 | 5517.245 | 0 | 417.06 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 24069900000 | 15693.919 | 01-DEC-16:30 | 4950.048 | 3712.536 | 5517.245 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 277226000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 19776700000 | 14223.174 |  | 4950.048 | 3712.536 | 5517.245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 27205000000 | 23356.98 |  | 4950.048 | 3712.536 | 5517.245 | 0 | 9177.151 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 5752.24 | 1209.32 | 0 | 6961.56
Cost per Total Building Area ($/m2) | 5.33 | 1.12 | 0 | 6.45
Cost per Net Conditioned Building Area ($/m2) | 11.25 | 2.37 | 0 | 13.62
14-helena
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 382.4 | 354.36 | 748.11
Net Site Energy | 382.4 | 354.36 | 748.11
Total Source Energy | 1062.09 | 984.21 | 2077.82
Net Source Energy | 1062.09 | 984.21 | 2077.82
Area (m2)
Total Building Area | 1079.13
Net Conditioned Building Area | 511.16
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 99.74 | 0 | 0 | 0 | 0
Cooling | 16.01 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.77 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 108.08 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 12.31 | 0 | 0 | 0 | 17.65
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 270.35 | 112.05 | 0 | 0 | 0 | 17.65
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 270.35 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 270.35 | 100
Total On-Site and Utility Electric Sources | 270.35 | 100
Total Electricity End Uses | 270.35 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 90 | 180
ATTIC_SOFFIT_WEST | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 11.44 | 270 | 180
ATTIC_SOFFIT_SOUTH | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 16.97 | 225 | 180
ATTIC_SOFFIT_EAST | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 16.97 | 315 | 180
ATTIC_ROOF_NORTH | ROOFS | 0.22 | 0.154 | 0.16 | 197.51 | 0 | 18.45
ATTIC_ROOF_WEST | ROOFS | 0.22 | 0.154 | 0.16 | 101.87 | 270 | 18.45
ATTIC_ROOF_EAST | ROOFS | 0.22 | 0.154 | 0.16 | 101.87 | 90 | 18.45
ATTIC_ROOF_SOUTH | ROOFS | 0.22 | 0.154 | 0.16 | 197.51 | 180 | 18.45
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW_SOUTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW_SOUTH | 3.91 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW_EAST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW_EAST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW_EAST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW_EAST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW_NORTH | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW_WEST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW_WEST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW_WEST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW_WEST | 2.79 | 3.24 | 0.39 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7256.73 | 3.05
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13274.65 | 3.05
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8226.84 | 3.05
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12963.13 | 3.05
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8256.63 | 3.05
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.44 | 831.28 | 1 | Fan Energy
PSZ-AC:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.8 | 1520.65 | 1 | Fan Energy
PSZ-AC:3 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.5 | 942.41 | 1 | Fan Energy
PSZ-AC:4 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.78 | 1484.96 | 1 | Fan Energy
PSZ-AC:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.5 | 945.82 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
Nominal Capacity [W]
PSZ-AC:1_HEATC | 6725.65
PSZ-AC:2_HEATC | 7921.85
PSZ-AC:3_HEATC | 4827.86
PSZ-AC:4_HEATC | 7808.16
PSZ-AC:5_HEATC | 4838.73
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 7307.2825 | 11.5679 | 17.8807 | 0 | 0.0001 | 423993.4642 | 3006.0989
February | 6035.9986 | 9.7788 | 15.5778 | 0 | 0.0001 | 369426.7584 | 2504.7071
March | 5982.5471 | 10.1159 | 16.9722 | 0 | 0.0001 | 402567.0986 | 2523.4839
April | 4906.4565 | 8.5238 | 14.7422 | 0 | 0.0001 | 349708.3664 | 2091.573
May | 5242.1067 | 9.2244 | 16.1757 | 0 | 0.0001 | 383730.7558 | 2246.0169
June | 5564.6761 | 9.827 | 17.2975 | 0 | 0.0001 | 410348.4039 | 2387.6041
July | 5772.2999 | 10.2009 | 17.9691 | 0 | 0.0001 | 426279.5459 | 2477.3862
August | 6049.0056 | 10.6915 | 18.836 | 0 | 0.0001 | 446846.085 | 2596.2927
September | 5187.9203 | 9.1557 | 16.1049 | 0 | 0.0001 | 382054.4726 | 2225.3765
October | 5154.7117 | 9.0071 | 15.6762 | 0 | 0.0001 | 371872.1961 | 2202.429
November | 5574.8872 | 9.4498 | 15.8998 | 0 | 0.0001 | 377134.5783 | 2353.7784
December | 6889.3316 | 11.0602 | 17.415 | 0 | 0.0001 | 412977.1687 | 2849.0473
Annual Sum or Average | 69667.2239 | 118.6031 | 200.5473 | 0 | 0.0014 | 4756938.8939 | 29463.794
Minimum of Months | 4906.4565 | 8.5238 | 14.7422 | 0 | 0.0001 | 349708.3664 | 2091.573
Maximum of Months | 7307.2825 | 11.5679 | 18.836 | 0 | 0.0001 | 446846.085 | 3006.0989
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 24096600000 | 15901.781 | 02-JAN-08:09 | 4950.048 | 3712.536 | 5725.107 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 20995400000 | 14956.359 | 03-FEB-14:30 | 4950.048 | 3712.536 | 5725.107 | 0 | 568.668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 22878900000 | 17047.372 | 30-MAR-15:00 | 4950.048 | 3712.536 | 5725.107 | 0 | 2659.681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 19874800000 | 15946.701 | 06-APR-15:00 | 4950.048 | 3712.536 | 5725.107 | 0 | 1559.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 21808300000 | 18537.975 | 17-MAY-15:39 | 4950.048 | 3712.536 | 5725.107 | 0 | 4150.283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 23321100000 | 22347.068 | 26-JUN-14:00 | 4950.048 | 3712.536 | 5725.107 | 0 | 7959.377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 24226500000 | 21906.434 | 21-JUL-15:00 | 4950.048 | 3712.536 | 5725.107 | 0 | 7518.742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 25395300000 | 21223.974 | 09-AUG-15:00 | 4950.048 | 3712.536 | 5725.107 | 0 | 6836.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 21713100000 | 19904.591 | 12-SEP-13:00 | 4950.048 | 3712.536 | 5725.107 | 0 | 5516.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 21134400000 | 17872.718 | 06-OCT-15:39 | 4950.048 | 3712.536 | 5725.107 | 0 | 3485.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 21433500000 | 15901.781 | 08-NOV-16:00 | 4950.048 | 3712.536 | 5725.107 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 23470500000 | 15901.781 | 01-DEC-16:40 | 4950.048 | 3712.536 | 5725.107 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 270348000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 19874800000 | 14956.359 |  | 4950.048 | 3712.536 | 5725.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 25395300000 | 22347.068 |  | 4950.048 | 3712.536 | 5725.107 | 0 | 7959.377 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 5716.53 | 897.07 | 0 | 6613.6
Cost per Total Building Area ($/m2) | 5.3 | 0.83 | 0 | 6.13
Cost per Net Conditioned Building Area ($/m2) | 11.18 | 1.75 | 0 | 12.94
15-duluth
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 454.62 | 421.28 | 889.39
Net Site Energy | 454.62 | 421.28 | 889.39
Total Source Energy | 1128.15 | 1045.42 | 2207.05
Net Source Energy | 1128.15 | 1045.42 | 2207.05
Area (m2)
Total Building Area | 1079.13
Net Conditioned Building Area | 511.16
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 172.58 | 0 | 0 | 0 | 0
Cooling | 12.57 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.75 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 110.58 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 12.65 | 0 | 0 | 0 | 17.65
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 269.39 | 185.23 | 0 | 0 | 0 | 17.65
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 269.39 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 269.39 | 100
Total On-Site and Utility Electric Sources | 269.39 | 100
Total Electricity End Uses | 269.39 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 90 | 180
ATTIC_SOFFIT_WEST | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 11.44 | 270 | 180
ATTIC_SOFFIT_SOUTH | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 16.97 | 225 | 180
ATTIC_SOFFIT_EAST | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 16.97 | 315 | 180
ATTIC_ROOF_NORTH | ROOFS | 0.22 | 0.154 | 0.16 | 197.51 | 0 | 18.45
ATTIC_ROOF_WEST | ROOFS | 0.22 | 0.154 | 0.16 | 101.87 | 270 | 18.45
ATTIC_ROOF_EAST | ROOFS | 0.22 | 0.154 | 0.16 | 101.87 | 90 | 18.45
ATTIC_ROOF_SOUTH | ROOFS | 0.22 | 0.154 | 0.16 | 197.51 | 180 | 18.45
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW_SOUTH | 2.79 | 3.24 | 0.49 | 0.49 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW_SOUTH | 2.79 | 3.24 | 0.49 | 0.49 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW_SOUTH | 2.79 | 3.24 | 0.49 | 0.49 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW_SOUTH | 2.79 | 3.24 | 0.49 | 0.49 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW_SOUTH | 2.79 | 3.24 | 0.49 | 0.49 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW_SOUTH | 2.79 | 3.24 | 0.49 | 0.49 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW_SOUTH | 3.91 | 3.24 | 0.49 | 0.49 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW_EAST | 2.79 | 3.24 | 0.49 | 0.49 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW_EAST | 2.79 | 3.24 | 0.49 | 0.49 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW_EAST | 2.79 | 3.24 | 0.49 | 0.49 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW_EAST | 2.79 | 3.24 | 0.49 | 0.49 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW_NORTH | 2.79 | 3.24 | 0.49 | 0.49 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW_NORTH | 2.79 | 3.24 | 0.49 | 0.49 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW_NORTH | 2.79 | 3.24 | 0.49 | 0.49 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW_NORTH | 2.79 | 3.24 | 0.49 | 0.49 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW_NORTH | 2.79 | 3.24 | 0.49 | 0.49 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW_NORTH | 2.79 | 3.24 | 0.49 | 0.49 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW_WEST | 2.79 | 3.24 | 0.49 | 0.49 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW_WEST | 2.79 | 3.24 | 0.49 | 0.49 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW_WEST | 2.79 | 3.24 | 0.49 | 0.49 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW_WEST | 2.79 | 3.24 | 0.49 | 0.49 | No | PERIMETER_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6950.13 | 3.05
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12757.75 | 3.05
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7888.91 | 3.05
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13184.68 | 3.05
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7927.81 | 3.05
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.42 | 796.16 | 1 | Fan Energy
PSZ-AC:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.77 | 1461.43 | 1 | Fan Energy
PSZ-AC:3 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.48 | 903.7 | 1 | Fan Energy
PSZ-AC:4 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.75 | 1428.51 | 1 | Fan Energy
PSZ-AC:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.48 | 908.15 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
Nominal Capacity [W]
PSZ-AC:1_HEATC | 7396.31
PSZ-AC:2_HEATC | 8591.89
PSZ-AC:3_HEATC | 5225.1
PSZ-AC:4_HEATC | 8476.98
PSZ-AC:5_HEATC | 5240.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 7776.1932 | 12.0214 | 16.1958 | 0 | 0.0001 | 10638.2223 | 3165.7387
February | 6622.247 | 10.3714 | 14.2285 | 0 | 0.0001 | 9346.6961 | 2708.7603
March | 6370.0857 | 10.5211 | 15.46 | 0 | 0.0001 | 10158.5103 | 2657.6743
April | 4788.1283 | 8.371 | 13.1274 | 0 | 0.0001 | 8627.9136 | 2041.8958
May | 4743.6834 | 8.5116 | 13.7166 | 0 | 0.0001 | 9015.9813 | 2043.8131
June | 5006.1054 | 9.0838 | 14.805 | 0 | 0.0001 | 9731.8304 | 2166.5552
July | 5217.093 | 9.4703 | 15.441 | 0 | 0.0001 | 10149.892 | 2258.2193
August | 5411.0475 | 9.8195 | 16.0058 | 0 | 0.0001 | 10521.1586 | 2341.9018
September | 4583.4224 | 8.2806 | 13.4373 | 0 | 0.0001 | 8832.6328 | 1980.1701
October | 4866.7798 | 8.6098 | 13.673 | 0 | 0.0001 | 8986.9061 | 2085.1227
November | 5950.6013 | 9.8979 | 14.6689 | 0 | 0.0001 | 9638.9796 | 2489.3223
December | 7364.4918 | 11.5573 | 15.8997 | 0 | 0.0001 | 10444.6393 | 3014.6115
Annual Sum or Average | 68699.8789 | 116.5157 | 176.659 | 0 | 0.0013 | 116093.3624 | 28953.7852
Minimum of Months | 4583.4224 | 8.2806 | 13.1274 | 0 | 0.0001 | 8627.9136 | 1980.1701
Maximum of Months | 7776.1932 | 12.0214 | 16.1958 | 0 | 0.0001 | 10638.2223 | 3165.7387
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 24685200000 | 15674.619 | 02-JAN-16:30 | 4950.048 | 3712.536 | 5497.945 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 21688300000 | 14228.877 | 28-FEB-13:39 | 4950.048 | 3712.536 | 5497.945 | 0 | 68.347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 23572100000 | 14319.484 | 22-MAR-14:30 | 4950.048 | 3712.536 | 5497.945 | 0 | 158.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 20020400000 | 14905.171 | 04-APR-15:50 | 4950.048 | 3712.536 | 5497.945 | 0 | 744.641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 20920900000 | 18175.533 | 31-MAY-15:00 | 4950.048 | 3712.536 | 5497.945 | 0 | 4015.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 22582000000 | 20946.007 | 14-JUN-14:00 | 4950.048 | 3712.536 | 5497.945 | 0 | 6785.477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 23552100000 | 22194.277 | 07-JUL-14:39 | 4950.048 | 3712.536 | 5497.945 | 0 | 8033.747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 24413600000 | 21303.258 | 11-AUG-15:30 | 4950.048 | 3712.536 | 5497.945 | 0 | 7142.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 20495500000 | 20012.282 | 07-SEP-14:00 | 4950.048 | 3712.536 | 5497.945 | 0 | 5851.752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 20853400000 | 15787.565 | 06-OCT-14:00 | 4950.048 | 3712.536 | 5497.945 | 0 | 1627.036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 22366500000 | 15674.619 | 01-NOV-16:49 | 4950.048 | 3712.536 | 5497.945 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 24236000000 | 15674.619 | 01-DEC-16:19 | 4950.048 | 3712.536 | 5497.945 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 269386000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 20020400000 | 14228.877 |  | 4950.048 | 3712.536 | 5497.945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 24685200000 | 22194.277 |  | 4950.048 | 3712.536 | 5497.945 | 0 | 8033.747 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 5575.23 | 1462.26 | 0 | 7037.49
Cost per Total Building Area ($/m2) | 5.17 | 1.36 | 0 | 6.52
Cost per Net Conditioned Building Area ($/m2) | 10.91 | 2.86 | 0 | 13.77
16-fairbanks
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 635.45 | 588.85 | 1243.16
Net Site Energy | 635.45 | 588.85 | 1243.16
Total Source Energy | 1422.74 | 1318.41 | 2783.37
Net Source Energy | 1422.74 | 1318.41 | 2783.37
Area (m2)
Total Building Area | 1079.13
Net Conditioned Building Area | 511.16
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 328.46 | 0 | 0 | 0 | 0
Cooling | 10.14 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.61 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 137.65 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 13.11 | 0 | 0 | 0 | 17.65
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 293.88 | 341.57 | 0 | 0 | 0 | 17.65
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 293.88 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 293.88 | 100
Total On-Site and Utility Electric Sources | 293.88 | 100
Total Electricity End Uses | 293.88 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 90 | 180
ATTIC_SOFFIT_WEST | EXPOSED-FLOOR | 0.3 | 0.363 | 0.4 | 11.44 | 270 | 180
ATTIC_SOFFIT_SOUTH | EXPOSED-FLOOR | 0.3 | 0.363 | 0.4 | 16.97 | 225 | 180
ATTIC_SOFFIT_EAST | EXPOSED-FLOOR | 0.3 | 0.363 | 0.4 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | EXPOSED-FLOOR | 0.3 | 0.363 | 0.4 | 16.97 | 315 | 180
ATTIC_ROOF_NORTH | ROOFS | 0.22 | 0.154 | 0.16 | 197.51 | 0 | 18.45
ATTIC_ROOF_WEST | ROOFS | 0.22 | 0.154 | 0.16 | 101.87 | 270 | 18.45
ATTIC_ROOF_EAST | ROOFS | 0.22 | 0.154 | 0.16 | 101.87 | 90 | 18.45
ATTIC_ROOF_SOUTH | ROOFS | 0.22 | 0.154 | 0.16 | 197.51 | 180 | 18.45
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW_SOUTH | 2.79 | 2.62 | 0.49 | 0.49 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW_SOUTH | 2.79 | 2.62 | 0.49 | 0.49 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW_SOUTH | 2.79 | 2.62 | 0.49 | 0.49 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW_SOUTH | 2.79 | 2.62 | 0.49 | 0.49 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW_SOUTH | 2.79 | 2.62 | 0.49 | 0.49 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW_SOUTH | 2.79 | 2.62 | 0.49 | 0.49 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW_SOUTH | 3.91 | 2.62 | 0.49 | 0.49 | No | PERIMETER_ZN_1_WALL_SOUTH
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW_EAST | 2.79 | 2.62 | 0.49 | 0.49 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW_EAST | 2.79 | 2.62 | 0.49 | 0.49 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW_EAST | 2.79 | 2.62 | 0.49 | 0.49 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW_EAST | 2.79 | 2.62 | 0.49 | 0.49 | No | PERIMETER_ZN_2_WALL_EAST
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW_NORTH | 2.79 | 2.62 | 0.49 | 0.49 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW_NORTH | 2.79 | 2.62 | 0.49 | 0.49 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW_NORTH | 2.79 | 2.62 | 0.49 | 0.49 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW_NORTH | 2.79 | 2.62 | 0.49 | 0.49 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW_NORTH | 2.79 | 2.62 | 0.49 | 0.49 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW_NORTH | 2.79 | 2.62 | 0.49 | 0.49 | No | PERIMETER_ZN_3_WALL_NORTH
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW_WEST | 2.79 | 2.62 | 0.49 | 0.49 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW_WEST | 2.79 | 2.62 | 0.49 | 0.49 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW_WEST | 2.79 | 2.62 | 0.49 | 0.49 | No | PERIMETER_ZN_4_WALL_WEST
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW_WEST | 2.79 | 2.62 | 0.49 | 0.49 | No | PERIMETER_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8176.22 | 3.05
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14910.51 | 3.05
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9247.73 | 3.05
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14596.86 | 3.05
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9247.73 | 3.05
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.49 | 936.61 | 1 | Fan Energy
PSZ-AC:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.9 | 1708.04 | 1 | Fan Energy
PSZ-AC:3 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.56 | 1059.35 | 1 | Fan Energy
PSZ-AC:4 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.88 | 1672.11 | 1 | Fan Energy
PSZ-AC:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.56 | 1059.35 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
Nominal Capacity [W]
PSZ-AC:1_HEATC | 9466.85
PSZ-AC:2_HEATC | 10771.25
PSZ-AC:3_HEATC | 6556.46
PSZ-AC:4_HEATC | 10641.32
PSZ-AC:5_HEATC | 6556.46
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 9432.4482 | 10.4402 | 39.3131 | 0 | 0.0001 | 7886.3079 | 3553.5475
February | 8075.597 | 9.0019 | 34.9858 | 0 | 0.0001 | 7018.5699 | 3052.1393
March | 7318.0006 | 8.4375 | 37.5632 | 0 | 0.0001 | 7537.0197 | 2808.9088
April | 5093.4932 | 6.1151 | 31.2159 | 0 | 0.0001 | 6264.4658 | 1992.3645
May | 4422.777 | 5.4999 | 31.0823 | 0 | 0.0001 | 6238.3241 | 1759.2606
June | 4672.2344 | 5.8325 | 33.3037 | 0 | 0.0001 | 6684.235 | 1861.9323
July | 4611.8793 | 5.7575 | 32.8815 | 0 | 0.0001 | 6599.4877 | 1837.9388
August | 4793.1618 | 5.9811 | 34.1169 | 0 | 0.0001 | 6847.4323 | 1909.764
September | 4341.7996 | 5.3651 | 29.7997 | 0 | 0.0001 | 5980.7854 | 1721.8013
October | 5846.7538 | 6.9501 | 34.3834 | 0 | 0.0001 | 6899.8823 | 2276.3514
November | 7852.7977 | 8.9242 | 37.5913 | 0 | 0.0001 | 7542.1058 | 2994.1976
December | 8876.9846 | 9.9404 | 39.4041 | 0 | 0.0001 | 7905.149 | 3361.9819
Annual Sum or Average | 75337.9272 | 88.2456 | 415.641 | 0 | 0.0014 | 83403.7648 | 29130.1881
Minimum of Months | 4341.7996 | 5.3651 | 29.7997 | 0 | 0.0001 | 5980.7854 | 1721.8013
Maximum of Months | 9432.4482 | 10.4402 | 39.4041 | 0 | 0.0001 | 7905.149 | 3553.5475
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 27788300000 | 16612.13 | 02-JAN-08:09 | 4950.048 | 3712.536 | 6435.457 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 24730700000 | 16612.13 | 01-FEB-08:09 | 4950.048 | 3712.536 | 6435.457 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 26557500000 | 16612.13 | 01-MAR-08:09 | 4950.048 | 3712.536 | 6435.457 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 22073500000 | 16252.744 | 25-APR-15:00 | 4950.048 | 3712.536 | 6435.457 | 0 | 1154.703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 21981400000 | 19274.398 | 24-MAY-14:00 | 4950.048 | 3712.536 | 6435.457 | 0 | 4176.356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 23552600000 | 21347.788 | 21-JUN-15:00 | 4950.048 | 3712.536 | 6435.457 | 0 | 6249.746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 23254000000 | 21055.867 | 11-JUL-15:00 | 4950.048 | 3712.536 | 6435.457 | 0 | 5957.826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 24127700000 | 20828.461 | 15-AUG-14:30 | 4950.048 | 3712.536 | 6435.457 | 0 | 5730.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 21073900000 | 16671.174 | 01-SEP-15:39 | 4950.048 | 3712.536 | 6435.457 | 0 | 1573.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 24312500000 | 16612.13 | 03-OCT-07:10 | 4950.048 | 3712.536 | 6435.457 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 26575400000 | 16612.13 | 01-NOV-08:09 | 4950.048 | 3712.536 | 6435.457 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 27854600000 | 16612.13 | 01-DEC-08:09 | 4950.048 | 3712.536 | 6435.457 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 293882000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 21073900000 | 16252.744 |  | 4950.048 | 3712.536 | 6435.457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 27854600000 | 21347.788 |  | 4950.048 | 3712.536 | 6435.457 | 0 | 6249.746 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 8109.48 | 1401.35 | 0 | 9510.84
Cost per Total Building Area ($/m2) | 7.51 | 1.3 | 0 | 8.81
Cost per Net Conditioned Building Area ($/m2) | 15.86 | 2.74 | 0 | 18.61

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago-O'Hare | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7A | 8A
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 200.6 | 1755.3 | 396.1 | 1969.7 | 2244.9 | 250 | 102.9 | 4464.9 | 111.5 | 561.4 | 3959.5 | 892.2 | 1126.2 | 133.5 | 153.9 | 7.93
Fabric
Exterior walls
| Construction Type | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall
| R-value (m2·K / W) | 0.38314 | 0.38314 | 0.38314 | 1.1682 | 1.1682 | 1.1682 | 1.1682 | 1.1682 | 1.1682 | 1.1682 | 1.4327 | 1.4327 | 1.692 | 1.692 | 1.9531 | 2.2026
Roof
| Construction Type | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic
| R-value (m2·K / W) | 5.1546 | 5.1546 | 5.1546 | 5.1546 | 5.1546 | 5.1546 | 5.1546 | 5.1546 | 5.1546 | 5.1546 | 5.1546 | 5.1546 | 6.4935 | 6.4935 | 6.4935 | 6.4935
Window
| U-Factor (W / m2·K) | 6.88 | 6.88 | 6.88 | 3.24 | 3.24 | 3.24 | 6.88 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 2.62
| SHGC | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.49 | 0.49
| Visible transmittance | 0.25 | 0.25 | 0.25 | 0.318 | 0.318 | 0.318 | 0.39 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.49 | 0.49
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC:1_COOLC DXCOIL | 8.873 | 7.5704 | 7.5484 | 6.5358 | 4.8013 | 6.8641 | 4.1303 | 6.4773 | 6.1895 | 4.6992 | 7.8951 | 6.9495 | 8.1694 | 7.2567 | 6.9501 | 8.1762
| PSZ-AC:2_COOLC DXCOIL | 7.7889 | 11.5604 | 11.0102 | 10.556 | 5.7824 | 8.4192 | 7.3377 | 11.0874 | 10.3771 | 8.0376 | 13.3154 | 12.391 | 13.835 | 13.2746 | 12.7577 | 14.9105
| PSZ-AC:3_COOLC DXCOIL | 6.4792 | 6.9315 | 7.7323 | 5.9959 | 3.5652 | 5.5523 | 3.7007 | 6.2422 | 6.4998 | 5.0405 | 7.5348 | 7.7035 | 7.982 | 8.2268 | 7.8889 | 9.2477
| PSZ-AC:4_COOLC DXCOIL | 8.3104 | 11.0639 | 9.4722 | 9.9827 | 4.592 | 7.5291 | 5.7648 | 10.6977 | 10.1593 | 7.8533 | 13.8017 | 12.0221 | 14.3121 | 12.9631 | 13.1847 | 14.5969
| PSZ-AC:5_COOLC DXCOIL | 7.3048 | 7.1314 | 8.5478 | 6.106 | 3.9828 | 6.0185 | 4.22 | 6.4604 | 6.4998 | 5.0264 | 7.814 | 7.7035 | 8.1561 | 8.2566 | 7.9278 | 9.2477
Heating (kW)
| PSZ-AC:1_HEATC | 4446.67 | 5033.73 | 4736.89 | 4976.96 | 3393.2 | 4702.56 | 3331.51 | 5469.5 | 4535.7 | 4380.94 | 6811.71 | 5676.72 | 7450.9 | 6725.65 | 7396.31 | 9466.85
| PSZ-AC:2_HEATC | 3723.35 | 5769 | 5702.41 | 5643.9 | 3478.39 | 4824.95 | 4400.25 | 6394.51 | 5411.87 | 5182.55 | 7849.81 | 6752.79 | 8524.88 | 7921.85 | 8591.89 | 10771.25
| PSZ-AC:3_HEATC | 3036.87 | 3599.72 | 3886.42 | 3461.06 | 2120.53 | 3081.25 | 2333.77 | 3906.07 | 3330.24 | 3187.94 | 4762.12 | 4127.81 | 5188.74 | 4827.86 | 5225.1 | 6556.46
| PSZ-AC:4_HEATC | 3995.32 | 5711.63 | 5119.67 | 5571.6 | 2975 | 4475.73 | 3733.21 | 6305 | 5335.89 | 5115.79 | 7734.39 | 6625.33 | 8418.87 | 7808.16 | 8476.98 | 10641.32
| PSZ-AC:5_HEATC | 3452.7 | 3858.54 | 4217 | 3469.09 | 2297.1 | 3264.04 | 2554.03 | 3915.18 | 3330.24 | 3182.06 | 4776.06 | 4127.81 | 5203.1 | 4838.73 | 5240.65 | 6556.46
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC:1_COOLC DXCOIL | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05
| PSZ-AC:2_COOLC DXCOIL | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05
| PSZ-AC:3_COOLC DXCOIL | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05
| PSZ-AC:4_COOLC DXCOIL | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05
| PSZ-AC:5_COOLC DXCOIL | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05
| Heating Efficiency (%) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
HVAC Control
| Economizer | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
Fan Max Flow Rate (m3/s )
| PSZ-AC:1 FAN | 0.46 | 0.4 | 0.46 | 0.35 | 0.29 | 0.41 | 0.25 | 0.34 | 0.37 | 0.28 | 0.42 | 0.42 | 0.45 | 0.44 | 0.42 | 0.49
| PSZ-AC:2 FAN | 0.4 | 0.58 | 0.66 | 0.54 | 0.35 | 0.51 | 0.44 | 0.58 | 0.63 | 0.49 | 0.71 | 0.75 | 0.77 | 0.8 | 0.77 | 0.9
| PSZ-AC:3 FAN | 0.35 | 0.37 | 0.47 | 0.34 | 0.22 | 0.34 | 0.22 | 0.36 | 0.39 | 0.3 | 0.44 | 0.47 | 0.47 | 0.5 | 0.48 | 0.56
| PSZ-AC:4 FAN | 0.44 | 0.58 | 0.57 | 0.53 | 0.28 | 0.45 | 0.35 | 0.57 | 0.61 | 0.47 | 0.69 | 0.73 | 0.75 | 0.78 | 0.75 | 0.88
| PSZ-AC:5 FAN | 0.41 | 0.41 | 0.52 | 0.34 | 0.24 | 0.36 | 0.25 | 0.36 | 0.39 | 0.3 | 0.44 | 0.47 | 0.48 | 0.5 | 0.48 | 0.56
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.10225 | 0.12263 | 0.12236 | 0.11699 | 0.12825 | 0.1015 | 0.16223 | 0.074945 | 0.075129 | 0.073194 | 0.062163 | 0.075088 | 0.074696 | 0.076122 | 0.074505 | 0.09934
| Total Cost ($/m2) | 8.12 | 9.04 | 9.77 | 7.48 | 6.76 | 6.75 | 8.43 | 4.85 | 4.95 | 4.07 | 4.3 | 5.13 | 5.33 | 5.3 | 5.17 | 7.51
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011465 | 0.0081013 | 0.0083754 | 0.0097708 | 0.0085303 | 0.0078536 | 0.0086534 | 0.0097165 | 0.0069275 | 0.0084436 | 0.0083012 | 0.0068992 | 0.0079294 | 0.008006 | 0.0078943 | 0.0041027
| Total Cost ($/m2) | 0.12 | 0.26 | 0.17 | 0.41 | 0.12 | 0.18 | 0.29 | 0.7 | 0.28 | 0.54 | 0.83 | 0.44 | 1.12 | 0.83 | 1.36 | 1.3
Total Utility Costs
| Cost Intensity ($/m2) | 8.23 | 9.3 | 9.95 | 7.89 | 6.89 | 6.93 | 8.72 | 5.55 | 5.23 | 4.62 | 5.12 | 5.57 | 6.45 | 6.13 | 6.52 | 8.81
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 26861.1111 | 17763.8889 | 21394.4444 | 9138.8889 | 4044.4444 | 12552.7778 | 1616.6667 | 8044.4444 | 8297.2222 | 2283.3333 | 7169.4444 | 6002.7778 | 6502.7778 | 4447.2222 | 3491.6667 | 2816.6667
| Interior Lighting | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222
| Exterior Lighting | 6619.4444 | 6616.6667 | 6613.8889 | 6613.8889 | 6608.3333 | 6605.5556 | 6611.1111 | 6605.5556 | 6608.3333 | 6594.4444 | 6608.3333 | 6602.7778 | 6602.7778 | 6602.7778 | 6597.2222 | 6558.3333
| Interior Equipment | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 18138.8889 | 21127.7778 | 24169.4444 | 19227.7778 | 12241.6667 | 18630.5556 | 13838.8889 | 21158.3333 | 22155.5556 | 17133.3333 | 26772.2222 | 27083.3333 | 29877.7778 | 30022.2222 | 30716.6667 | 38236.1111
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 85641.6667 | 79530.5556 | 86202.7778 | 69005.5556 | 56919.4444 | 71813.8889 | 56088.8889 | 69836.1111 | 71086.1111 | 60036.1111 | 74572.2222 | 73713.8889 | 77008.3333 | 75097.2222 | 74830.5556 | 81633.3333
Gas (MJ)
| Heating | 300 | 23280 | 11490 | 33280 | 3930 | 13450 | 24360 | 65640 | 31830 | 57490 | 95710 | 56250 | 140240 | 99740 | 172580 | 328460
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 10690 | 11090 | 10860 | 11480 | 11400 | 11140 | 11730 | 11780 | 11720 | 11940 | 12040 | 12030 | 12270 | 12310 | 12650 | 13110
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 11000 | 34370 | 22350 | 44760 | 15330 | 24590 | 36090 | 77420 | 43560 | 69430 | 107760 | 68280 | 152510 | 112050 | 185230 | 341570
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 319310 | 320680 | 332680 | 293180 | 220240 | 283120 | 238010 | 328830 | 299460 | 285560 | 376220 | 333650 | 429740 | 382400 | 454620 | 635450
| On-Site Production (MJ) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 89.6092 | 59.2607 | 71.3723 | 30.4875 | 13.4924 | 41.8763 | 5.3932 | 26.8364 | 27.6797 | 7.6172 | 23.9174 | 20.0254 | 21.6934 | 14.836 | 11.6483 | 9.3965
| Interior Lighting (elec) | 52.5331 | 52.5331 | 52.5331 | 52.5331 | 52.5331 | 52.5331 | 52.5331 | 52.5331 | 52.5331 | 52.5331 | 52.5331 | 52.5331 | 52.5331 | 52.5331 | 52.5331 | 52.5331
| Exterior Lighting (elec) | 22.0826 | 22.0733 | 22.0641 | 22.0641 | 22.0455 | 22.0363 | 22.0548 | 22.0363 | 22.0455 | 21.9992 | 22.0455 | 22.027 | 22.027 | 22.027 | 22.0085 | 21.8787
| Interior Equipment (elec) | 60.9658 | 60.9658 | 60.9658 | 60.9658 | 60.9658 | 60.9658 | 60.9658 | 60.9658 | 60.9658 | 60.9658 | 60.9658 | 60.9658 | 60.9658 | 60.9658 | 60.9658 | 60.9658
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 60.5117 | 70.4827 | 80.6298 | 64.1443 | 40.8385 | 62.1519 | 46.1668 | 70.5846 | 73.9114 | 57.1572 | 89.3127 | 90.3506 | 99.6729 | 100.1548 | 102.4714 | 127.5565
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 285.7024 | 265.3156 | 287.5742 | 230.204 | 189.8844 | 239.5726 | 187.1137 | 232.9747 | 237.1447 | 200.2817 | 248.7745 | 245.9111 | 256.9014 | 250.5259 | 249.6363 | 272.3305
Gas (MJ/m2)
| Heating (gas) | 0.278 | 21.5729 | 10.6475 | 30.8397 | 3.6418 | 12.4637 | 22.5737 | 60.8268 | 29.496 | 53.2744 | 88.6918 | 52.1253 | 129.9565 | 92.4263 | 159.9251 | 304.3748
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 9.9061 | 10.2768 | 10.0637 | 10.6382 | 10.5641 | 10.3231 | 10.8699 | 10.9162 | 10.8606 | 11.0645 | 11.1571 | 11.1479 | 11.3703 | 11.4073 | 11.7224 | 12.1487
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 10.1934 | 31.8497 | 20.7111 | 41.4779 | 14.2059 | 22.7869 | 33.4436 | 71.743 | 40.3659 | 64.3389 | 99.8582 | 63.2732 | 141.3268 | 103.8336 | 171.6475 | 316.5235
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 295.8958 | 297.1653 | 308.2854 | 271.6818 | 204.0903 | 262.3595 | 220.5573 | 304.7177 | 277.5013 | 264.6206 | 348.6327 | 309.1843 | 398.2282 | 354.3595 | 421.2838 | 588.854
| On-Site Production (MJ/m2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 19.8672 | 17.7953 | 16.9438 | 13.2502 | 13.9307 | 14.3829 | 13.0581 | 14.3988 | 14.243 | 13.6885 | 15.3048 | 15.5343 | 15.6939 | 15.9018 | 15.6746 | 16.6121
| Feb | 20.51 | 18.3054 | 18.0108 | 13.5521 | 13.3392 | 14.1126 | 13.0985 | 13.0103 | 15.0069 | 12.3715 | 15.3048 | 14.6206 | 14.2232 | 14.9564 | 14.2289 | 16.6121
| Mar | 20.4326 | 18.989 | 20.7009 | 15.6592 | 14.0985 | 16.0034 | 12.2652 | 15.2286 | 15.7052 | 13.7197 | 15.1796 | 16.9293 | 14.8321 | 17.0474 | 14.3195 | 16.6121
| Apr | 21.5802 | 20.0476 | 21.0024 | 17.7862 | 14.5821 | 18.3072 | 14.0147 | 16.6834 | 17.9012 | 13.547 | 16.6144 | 18.4025 | 16.6003 | 15.9467 | 14.9052 | 16.2527
| May | 22.1438 | 23.2462 | 25.1799 | 19.4533 | 15.0053 | 20.0308 | 14.4971 | 18.678 | 19.0974 | 15.7943 | 19.9192 | 19.5851 | 20.8384 | 18.538 | 18.1755 | 19.2744
| Jun | 23.5595 | 23.3688 | 30.0962 | 20.5495 | 15.0293 | 24.2359 | 15.0727 | 22.0543 | 20.8611 | 16.8425 | 22.9943 | 21.0507 | 23.357 | 22.3471 | 20.946 | 21.3478
| Jul | 23.1157 | 24.8877 | 29.571 | 22.4379 | 15.2857 | 23.7445 | 16.5306 | 23.0328 | 21.75 | 17.7173 | 23.6041 | 22.1581 | 23.0533 | 21.9064 | 22.1943 | 21.0559
| Aug | 23.3612 | 24.5092 | 29.1751 | 20.7423 | 16.0891 | 22.9568 | 15.2983 | 22.8268 | 21.99 | 17.5441 | 23.2708 | 22.1439 | 22.6655 | 21.224 | 21.3033 | 20.8285
| Sep | 22.7652 | 22.7874 | 26.7468 | 19.6403 | 15.8651 | 22.2429 | 17.2005 | 19.8903 | 19.1003 | 17.0138 | 20.6603 | 20.0016 | 20.9105 | 19.9046 | 20.0123 | 16.6712
| Oct | 22.0205 | 21.3368 | 21.8223 | 17.8653 | 14.8917 | 18.6136 | 14.4221 | 18.2528 | 17.9606 | 14.1865 | 19.227 | 18.8819 | 16.7659 | 17.8727 | 15.7876 | 16.6121
| Nov | 20.6993 | 19.1691 | 19.3746 | 15.3382 | 14.8303 | 16.4082 | 13.2875 | 16.6286 | 15.1943 | 13.6885 | 18.8246 | 16.1315 | 16.111 | 15.9018 | 15.6746 | 16.6121
| Dec | 19.6473 | 17.7213 | 16.298 | 13.1141 | 14.147 | 14.9115 | 13.0581 | 14.3988 | 14.9944 | 13.6885 | 15.3048 | 15.6006 | 15.6939 | 15.9018 | 15.6746 | 16.6121
Time of Peak Electrical Demand
| Jan | 23-JAN-15:00 | 20-JAN-16:49 | 27-JAN-16:00 | 23-JAN-16:40 | 26-JAN-13:00 | 30-JAN-16:00 | 02-JAN-16:00 | 02-JAN-16:49 | 27-JAN-15:09 | 02-JAN-16:30 | 02-JAN-16:30 | 02-JAN-16:49 | 02-JAN-16:40 | 02-JAN-08:09 | 02-JAN-16:30 | 02-JAN-08:09
| Feb | 22-FEB-15:00 | 23-FEB-15:30 | 28-FEB-16:00 | 22-FEB-15:00 | 13-FEB-11:00 | 08-FEB-15:00 | 15-FEB-15:00 | 15-FEB-13:20 | 14-FEB-15:00 | 24-FEB-14:30 | 01-FEB-16:00 | 10-FEB-14:30 | 16-FEB-13:20 | 03-FEB-14:30 | 28-FEB-13:39 | 01-FEB-08:09
| Mar | 13-MAR-15:50 | 28-MAR-14:00 | 17-MAR-15:00 | 28-MAR-15:00 | 31-MAR-14:39 | 31-MAR-15:30 | 01-MAR-13:30 | 10-MAR-10:00 | 21-MAR-15:39 | 29-MAR-15:50 | 31-MAR-15:50 | 30-MAR-15:00 | 23-MAR-15:30 | 30-MAR-15:00 | 22-MAR-14:30 | 01-MAR-08:09
| Apr | 03-APR-14:30 | 21-APR-15:30 | 26-APR-15:00 | 14-APR-15:00 | 11-APR-15:00 | 21-APR-15:20 | 13-APR-14:00 | 05-APR-15:00 | 21-APR-15:30 | 19-APR-15:30 | 28-APR-15:30 | 26-APR-15:39 | 27-APR-14:00 | 06-APR-15:00 | 04-APR-15:50 | 25-APR-15:00
| May | 19-MAY-14:00 | 18-MAY-15:30 | 30-MAY-15:00 | 15-MAY-14:00 | 30-MAY-13:00 | 31-MAY-15:00 | 17-MAY-13:00 | 31-MAY-15:00 | 31-MAY-15:00 | 05-MAY-13:39 | 30-MAY-15:00 | 24-MAY-15:00 | 31-MAY-12:09 | 17-MAY-15:39 | 31-MAY-15:00 | 24-MAY-14:00
| Jun | 28-JUN-14:00 | 13-JUN-14:00 | 28-JUN-15:00 | 19-JUN-14:00 | 30-JUN-14:00 | 27-JUN-15:00 | 16-JUN-14:00 | 30-JUN-15:20 | 29-JUN-13:00 | 28-JUN-14:00 | 08-JUN-12:00 | 28-JUN-13:30 | 30-JUN-14:00 | 26-JUN-14:00 | 14-JUN-14:00 | 21-JUN-15:00
| Jul | 13-JUL-14:00 | 31-JUL-13:00 | 11-JUL-15:00 | 03-JUL-14:00 | 12-JUL-13:39 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-13:30 | 31-JUL-14:00 | 24-JUL-14:00 | 14-JUL-10:00 | 18-JUL-13:00 | 13-JUL-15:20 | 21-JUL-15:00 | 07-JUL-14:39 | 11-JUL-15:00
| Aug | 21-AUG-14:00 | 31-AUG-15:00 | 01-AUG-15:00 | 17-AUG-15:30 | 09-AUG-13:09 | 04-AUG-14:00 | 15-AUG-12:09 | 09-AUG-14:39 | 01-AUG-13:00 | 07-AUG-14:00 | 04-AUG-15:30 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-15:30 | 15-AUG-14:30
| Sep | 11-SEP-14:00 | 15-SEP-14:00 | 11-SEP-15:00 | 11-SEP-13:39 | 25-SEP-15:20 | 01-SEP-14:00 | 28-SEP-14:00 | 08-SEP-15:09 | 29-SEP-14:30 | 01-SEP-15:50 | 06-SEP-10:00 | 01-SEP-12:00 | 14-SEP-14:00 | 12-SEP-13:00 | 07-SEP-14:00 | 01-SEP-15:39
| Oct | 06-OCT-15:00 | 06-OCT-15:00 | 02-OCT-15:00 | 02-OCT-13:30 | 05-OCT-14:20 | 06-OCT-13:50 | 13-OCT-15:30 | 03-OCT-14:00 | 03-OCT-14:50 | 03-OCT-15:39 | 31-OCT-16:49 | 05-OCT-14:00 | 06-OCT-14:00 | 06-OCT-15:39 | 06-OCT-14:00 | 03-OCT-07:10
| Nov | 07-NOV-15:09 | 03-NOV-14:39 | 13-NOV-16:49 | 22-NOV-14:00 | 09-NOV-16:00 | 10-NOV-16:40 | 14-NOV-16:00 | 03-NOV-13:00 | 10-NOV-14:00 | 01-NOV-16:49 | 02-NOV-16:49 | 01-NOV-16:00 | 02-NOV-16:00 | 08-NOV-16:00 | 01-NOV-16:49 | 01-NOV-08:09
| Dec | 15-DEC-15:39 | 20-DEC-11:00 | 13-DEC-16:00 | 05-DEC-14:00 | 19-DEC-16:49 | 06-DEC-16:30 | 01-DEC-16:49 | 01-DEC-16:40 | 08-DEC-16:49 | 01-DEC-16:19 | 01-DEC-16:19 | 22-DEC-16:40 | 01-DEC-16:30 | 01-DEC-16:40 | 01-DEC-16:19 | 01-DEC-08:09
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65
| Total Building | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65
Emissions
| Carbon Equivalent (kg) | 23685.3447 | 27148.2815 | 26425.6348 | 22062.9931 | 6928.3267 | 24664.6437 | 7205.6886 | 20241.4681 | 29823.8463 | 5624.7208 | 41701.3868 | 31343.518 | 29109.2412 | 29463.794 | 28953.7852 | 29130.1881
| CO2 (kg) | 54958.455 | 68358.262 | 62361.7924 | 50574.2745 | 18558.1049 | 58649.4063 | 19380.7444 | 46294.9586 | 69931.5818 | 14004.5705 | 97347.1908 | 73721.8296 | 68713.8043 | 69667.2239 | 68699.8789 | 75337.9272
| NOX (kg) | 96.4347 | 89.1228 | 104.4904 | 95.2729 | 15.9232 | 95.2429 | 16.6835 | 88.1597 | 120.7764 | 19.9738 | 172.1331 | 126.3359 | 118.1043 | 118.6031 | 116.5157 | 88.2456
| SO2 (kg) | 366.5807 | 379.3736 | 346.6449 | 242.2169 | 165.6316 | 395.0431 | 163.2209 | 254.9471 | 310.4294 | 46.4225 | 502.5871 | 321.9152 | 181.7905 | 200.5473 | 176.659 | 415.641
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0017 | 0.0011 | 0.0009 | 0.0009 | 0.0001 | 0.0007 | 0.0001 | 0.001 | 0.0012 | 0.0002 | 0.0015 | 0.0013 | 0.0013 | 0.0014 | 0.0013 | 0.0014
| Water Environmental Factors (m3) | 45.369 | 129.4068 | 2560.6036 | 2560.6036 | 999.3702 | 1970.1553 | 984.7907 | 15.8552 | 322.7866 | 613.3869 | 115.6946 | 334.7231 | 119.4723 | 4756.9389 | 116.0934 | 83.4038

## Picture
DOE Commercial Building Benchmark - Small Office

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | 11.15 | 70.85 | 3694.32
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | 9.85
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 5.25
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | 7.2 | 46.3 | 2414.21
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | 7.5
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 2.8
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | 13.7 | 89.4 | 4661.57
|  |  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15 | 12.15
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 8.75
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.22 | 0.64 | 0.74 | 0.68 | 0.68 | 0.71 | 0.72 | 0.72 | 0.73 | 0.68 | 0.68 | 0.58 | 0.54 | 0 | 0 | 0 | 8.44 | 52.69 | 2747.41
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.21 | 0.56 | 0.66 | 0.68 | 0.68 | 0.69 | 0.7 | 0.69 | 0.66 | 0.58 | 0.47 | 0.43 | 0.43 | 0.08 | 0 | 0 | 7.61
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.13 | 0.35 | 0.37 | 0.37 | 0.39 | 0.41 | 0.38 | 0.34 | 0.03 | 0 | 0 | 0 | 0 | 0 | 2.88
INFIL_SCH | fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 9 | 68 | 3545.71
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 15
INFIL_HALF_ON_SCH | fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 16.5 | 118 | 6152.86
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19.5
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0.23 | 0.13 | 0.08 | 6.62 | 44.59 | 2325.05
|  |  | Sat, WinterDesign | 0.11 | 0.1 | 0.08 | 0.06 | 0.06 | 0.06 | 0.07 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0.16 | 0.13 | 6.9
|  |  | Sun, Hol, Other | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07 | 0.1 | 0.12 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.1 | 0.06 | 4.59
Hours_of_operation | on/off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 100 | 5214.29
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | on/off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 100 | 5214.29
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | WD, WinterDesign | 13 | 13 | 13 | 13 | 13 | 13 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 13 | 13 | 13 | 432 | 2992 | 156011.43
|  |  | SummerDesign | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312
|  |  | Sat | 13 | 13 | 13 | 13 | 13 | 13 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 13 | 13 | 440
|  |  | Sun, Hol, Other | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 13 | 13 | 13 | 13 | 13 | 13 | 392
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 33 | 33 | 33 | 33 | 33 | 33 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 33 | 33 | 33 | 657 | 4644 | 242151.43
|  |  | Sat | 33 | 33 | 33 | 33 | 33 | 33 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 33 | 33 | 648
|  |  | WinterDesign | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 792
|  |  | Sun, Hol, Other | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 711
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 100 | 5214.29
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 126984
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Temperature Schedules (oF)
HTGSETP_SCH | Temperature | Through 12/31 | WD, WinterDesign | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 55.4 | 55.4 | 55.4
|  |  | SummerDesign | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4
|  |  | Sat | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 55.4 | 55.4
|  |  | Sun, Hol, Other | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 91.4 | 91.4 | 91.4
|  |  | Sat | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 91.4 | 91.4
|  |  | WinterDesign | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4
|  |  | Sun, Hol, Other | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4