## BuildingSummary
Building Summary Retail new construction version 1.1_3.1
|  | Value | Data Source
Program
| Building Name | Retail
| Available Fuel Types | gas, electricity
| Principal Building Activity | Retail
Form
| Total Floor Area (m2) | 2294 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 1.3
| Number of Floors | 1
Window Fraction (Window to Wall Ratio)
| South | 0.254
| East | 0
| North | 0
| West | 0
| Total | 0.071
| Skylight/TDD Percentage | 0.00%
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | Back, CoreRetail, FrontRetail, PointofSale, FrontEntry
| Floor to Ceiling Height (m) | 6.1
| Roof type | Insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Mass wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1177
| Net Dimensions - Total Area (m2) | 1093.1
| Wall to Skin Ratio | 0.34
Roof
| Construction Type | Insulation entirely above deck | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 2294
| Net Dimensions - Total Area (m2) | 2294
| Roof to Skin Ratio | 0.66
Window Dimensions (m2)
| South | 83.9
| East | 0
| North | 0
| West | 0
| Total Area (m2) | 83.9
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab-on-grade
| Dimensions - Total Area (m2) | 2294
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Internal Mass | 244.23
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 7764.95
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.27 | See Benchmark Technical Report
HVAC
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | Unitary DX | 2003 CBECS
| Fan Control | Constant volume | 2003 CBECS
Service Water Heating
| SWH Type | N/A
| Fuel | N/A
| Thermal Efficiency (%) | N/A
| Temperature Setpoint (ºC ) | N/A
| Water Consumption (L ) | N/A

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Back_Space | Yes | 1 | 379.89 | 2317.33 | 6.1 | 416.17 | 0 | 27.8709 | 13.6303 | 8.608 | 8.07 | 0 |  | 3.8 | 0.6 | 279.7292 |  | 0.37388
Core_Retail | Yes | 1 | 1600.48 | 9762.95 | 6.1 | 356.86 | 0 | 6.1939 | 258.3982 | 18.292 | 3.228 | 0 |  | 3.8 | 0.6 | 1942.2011 |  | 0.2182
Point_of_Sale | Yes | 1 | 150.81 | 919.94 | 6.1 | 189.8 | 38.05 | 6.1939 | 24.3483 | 18.292 | 21.52 | 0 |  | 3.8 | 0.6 | 183.0097 |  | 0.40297
Front_Retail | Yes | 1 | 150.81 | 919.94 | 6.1 | 189.8 | 38.05 | 6.1939 | 24.3483 | 18.292 | 3.228 | 0 |  | 3.8 | 0.6 | 183.0097 |  | 0.40297
Front_Entry | Yes | 1 | 12 | 73.2 | 6.1 | 24.38 | 7.83 | 6.1939 | 1.9374 | 11.836 | 0 | 0 |  | 3.8 | 0.6 | 14.5621 |  | 0.54091
Total Conditioned Zones |  |  | 2293.99 | 13993.36 |  | 1177.01 | 83.93 |  | 322.6626
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7A | 8A
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Weighting Factor
Fabric
Exterior walls
| Construction Type | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall
| R-value (m2·K / W) | 0.38314 | 0.38314 | 0.38314 | 1.1682 | 1.1682 | 1.1682 | 1.1682 | 1.1682 | 1.1682 | 1.1682 | 1.4327 | 1.4327 | 1.692 | 1.692 | 1.9531 | 2.2026
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 3.663
Window
| U-Factor (W / m2·K) | 6.49 | 6.49 | 6.49 | 3.18 | 3.18 | 3.18 | 6.49 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 2.58
| SHGC | 0.25 | 0.25 | 0.25 | 0.262 | 0.262 | 0.262 | 0.391 | 0.402 | 0.402 | 0.402 | 0.402 | 0.402 | 0.402 | 0.402 | 0.501 | 0.504
| Visible transmittance | 0.25 | 0.25 | 0.25 | 0.318 | 0.318 | 0.318 | 0.39 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.49 | 0.49
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade
| R-value (m2·K / W) | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | 43.6411 | 40.6885 | 40.26 | 31.3335 | 17.6126 | 22.892 | 11.4492 | 28.6625 | 21.6263 | 16.0168 | 35.3689 | 26.4454 | 36.6515 | 30.0922 | 34.1115 | 34.8237
| PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | 194.5827 | 193.4224 | 158.4094 | 169.5333 | 110.5724 | 105.9528 | 55.3564 | 156.6659 | 98.8809 | 68.3859 | 144.7075 | 80.4568 | 142.3667 | 76.0522 | 95.7684 | 87.2401
| PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | 26.7993 | 25.2563 | 23.7769 | 23.9307 | 17.3398 | 20.4768 | 15.4726 | 23.7074 | 18.3937 | 17.0299 | 22.6451 | 18.779 | 23.1651 | 18.5747 | 18.2534 | 17.3072
| PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | 22.228 | 23.5341 | 19.9057 | 18.9982 | 12.7281 | 14.4803 | 12.1791 | 20.2986 | 15.2188 | 13.6996 | 19.6525 | 14.5623 | 18.8179 | 15.2598 | 17.0646 | 17.3072
Heating (kW)
| FRONT_ENTRY UNIT HEATER COIL | 1.1964 | 2.2904 | 1.8092 | 1.9066 | 1.0051 | 1.5644 | 1.42 | 2.202 | 1.9185 | 1.7485 | 2.7838 | 2.4319 | 3.0957 | 3.0071 | 3.2225 | 4.0199
| PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | 19.1101 | 38.3119 | 31.1589 | 33.0182 | 17.8173 | 27.8402 | 22.0283 | 38.4908 | 33.2144 | 30.5963 | 47.6413 | 41.3675 | 52.3814 | 50.6841 | 53.9379 | 69.1371
| PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | 92.9463 | 122.7975 | 103.523 | 133.5186 | 96.6681 | 111.911 | 106.8502 | 156.281 | 130.0446 | 127.425 | 198.3176 | 167.1524 | 222.3818 | 211.2938 | 232.0585 | 300.7081
| PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | 11.0256 | 21.2967 | 16.8664 | 19.2306 | 10.2477 | 15.7768 | 13.5792 | 22.31 | 18.9651 | 17.7359 | 28.0453 | 24.0483 | 31.1096 | 29.8416 | 32.2791 | 40.7568
| PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | 11.0279 | 21.2967 | 16.8574 | 19.2307 | 10.2497 | 15.7761 | 13.5809 | 22.3109 | 18.9651 | 17.736 | 28.046 | 24.047 | 31.1106 | 29.8434 | 32.2797 | 40.7568
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | 3.25 | 3.3 | 3.47 | 3.51 | 4.03 | 3.79 | 4.05 | 3.52 | 3.79 | 4.04 | 3.46 | 3.75 | 3.49 | 3.75 | 3.58 | 3.74
| PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | 3.51 | 3.51 | 3.78 | 3.51 | 3.95 | 4.1 | 3.47 | 3.51 | 4.18 | 4.32 | 3.51 | 4.18 | 3.51 | 4.18 | 3.64 | 4.18
| PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | 3.53 | 3.59 | 3.75 | 3.59 | 4.04 | 3.79 | 4.03 | 3.57 | 4.03 | 4.03 | 3.55 | 4.03 | 3.52 | 4.03 | 3.93 | 4.04
| PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | 3.45 | 3.52 | 3.79 | 3.68 | 4.03 | 4.03 | 4.04 | 3.51 | 4.03 | 4.02 | 3.51 | 4.03 | 3.76 | 4.03 | 3.85 | 4.04
Heating Efficiency (%)
| FRONT_ENTRY UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78
| PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
HVAC Control - Economizer
| PSZ-AC:1_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ-AC:2_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC:3_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC:4_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
Fan Max Flow Rate (m3/s )
| FRONT_ENTRY UNIT HEATERFAN | 0.05 | 0.1 | 0.08 | 0.08 | 0.04 | 0.07 | 0.06 | 0.09 | 0.1 | 0.08 | 0.12 | 0.13 | 0.14 | 0.15 | 0.15 | 0.18
| PSZ-AC:1_UNITARY_PACKAGE_FAN | 1.94 | 1.97 | 2.43 | 1.44 | 1.06 | 1.38 | 0.69 | 1.28 | 1.31 | 0.97 | 1.5 | 1.6 | 1.64 | 1.82 | 1.72 | 2.1
| PSZ-AC:2_UNITARY_PACKAGE_FAN | 7.84 | 7.79 | 7.98 | 6.83 | 6.02 | 6.19 | 3.34 | 6.31 | 5.97 | 4.13 | 5.83 | 4.86 | 5.73 | 4.59 | 4.31 | 5.27
| PSZ-AC:3_UNITARY_PACKAGE_FAN | 1.21 | 1.24 | 1.44 | 1.17 | 1.05 | 1.24 | 0.93 | 1.13 | 1.11 | 1.03 | 1.06 | 1.13 | 1.04 | 1.12 | 1.01 | 1.05
| PSZ-AC:4_UNITARY_PACKAGE_FAN | 0.9 | 1.05 | 1.2 | 0.8 | 0.77 | 0.87 | 0.74 | 0.89 | 0.92 | 0.82 | 0.87 | 0.88 | 0.87 | 0.92 | 0.88 | 1.05
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.08775 | 0.12788 | 0.11007 | 0.10362 | 0.13319 | 0.10111 | 0.1507 | 0.078632 | 0.037722 | 0.07232 | 0.053201 | 0.037762 | 0.063339 | 0.076648 | 0.061509 | 0.098781
| Total Cost ($/m2) | 13.2 | 16.99 | 14.65 | 11.73 | 13.82 | 11.58 | 14.19 | 8.55 | 3.99 | 6.94 | 5.58 | 3.8 | 6.6 | 7.57 | 6.04 | 9.79
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011407 | 0.0080481 | 0.0080541 | 0.0094321 | 0.0087625 | 0.0075876 | 0.0086007 | 0.0096454 | 0.0068539 | 0.0084327 | 0.0082702 | 0.006884 | 0.0079055 | 0.008031 | 0.0078918 | 0.0041097
| Total Cost ($/m2) | 0.01 | 0.35 | 0.33 | 0.57 | 0.15 | 0.43 | 0.51 | 1.12 | 0.67 | 0.9 | 1.35 | 1.01 | 1.92 | 1.83 | 2.68 | 2.65
Total Utility Costs
| Cost Intensity ($/m2) | 13.21 | 17.34 | 14.98 | 12.3 | 13.97 | 12.01 | 14.7 | 9.67 | 4.65 | 7.84 | 6.93 | 4.81 | 8.52 | 9.4 | 8.72 | 12.44
Energy - End Uses
Electricity (kWh)
| Heating | 5.5556 | 375 | 188.8889 | 394.4444 | 77.7778 | 202.7778 | 411.1111 | 750 | 455.5556 | 763.8889 | 1180.5556 | 850 | 1600 | 1413.8889 | 2025 | 3691.6667
| Cooling | 109519.4444 | 75238.8889 | 70938.8889 | 38694.4444 | 15247.2222 | 36219.4444 | 3816.6667 | 29472.2222 | 20136.1111 | 4852.7778 | 20319.4444 | 11552.7778 | 17463.8889 | 7144.4444 | 5355.5556 | 1708.3333
| Interior Lighting | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667
| Exterior Lighting | 13844.4444 | 13838.8889 | 13836.1111 | 13833.3333 | 13825 | 13819.4444 | 13827.7778 | 13819.4444 | 13825 | 13797.2222 | 13822.2222 | 13813.8889 | 13813.8889 | 13808.3333 | 13802.7778 | 13716.6667
| Interior Equipment | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 27533.3333 | 21066.6667 | 26150 | 12577.7778 | 14736.1111 | 18369.4444 | 3686.1111 | 11319.4444 | 13755.5556 | 6533.3333 | 11080.5556 | 10597.2222 | 11983.3333 | 9961.1111 | 10019.4444 | 13963.8889
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 345094.4444 | 304708.3333 | 305308.3333 | 259694.4444 | 238077.7778 | 262805.5556 | 215936.1111 | 249552.7778 | 242363.8889 | 220141.6667 | 240597.2222 | 231005.5556 | 239055.5556 | 226522.2222 | 225397.2222 | 227275
Gas (MJ)
| Heating | 1080 | 99980 | 92720 | 139690 | 39160 | 130000 | 137030 | 265930 | 223080 | 243800 | 375260 | 336260 | 556280 | 523610 | 777760 | 1481790
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1080 | 99980 | 92720 | 139690 | 39160 | 130000 | 137030 | 265930 | 223080 | 243800 | 375260 | 336260 | 556280 | 523610 | 777760 | 1481790
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 1243420 | 1196930 | 1191820 | 1074590 | 896240 | 1076100 | 914400 | 1164320 | 1095590 | 1036300 | 1241410 | 1167880 | 1416870 | 1339090 | 1589180 | 2299980
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0.0087184 | 0.58849 | 0.29643 | 0.61901 | 0.12206 | 0.31822 | 0.64516 | 1.177 | 0.71491 | 1.1988 | 1.8527 | 1.3339 | 2.5109 | 2.2188 | 3.1779 | 5.7934
| Cooling (elec) | 171.8708 | 118.0737 | 111.3257 | 60.7239 | 23.9277 | 56.8398 | 5.9896 | 46.2513 | 31.6 | 7.6156 | 31.8877 | 18.13 | 27.4064 | 11.2119 | 8.4046 | 2.6809
| Interior Lighting (elec) | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829
| Exterior Lighting (elec) | 21.7263 | 21.7176 | 21.7133 | 21.7089 | 21.6958 | 21.6871 | 21.7002 | 21.6871 | 21.6958 | 21.6522 | 21.6915 | 21.6784 | 21.6784 | 21.6697 | 21.6609 | 21.5258
| Interior Equipment (elec) | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 43.2086 | 33.0603 | 41.0377 | 19.7385 | 23.1256 | 28.8275 | 5.7847 | 17.7638 | 21.5868 | 10.2529 | 17.3889 | 16.6304 | 18.8057 | 15.6322 | 15.7237 | 21.9138
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 541.563 | 478.1843 | 479.1259 | 407.5432 | 373.6198 | 412.4255 | 338.8724 | 391.6277 | 380.346 | 345.4723 | 377.5736 | 362.5212 | 375.1542 | 355.4854 | 353.7199 | 356.6668
Gas (MJ/m2)
| Heating (gas) | 0.4708 | 43.5835 | 40.4187 | 60.8939 | 17.0707 | 56.6698 | 59.7343 | 115.9247 | 97.2454 | 106.2777 | 163.584 | 146.583 | 242.4945 | 228.253 | 339.0425 | 645.9444
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0.4708 | 43.5835 | 40.4187 | 60.8939 | 17.0707 | 56.6698 | 59.7343 | 115.9247 | 97.2454 | 106.2777 | 163.584 | 146.583 | 242.4945 | 228.253 | 339.0425 | 645.9444
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 542.0337 | 521.7677 | 519.5402 | 468.4371 | 390.6905 | 469.0953 | 398.6068 | 507.5523 | 477.5914 | 451.7456 | 541.1575 | 509.1042 | 617.6444 | 583.7384 | 692.758 | 1002.6112
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 81.3475 | 64.0086 | 63.3938 | 52.4779 | 58.2997 | 49.9807 | 49.124 | 52.2045 | 49.7892 | 48.9448 | 50.8768 | 50.4586 | 51.9267 | 51.8878 | 51.6732 | 57.2615
| Feb | 85.2863 | 65.683 | 63.5512 | 54.0998 | 59.5661 | 58.4937 | 52.1431 | 49.482 | 58.2262 | 48.8134 | 49.1229 | 50.5654 | 50.553 | 50.655 | 51.2993 | 56.6842
| Mar | 86.2062 | 72.5381 | 73.2353 | 57.0018 | 59.205 | 58.9127 | 49.2792 | 52.4265 | 57.8579 | 55.2286 | 48.6495 | 56.2697 | 49.3581 | 49.3412 | 49.7238 | 51.4606
| Apr | 96.1359 | 93.2493 | 80.5141 | 68.9782 | 60.0016 | 71.5656 | 54.2073 | 57.3125 | 59.2201 | 55.4559 | 58.2959 | 56.4621 | 56.7008 | 49.2615 | 48.3509 | 49.0332
| May | 101.8272 | 102.3272 | 105.2914 | 81.912 | 63.2297 | 85.6883 | 54.4999 | 68.9502 | 67.5106 | 56.3172 | 63.7917 | 60.8769 | 80.6216 | 55.9634 | 55.7326 | 51.6925
| Jun | 111.3103 | 104.3855 | 132.8786 | 91.1987 | 64.2784 | 105.0505 | 57.1569 | 96.8401 | 82.2164 | 60.8299 | 88.4948 | 72.5294 | 89.6355 | 75.0491 | 66.268 | 58.0235
| Jul | 108.1437 | 112.3358 | 122.2194 | 102.6053 | 71.4771 | 103.3508 | 62.6414 | 103.0379 | 87.6054 | 68.3497 | 96.1077 | 82.2013 | 96.5175 | 78.9056 | 81.2995 | 59.2303
| Aug | 107.4193 | 111.8361 | 127.9708 | 95.9539 | 79.1153 | 101.9078 | 57.1544 | 107.6712 | 85.037 | 66.2731 | 95.404 | 81.8394 | 89.4285 | 70.909 | 77.9864 | 58.577
| Sep | 104.0111 | 110.5114 | 110.5971 | 85.1798 | 74.9716 | 98.1451 | 72.9421 | 83.9987 | 73.6444 | 79.2337 | 74.6998 | 71.6146 | 69.02 | 62.1181 | 60.9112 | 47.6043
| Oct | 100.8971 | 90.5786 | 82.7446 | 68.894 | 66.3887 | 72.5406 | 55.0748 | 66.0219 | 59.8988 | 54.7935 | 59.0911 | 58.4638 | 58.0591 | 52.7036 | 54.6042 | 52.7472
| Nov | 88.789 | 73.5092 | 67.1262 | 54.9772 | 62.1174 | 61.6408 | 50.464 | 59.7752 | 55.3709 | 51.3421 | 54.7089 | 50.9608 | 49.8832 | 48.8067 | 50.3019 | 53.9092
| Dec | 81.6122 | 65.0279 | 65.8314 | 50.0731 | 60.7258 | 50.2156 | 49.1415 | 49.8503 | 49.6584 | 49.0509 | 49.6001 | 50.6271 | 50.8544 | 51.9761 | 50.8832 | 56.3359
Time of Peak Electrical Demand
| Jan | 23-JAN-15:00 | 21-JAN-17:49 | 30-JAN-15:50 | 23-JAN-17:00 | 27-JAN-15:09 | 18-JAN-16:49 | 17-JAN-17:19 | 17-JAN-09:09 | 26-JAN-17:30 | 09-JAN-17:30 | 27-JAN-09:09 | 06-JAN-09:09 | 06-JAN-09:09 | 06-JAN-09:09 | 09-JAN-17:00 | 13-JAN-09:09
| Feb | 22-FEB-15:00 | 23-FEB-16:00 | 08-FEB-17:10 | 18-FEB-16:00 | 13-FEB-15:20 | 27-FEB-15:39 | 15-FEB-15:20 | 21-FEB-09:09 | 14-FEB-16:40 | 21-FEB-17:40 | 03-FEB-17:00 | 15-FEB-09:09 | 04-FEB-10:09 | 27-FEB-09:09 | 01-FEB-17:00 | 03-FEB-09:09
| Mar | 13-MAR-14:00 | 25-MAR-15:00 | 17-MAR-15:00 | 28-MAR-15:00 | 29-MAR-14:00 | 21-MAR-15:39 | 01-MAR-17:00 | 25-MAR-15:00 | 02-MAR-16:00 | 29-MAR-15:39 | 07-MAR-17:00 | 27-MAR-15:09 | 01-MAR-17:00 | 03-MAR-09:09 | 09-MAR-17:00 | 14-MAR-08:09
| Apr | 15-APR-15:00 | 29-APR-15:00 | 01-APR-16:00 | 15-APR-15:00 | 13-APR-15:39 | 21-APR-15:00 | 29-APR-14:00 | 05-APR-15:00 | 08-APR-15:50 | 29-APR-13:00 | 28-APR-14:30 | 27-APR-13:30 | 14-APR-16:00 | 14-APR-15:50 | 03-APR-08:09 | 03-APR-08:09
| May | 24-MAY-14:00 | 18-MAY-15:00 | 27-MAY-16:00 | 15-MAY-14:00 | 30-MAY-14:00 | 31-MAY-15:00 | 17-MAY-14:09 | 15-MAY-15:00 | 31-MAY-15:00 | 04-MAY-14:00 | 30-MAY-15:00 | 23-MAY-15:00 | 27-MAY-14:00 | 15-MAY-15:30 | 27-MAY-14:20 | 25-MAY-14:39
| Jun | 27-JUN-14:00 | 30-JUN-14:00 | 28-JUN-15:00 | 19-JUN-14:00 | 30-JUN-14:00 | 27-JUN-15:00 | 16-JUN-14:00 | 30-JUN-14:00 | 29-JUN-14:00 | 28-JUN-14:00 | 08-JUN-12:00 | 27-JUN-15:00 | 29-JUN-14:00 | 30-JUN-15:00 | 14-JUN-14:00 | 09-JUN-14:50
| Jul | 13-JUL-14:00 | 05-JUL-15:00 | 11-JUL-15:00 | 03-JUL-14:00 | 24-JUL-14:00 | 24-JUL-15:00 | 03-JUL-14:20 | 25-JUL-14:39 | 31-JUL-14:00 | 24-JUL-14:00 | 13-JUL-14:00 | 17-JUL-15:00 | 15-JUL-14:00 | 21-JUL-15:00 | 08-JUL-15:30 | 29-JUL-15:00
| Aug | 21-AUG-14:00 | 31-AUG-15:00 | 01-AUG-16:00 | 17-AUG-14:00 | 09-AUG-14:00 | 04-AUG-15:00 | 26-AUG-14:39 | 09-AUG-14:00 | 01-AUG-14:00 | 07-AUG-14:00 | 04-AUG-15:00 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-15:00 | 12-AUG-14:00 | 12-AUG-14:50
| Sep | 09-SEP-15:00 | 16-SEP-15:20 | 09-SEP-15:00 | 11-SEP-14:09 | 25-SEP-14:00 | 01-SEP-14:00 | 28-SEP-14:00 | 09-SEP-15:30 | 02-SEP-15:50 | 02-SEP-15:00 | 05-SEP-14:00 | 02-SEP-15:50 | 14-SEP-14:00 | 02-SEP-15:00 | 07-SEP-14:00 | 09-SEP-15:50
| Oct | 06-OCT-15:00 | 06-OCT-15:00 | 14-OCT-15:00 | 21-OCT-15:00 | 05-OCT-14:00 | 03-OCT-15:00 | 13-OCT-15:00 | 12-OCT-15:00 | 16-OCT-15:39 | 17-OCT-13:50 | 28-OCT-13:20 | 05-OCT-14:00 | 07-OCT-15:39 | 05-OCT-15:09 | 07-OCT-15:30 | 27-OCT-08:09
| Nov | 07-NOV-15:50 | 03-NOV-15:00 | 20-NOV-17:49 | 22-NOV-15:00 | 08-NOV-16:00 | 10-NOV-16:00 | 14-NOV-16:00 | 04-NOV-16:00 | 10-NOV-15:20 | 04-NOV-16:49 | 02-NOV-16:49 | 04-NOV-16:00 | 02-NOV-16:00 | 27-NOV-17:00 | 24-NOV-17:00 | 09-NOV-09:09
| Dec | 15-DEC-15:00 | 02-DEC-16:19 | 09-DEC-17:40 | 02-DEC-17:30 | 18-DEC-16:49 | 06-DEC-16:30 | 07-DEC-16:49 | 21-DEC-09:09 | 05-DEC-16:49 | 13-DEC-17:00 | 14-DEC-17:00 | 11-DEC-09:09 | 30-DEC-17:00 | 11-DEC-09:09 | 30-DEC-17:00 | 29-DEC-09:09
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emissions
| Carbon Equivalent (kg) | 94661.7656 | 103442.098 | 93836.6125 | 82514.3162 | 28529.296 | 90982.1964 | 27706.5283 | 72138.9262 | 103027.9388 | 20430.063 | 135041.3307 | 100428.9892 | 91857.9182 | 92221.9146 | 91176.6278 | 90672.7825
| CO2 (kg) | 219205.5499 | 260250.7941 | 221574.0515 | 188835.2813 | 76323.3119 | 216713.0149 | 74513.8151 | 164874.9813 | 242314.2125 | 50789.6493 | 315514.8549 | 237399.4531 | 217624.8493 | 219815.1786 | 218385.8298 | 237402.3364
| NOX (kg) | 386.5441 | 339.9583 | 370.7172 | 357.1944 | 65.4218 | 350.4356 | 64.139 | 314.5288 | 415.3092 | 72.729 | 556.6689 | 401.6937 | 370.5506 | 366.5347 | 361.3586 | 270.79
| SO2 (kg) | 1477.147 | 1453.4916 | 1227.7254 | 911.5632 | 692.7882 | 1445.68 | 628.383 | 911.0435 | 1058.4146 | 170.2168 | 1621.5347 | 1008.8457 | 564.3564 | 604.982 | 532.1798 | 1157.3134
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0067 | 0.0041 | 0.0033 | 0.0033 | 0.0003 | 0.0027 | 0.0003 | 0.0037 | 0.0041 | 0.0007 | 0.0049 | 0.004 | 0.0042 | 0.0042 | 0.004 | 0.0041
| Water Environmental Factors (m3) | 182.8171 | 495.7983 | 9068.96 | 1621.42 | 4180.11 | 7209.83 | 3791.34 | 56.6582 | 1100.53 | 2249.14 | 373.2725 | 1048.95 | 370.8791 | 14348.9 | 349.6889 | 232.2014

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1243.42 | 542.03 | 542.03
Net Site Energy | 1243.42 | 542.03 | 542.03
Total Source Energy | 4122.03 | 1796.88 | 1796.88
Net Source Energy | 4122.03 | 1796.88 | 1796.88
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0.02 | 1.08 | 0 | 0 | 0 | 0
Cooling | 394.27 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 49.84 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 99.12 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1242.34 | 1.08 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 8.61 | 27.86 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 18.29 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 21.52
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 11.84 | 6.19 | 0
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 379.89 | 90 | 180
BACK_SPACE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 379.89 | 90 | 0
CORE_RETAIL_WALL_WEST_2 | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 178.43 | 270 | 90 | W
CORE_RETAIL_WALL_EAST_2 | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 178.43 | 90 | 90 | E
CORE_RETAIL_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1600.48 | 180 | 0
POINT_OF_SALE_WALL_SOUTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 180 | 0
FRONT_RETAIL_WALLL_EAST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 36.58 | 90 | 90 | E
FRONT_RETAIL_WALL_SOUTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 153.22 | 180 | 90 | S
FRONT_RETAIL_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 90 | 0
FRONT_ENTRY_WALL_SOUTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 12 | 180 | 180
FRONT_ENTRY_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
POINT_OF_SALE_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 38.05 | 38.05 | 6.49 | 0.25 | 0.25 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 38.05 | 38.05 | 6.49 | 0.25 | 0.25 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
FRONT_ENTRY_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 7.83 | 7.83 | 6.49 | 0.25 | 0.25 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 6.49 | 0.25 | 0.25
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 6.49 | 0.25 | 0.25
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 43641.14 | 30645.73 | 12995.41 | 0.7 | 3.25
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 194582.7 | 131554.1 | 63028.6 | 0.68 | 3.51
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 26799.33 | 18915.55 | 7883.79 | 0.71 | 3.53
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 22227.96 | 15027.95 | 7200.01 | 0.68 | 3.45
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 1196.4 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 19110.12 | 0.8
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 92946.29 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11025.57 | 0.8
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11027.89 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.76 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.94 | 2126.95 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 7.84 | 14699.97 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.21 | 1378.61 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.9 | 1019.72 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 15024.957 | 26.4548 | 100.9325 | 0 | 0.0005 | 12491.7493 | 6484.3673
February | 14166.9248 | 24.9821 | 95.4681 | 0 | 0.0004 | 11815.4756 | 6117.8764
March | 16633.385 | 29.3329 | 112.1007 | 0 | 0.0005 | 13873.9904 | 7183.1463
April | 17579.7152 | 31.0037 | 118.4937 | 0 | 0.0005 | 14665.2097 | 7592.0134
May | 19927.4251 | 35.1441 | 134.3181 | 0 | 0.0006 | 16623.6975 | 8605.9004
June | 20741.9063 | 36.5805 | 139.808 | 0 | 0.0006 | 17303.1475 | 8957.644
July | 21884.7779 | 38.5961 | 147.5113 | 0 | 0.0007 | 18256.5448 | 9451.2069
August | 22418.7313 | 39.5378 | 151.1104 | 0 | 0.0007 | 18701.9751 | 9681.8012
September | 20014.7896 | 35.2982 | 134.9069 | 0 | 0.0006 | 16696.5781 | 8643.6298
October | 19182.5132 | 33.8304 | 129.2971 | 0 | 0.0006 | 16002.2831 | 8284.2012
November | 16447.8817 | 29.0076 | 110.8647 | 0 | 0.0005 | 13721.0206 | 7103.2173
December | 15182.5427 | 26.776 | 102.3355 | 0 | 0.0005 | 12665.4218 | 6556.7615
Annual Sum or Average | 219205.5499 | 386.5441 | 1477.147 | 0 | 0.0067 | 182817.0933 | 94661.7656
Minimum of Months | 14166.9248 | 24.9821 | 95.4681 | 0 | 0.0004 | 11815.4756 | 6117.8764
Maximum of Months | 22418.7313 | 39.5378 | 151.1104 | 0 | 0.0007 | 18701.9751 | 9681.8012
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 84888400000 | 81347.541 | 23-JAN-15:00 | 34382.155 | 10771.038 | 7358.131 | 0 | 28836.217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 80292700000 | 85286.29 | 22-FEB-15:00 | 34382.155 | 10771.038 | 8057.797 | 0 | 32075.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 94281500000 | 86206.243 | 13-MAR-14:00 | 34382.155 | 10771.038 | 8169.806 | 0 | 32883.244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 99658200000 | 96135.918 | 15-APR-15:00 | 34382.155 | 10771.038 | 10078.745 | 0 | 40903.979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 112967000000 | 101827.204 | 24-MAY-14:00 | 34382.155 | 10771.038 | 10816.517 | 0 | 45857.494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 117585000000 | 111310.257 | 27-JUN-14:00 | 34382.155 | 10771.038 | 12752.566 | 0 | 53404.498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 124063000000 | 108143.727 | 13-JUL-14:00 | 34382.155 | 10771.038 | 12161.752 | 0 | 50828.781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 127090000000 | 107419.276 | 21-AUG-14:00 | 34382.155 | 10771.038 | 11823.83 | 0 | 50442.253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 113463000000 | 104011.051 | 09-SEP-15:00 | 34382.155 | 10771.038 | 11394.626 | 0 | 47463.233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 108744000000 | 100897.059 | 06-OCT-15:00 | 34382.155 | 10771.038 | 10879.296 | 0 | 44864.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 93242000000 | 88789.001 | 07-NOV-15:50 | 34382.155 | 10771.038 | 8699.35 | 0 | 34936.458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 86068600000 | 81612.178 | 15-DEC-15:00 | 34382.155 | 10771.038 | 7409.815 | 0 | 29049.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1242340000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 80292700000 | 81347.541 |  | 34382.155 | 10771.038 | 7358.131 | 0 | 28836.217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 127090000000 | 111310.257 |  | 34382.155 | 10771.038 | 12752.566 | 0 | 53404.498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 30282.11 | 12.32 | 0 | 30294.42
Cost per Total Building Area ($/m2) | 13.2 | 0.01 | 0 | 13.21
Cost per Net Conditioned Building Area ($/m2) | 13.2 | 0.01 | 0 | 13.21

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1196.93 | 521.77 | 521.77
Net Site Energy | 1196.93 | 521.77 | 521.77
Total Source Energy | 109.18 | 47.59 | 47.59
Net Source Energy | 109.18 | 47.59 | 47.59
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 1.35 | 99.98 | 0 | 0 | 0 | 0
Cooling | 270.86 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 49.82 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 75.84 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1096.95 | 99.98 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 8.61 | 27.86 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 18.29 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 21.52
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 11.84 | 6.19 | 0
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 379.89 | 90 | 180
BACK_SPACE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 379.89 | 90 | 0
CORE_RETAIL_WALL_WEST_2 | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 178.43 | 270 | 90 | W
CORE_RETAIL_WALL_EAST_2 | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 178.43 | 90 | 90 | E
CORE_RETAIL_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1600.48 | 180 | 0
POINT_OF_SALE_WALL_SOUTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 180 | 0
FRONT_RETAIL_WALLL_EAST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 36.58 | 90 | 90 | E
FRONT_RETAIL_WALL_SOUTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 153.22 | 180 | 90 | S
FRONT_RETAIL_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 90 | 0
FRONT_ENTRY_WALL_SOUTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 12 | 180 | 180
FRONT_ENTRY_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
POINT_OF_SALE_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 38.05 | 38.05 | 6.49 | 0.25 | 0.25 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 38.05 | 38.05 | 6.49 | 0.25 | 0.25 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
FRONT_ENTRY_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 7.83 | 7.83 | 6.49 | 0.25 | 0.25 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 6.49 | 0.25 | 0.25
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 6.49 | 0.25 | 0.25
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 40688.46 | 29537.5 | 11150.96 | 0.73 | 3.3
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 193422.4 | 130769.64 | 62652.76 | 0.68 | 3.51
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 25256.33 | 18412.32 | 6844.01 | 0.73 | 3.59
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 23534.1 | 16529.05 | 7005.05 | 0.7 | 3.52
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 2290.37 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 38311.95 | 0.8
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 122797.52 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21296.68 | 0.8
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21296.68 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.1 | 9.15 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.97 | 2156.48 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 7.79 | 14612.31 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.24 | 1408.9 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.05 | 1195.32 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 17784.1192 | 22.6852 | 91.6813 | 0 | 0.0003 | 31270.8662 | 6998.3326
February | 15970.2089 | 20.3911 | 82.6057 | 0 | 0.0002 | 28175.4221 | 6287.0657
March | 17344.0235 | 22.6436 | 96.6926 | 0 | 0.0003 | 32982.6017 | 6892.1495
April | 19070.7049 | 25.0618 | 108.6138 | 0 | 0.0003 | 37049.7447 | 7599.4181
May | 23814.0601 | 31.3013 | 135.7137 | 0 | 0.0004 | 46293.9536 | 9490.3634
June | 27182.6752 | 35.7291 | 154.912 | 0 | 0.0004 | 52842.7698 | 10832.83
July | 29418.7441 | 38.6683 | 167.6552 | 0 | 0.0005 | 57189.6589 | 11723.9474
August | 29114.1043 | 38.2678 | 165.9191 | 0 | 0.0005 | 56597.4431 | 11602.5424
September | 24854.6373 | 32.6691 | 141.6447 | 0 | 0.0004 | 48317.0942 | 9905.0612
October | 21335.3274 | 28.042 | 121.5701 | 0 | 0.0003 | 41469.3547 | 8502.3787
November | 17146.6778 | 22.4567 | 96.5828 | 0 | 0.0003 | 32945.4716 | 6822.8438
December | 17215.5115 | 22.0421 | 89.9005 | 0 | 0.0003 | 30663.87 | 6785.1653
Annual Sum or Average | 260250.7941 | 339.9583 | 1453.4916 | 0 | 0.0041 | 495798.2506 | 103442.098
Minimum of Months | 15970.2089 | 20.3911 | 82.6057 | 0 | 0.0002 | 28175.4221 | 6287.0657
Maximum of Months | 29418.7441 | 38.6683 | 167.6552 | 0 | 0.0005 | 57189.6589 | 11723.9474
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 69186900000 | 64008.61 | 21-JAN-17:49 | 34382.155 | 10771.038 | 3347.491 | 0 | 12340.642 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 62338200000 | 65682.995 | 23-FEB-16:00 | 34382.155 | 10771.038 | 4231.305 | 0 | 16298.497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 72974100000 | 72538.129 | 25-MAR-15:00 | 34382.155 | 10771.038 | 5643.964 | 0 | 21740.972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 81972600000 | 93249.305 | 29-APR-15:00 | 34382.155 | 10771.038 | 9686.351 | 0 | 38409.761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 102425000000 | 102327.163 | 18-MAY-15:00 | 34382.155 | 10771.038 | 11140.291 | 0 | 46033.679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 116915000000 | 104385.521 | 30-JUN-14:00 | 34382.155 | 10771.038 | 11429.54 | 0 | 47802.788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 126532000000 | 112335.76 | 05-JUL-15:00 | 34382.155 | 10771.038 | 12852.125 | 0 | 54330.442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 125222000000 | 111836.107 | 31-AUG-15:00 | 34382.155 | 10771.038 | 12745.039 | 0 | 53937.875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 106902000000 | 110511.392 | 16-SEP-15:20 | 34382.155 | 10771.038 | 12936.907 | 0 | 52421.292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 91751000000 | 90578.569 | 06-OCT-15:00 | 34382.155 | 10771.038 | 8975.003 | 0 | 36450.374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 72891900000 | 73509.179 | 03-NOV-15:00 | 34382.155 | 10771.038 | 5889.287 | 0 | 22466.698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 67843900000 | 65027.882 | 02-DEC-16:19 | 34382.155 | 10771.038 | 4209.296 | 0 | 15665.394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1096950000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 62338200000 | 64008.61 |  | 34382.155 | 10771.038 | 3347.491 | 0 | 12340.642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 126532000000 | 112335.76 |  | 34382.155 | 10771.038 | 12936.907 | 0 | 54330.442 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 38967.61 | 804.65 | 0 | 39772.25
Cost per Total Building Area ($/m2) | 16.99 | 0.35 | 0 | 17.34
Cost per Net Conditioned Building Area ($/m2) | 16.99 | 0.35 | 0 | 17.34

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1191.82 | 519.54 | 519.54
Net Site Energy | 1191.82 | 519.54 | 519.54
Total Source Energy | 3577.72 | 1559.6 | 1559.6
Net Source Energy | 3577.72 | 1559.6 | 1559.6
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0.68 | 92.72 | 0 | 0 | 0 | 0
Cooling | 255.38 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 49.81 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 94.14 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1099.11 | 92.72 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 8.61 | 27.86 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 18.29 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 21.52
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 11.84 | 6.19 | 0
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 379.89 | 90 | 180
BACK_SPACE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 379.89 | 90 | 0
CORE_RETAIL_WALL_WEST_2 | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 178.43 | 270 | 90 | W
CORE_RETAIL_WALL_EAST_2 | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 178.43 | 90 | 90 | E
CORE_RETAIL_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1600.48 | 180 | 0
POINT_OF_SALE_WALL_SOUTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 180 | 0
FRONT_RETAIL_WALLL_EAST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 36.58 | 90 | 90 | E
FRONT_RETAIL_WALL_SOUTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 153.22 | 180 | 90 | S
FRONT_RETAIL_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 90 | 0
FRONT_ENTRY_WALL_SOUTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 12 | 180 | 180
FRONT_ENTRY_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
POINT_OF_SALE_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 38.05 | 38.05 | 6.49 | 0.25 | 0.25 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 38.05 | 38.05 | 6.49 | 0.25 | 0.25 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
FRONT_ENTRY_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 7.83 | 7.83 | 6.49 | 0.25 | 0.25 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 6.49 | 0.25 | 0.25
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 6.49 | 0.25 | 0.25
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 40260.03 | 32153.89 | 8106.15 | 0.8 | 3.47
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 158409.43 | 116837.63 | 41571.8 | 0.74 | 3.78
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 23776.92 | 18989.56 | 4787.36 | 0.8 | 3.75
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19905.66 | 15897.76 | 4007.9 | 0.8 | 3.79
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 1809.15 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 31158.93 | 0.8
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 103522.96 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 16866.41 | 0.8
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 16857.41 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.08 | 7.5 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.43 | 2659.82 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.6 | 1109.65 | 7.98 | 14742.63 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.44 | 1570.85 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.2 | 1369.88 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 14820.2102 | 23.9148 | 75.7443 | 0 | 0.0002 | 559463.8477 | 6187.2672
February | 13286.2825 | 21.5416 | 68.643 | 0 | 0.0002 | 507018.1696 | 5557.1932
March | 15226.281 | 25.5624 | 84.9987 | 0 | 0.0002 | 627872.986 | 6457.1512
April | 16315.8413 | 27.5753 | 92.4098 | 0 | 0.0003 | 682626.1249 | 6937.7845
May | 19551.8661 | 33.0458 | 110.7476 | 0 | 0.0003 | 818087.1595 | 8313.9346
June | 24062.7238 | 40.6699 | 136.2985 | 0 | 0.0004 | 1006830 | 10232.0623
July | 25325.2775 | 42.8038 | 143.45 | 0 | 0.0004 | 1059660 | 10768.9312
August | 25175.3527 | 42.5504 | 142.6008 | 0 | 0.0004 | 1053380 | 10705.1795
September | 21529.3548 | 36.3881 | 121.9487 | 0 | 0.0003 | 900829.0357 | 9154.8115
October | 17106.0633 | 28.912 | 96.8936 | 0 | 0.0003 | 715748.1121 | 7273.9153
November | 13907.9762 | 23.3523 | 77.6621 | 0 | 0.0002 | 573678.3054 | 5898.4014
December | 15266.8221 | 24.4007 | 76.3284 | 0 | 0.0002 | 563765.6903 | 6349.9805
Annual Sum or Average | 221574.0515 | 370.7172 | 1227.7254 | 0 | 0.0033 | 9068960 | 93836.6125
Minimum of Months | 13286.2825 | 21.5416 | 68.643 | 0 | 0.0002 | 507018.1696 | 5557.1932
Maximum of Months | 25325.2775 | 42.8038 | 143.45 | 0 | 0.0004 | 1059660 | 10768.9312
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 67803800000 | 63393.763 | 30-JAN-15:50 | 34382.155 | 10771.038 | 14864.56 | 0 | 3376.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 61447600000 | 63551.165 | 08-FEB-17:10 | 34382.155 | 10771.038 | 15482.791 | 0 | 2915.181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 76094500000 | 73235.268 | 17-MAR-15:00 | 34382.155 | 10771.038 | 6927.15 | 0 | 21154.925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 82730300000 | 80514.074 | 01-APR-16:00 | 34382.155 | 10771.038 | 8585.567 | 0 | 26775.315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 99147400000 | 105291.351 | 27-MAY-16:00 | 34382.155 | 10771.038 | 13895.289 | 0 | 46242.869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 122022000000 | 132878.595 | 28-JUN-15:00 | 34382.155 | 10771.038 | 19103.161 | 0 | 68622.241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 128424000000 | 122219.392 | 11-JUL-15:00 | 34382.155 | 10771.038 | 16699.537 | 0 | 60366.662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 127664000000 | 127970.817 | 01-AUG-16:00 | 34382.155 | 10771.038 | 17992.229 | 0 | 64825.395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 109175000000 | 110597.135 | 09-SEP-15:00 | 34382.155 | 10771.038 | 14691.925 | 0 | 50752.017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 86744500000 | 82744.568 | 14-OCT-15:00 | 34382.155 | 10771.038 | 9214.362 | 0 | 28377.012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 69526500000 | 67126.179 | 20-NOV-17:49 | 34382.155 | 10771.038 | 15136.339 | 0 | 3669.362 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 68325100000 | 65831.412 | 09-DEC-17:40 | 34382.155 | 10771.038 | 14385.358 | 0 | 3125.576 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1099110000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 61447600000 | 63393.763 |  | 34382.155 | 10771.038 | 6927.15 | 0 | 2915.181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 128424000000 | 132878.595 |  | 34382.155 | 10771.038 | 19103.161 | 0 | 68622.241 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 33606.72 | 746.78 | 0 | 34353.5
Cost per Total Building Area ($/m2) | 14.65 | 0.33 | 0 | 14.98
Cost per Net Conditioned Building Area ($/m2) | 14.65 | 0.33 | 0 | 14.98

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1074.59 | 468.44 | 468.44
Net Site Energy | 1074.59 | 468.44 | 468.44
Total Source Energy | 3297.54 | 1437.47 | 1437.47
Net Source Energy | 3297.54 | 1437.47 | 1437.47
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 1.42 | 139.69 | 0 | 0 | 0 | 0
Cooling | 139.3 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 49.8 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 45.28 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 934.9 | 139.69 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 8.61 | 27.86 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 18.29 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 21.52
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 11.84 | 6.19 | 0
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 379.89 | 90 | 180
BACK_SPACE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 379.89 | 90 | 0
CORE_RETAIL_WALL_WEST_2 | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 178.43 | 270 | 90 | W
CORE_RETAIL_WALL_EAST_2 | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 178.43 | 90 | 90 | E
CORE_RETAIL_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1600.48 | 180 | 0
POINT_OF_SALE_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 180 | 0
FRONT_RETAIL_WALLL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 36.58 | 90 | 90 | E
FRONT_RETAIL_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 153.22 | 180 | 90 | S
FRONT_RETAIL_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 90 | 0
FRONT_ENTRY_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 12 | 180 | 180
FRONT_ENTRY_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
POINT_OF_SALE_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 38.05 | 38.05 | 3.18 | 0.262 | 0.318 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 38.05 | 38.05 | 3.18 | 0.262 | 0.318 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
FRONT_ENTRY_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 7.83 | 7.83 | 3.18 | 0.262 | 0.318 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 3.18 | 0.262 | 0.318
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 3.18 | 0.262 | 0.318
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 31333.51 | 22253.52 | 9079.99 | 0.71 | 3.51
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 169533.27 | 114618.6 | 54914.67 | 0.68 | 3.51
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 23930.67 | 17414.47 | 6516.21 | 0.73 | 3.59
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18998.22 | 13051.53 | 5946.69 | 0.69 | 3.68
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 1906.6 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 33018.18 | 0.8
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 133518.59 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 19230.6 | 0.8
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 19230.73 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.08 | 7.88 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.44 | 1572.12 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 6.83 | 12807.58 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.17 | 1329.06 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.8 | 910.33 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 15140.4909 | 27.0225 | 65.1621 | 0 | 0.0002 | 115890.691 | 6466.544
February | 13375.2092 | 24.1334 | 58.8467 | 0 | 0.0002 | 104661.5534 | 5736.7418
March | 13850.1743 | 26.046 | 66.111 | 0 | 0.0002 | 117592.1715 | 6037.9452
April | 13506.2534 | 25.812 | 66.493 | 0 | 0.0002 | 118275.5101 | 5926.1381
May | 16182.0182 | 31.2465 | 81.2388 | 0 | 0.0003 | 144507.8897 | 7129.8129
June | 18158.1296 | 35.0633 | 91.1647 | 0 | 0.0003 | 162163.9719 | 8000.5859
July | 19528.0654 | 37.7087 | 98.0426 | 0 | 0.0004 | 174398.3947 | 8604.1882
August | 19925.8044 | 38.4767 | 100.0394 | 0 | 0.0004 | 177950.4644 | 8779.4345
September | 17533.3585 | 33.8569 | 88.0279 | 0 | 0.0003 | 156584.3578 | 7725.3078
October | 14004.6491 | 26.9422 | 69.8177 | 0 | 0.0003 | 124191.1273 | 6161.2304
November | 13139.4123 | 24.61 | 62.2314 | 0 | 0.0002 | 110690.5219 | 5718.9166
December | 14491.7161 | 26.2762 | 64.388 | 0 | 0.0002 | 114518.2408 | 6227.4708
Annual Sum or Average | 188835.2813 | 357.1944 | 911.5632 | 0 | 0.0033 | 1621420 | 82514.3162
Minimum of Months | 13139.4123 | 24.1334 | 58.8467 | 0 | 0.0002 | 104661.5534 | 5718.9166
Maximum of Months | 19925.8044 | 38.4767 | 100.0394 | 0 | 0.0004 | 177950.4644 | 8779.4345
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 66821500000 | 52477.851 | 23-JAN-17:00 | 34382.155 | 10771.038 | 904.601 | 0 | 3252.773 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 60346900000 | 54099.822 | 18-FEB-16:00 | 34382.155 | 10771.038 | 1993.557 | 0 | 6953.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 67802500000 | 57001.835 | 28-MAR-15:00 | 34382.155 | 10771.038 | 2580.811 | 0 | 9267.831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 68196500000 | 68978.214 | 15-APR-15:00 | 34382.155 | 10771.038 | 4844.69 | 0 | 18980.331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 83321900000 | 81912.042 | 15-MAY-14:00 | 34382.155 | 10771.038 | 7458.478 | 0 | 29300.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 93502200000 | 91198.715 | 19-JUN-14:00 | 34382.155 | 10771.038 | 8979.719 | 0 | 37065.804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 100556000000 | 102605.343 | 03-JUL-14:00 | 34382.155 | 10771.038 | 10904.467 | 0 | 46547.683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 102605000000 | 95953.932 | 17-AUG-14:00 | 34382.155 | 10771.038 | 9955.051 | 0 | 40845.687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 90285100000 | 85179.791 | 11-SEP-14:09 | 34382.155 | 10771.038 | 8173.555 | 0 | 31853.043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 71607400000 | 68894.047 | 21-OCT-15:00 | 34382.155 | 10771.038 | 4942.051 | 0 | 18798.802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 63823100000 | 54977.215 | 22-NOV-15:00 | 34382.155 | 10771.038 | 2163.075 | 0 | 7660.946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 66030100000 | 50073.106 | 02-DEC-17:30 | 34382.155 | 10771.038 | 359.251 | 0 | 1393.377 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 934898000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 60346900000 | 50073.106 |  | 34382.155 | 10771.038 | 359.251 | 0 | 1393.377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 102605000000 | 102605.343 |  | 34382.155 | 10771.038 | 10904.467 | 0 | 46547.683 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 26909.58 | 1317.57 | 0 | 28227.15
Cost per Total Building Area ($/m2) | 11.73 | 0.57 | 0 | 12.3
Cost per Net Conditioned Building Area ($/m2) | 11.73 | 0.57 | 0 | 12.3

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 896.24 | 390.69 | 390.69
Net Site Energy | 896.24 | 390.69 | 390.69
Total Source Energy | 2695.42 | 1174.99 | 1174.99
Net Source Energy | 2695.42 | 1174.99 | 1174.99
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0.28 | 39.16 | 0 | 0 | 0 | 0
Cooling | 54.89 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 49.77 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 53.05 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 857.08 | 39.16 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 8.61 | 27.86 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 18.29 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 21.52
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 11.84 | 6.19 | 0
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 379.89 | 90 | 180
BACK_SPACE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 379.89 | 90 | 0
CORE_RETAIL_WALL_WEST_2 | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 178.43 | 270 | 90 | W
CORE_RETAIL_WALL_EAST_2 | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 178.43 | 90 | 90 | E
CORE_RETAIL_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1600.48 | 180 | 0
POINT_OF_SALE_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 180 | 0
FRONT_RETAIL_WALLL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 36.58 | 90 | 90 | E
FRONT_RETAIL_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 153.22 | 180 | 90 | S
FRONT_RETAIL_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 90 | 0
FRONT_ENTRY_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 12 | 180 | 180
FRONT_ENTRY_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
POINT_OF_SALE_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 38.05 | 38.05 | 3.18 | 0.262 | 0.318 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 38.05 | 38.05 | 3.18 | 0.262 | 0.318 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
FRONT_ENTRY_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 7.83 | 7.83 | 3.18 | 0.262 | 0.318 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 3.18 | 0.262 | 0.318
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 3.18 | 0.262 | 0.318
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17612.6 | 14066.39 | 3546.2 | 0.8 | 4.03
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 110572.43 | 84267.59 | 26304.84 | 0.76 | 3.95
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17339.77 | 13848.49 | 3491.27 | 0.8 | 4.04
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12728.07 | 10165.34 | 2562.73 | 0.8 | 4.03
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 1005.08 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 17817.35 | 0.8
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 96668.12 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10247.7 | 0.8
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10249.71 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 4.02 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.06 | 1212.08 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 6.02 | 11285.18 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.05 | 1193.3 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.77 | 875.93 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 6272.3433 | 5.3956 | 53.5068 | 0 | 0 | 322835.1087 | 2334.1157
February | 5606.3256 | 4.8188 | 48.5118 | 0 | 0 | 292700.1031 | 2088.3664
March | 6226.4233 | 5.3447 | 55.1582 | 0 | 0 | 332806.2886 | 2323.2611
April | 5819.617 | 4.9893 | 52.67 | 0 | 0 | 317796.9232 | 2174.8732
May | 6158.7666 | 5.2733 | 56.9397 | 0 | 0 | 343563.5397 | 2305.2802
June | 6220.9584 | 5.324 | 57.9666 | 0 | 0 | 349761.4341 | 2329.9381
July | 6973.2976 | 5.9676 | 65.0342 | 0 | 0 | 392406.2903 | 2611.8869
August | 7566.8663 | 6.4755 | 70.57 | 0 | 0 | 425808.0063 | 2834.2113
September | 6961.4873 | 5.9575 | 64.9241 | 0 | 0 | 391741.6962 | 2607.4633
October | 6515.9745 | 5.5763 | 60.7566 | 0 | 0 | 366595.4261 | 2440.5556
November | 5850.8651 | 5.0148 | 53.1823 | 0 | 0 | 320888.9771 | 2187.2513
December | 6150.3868 | 5.2845 | 53.568 | 0 | 0 | 323208.0656 | 2292.093
Annual Sum or Average | 76323.3119 | 65.4218 | 692.7882 | 0 | 0.0003 | 4180110 | 28529.296
Minimum of Months | 5606.3256 | 4.8188 | 48.5118 | 0 | 0 | 292700.1031 | 2088.3664
Maximum of Months | 7566.8663 | 6.4755 | 70.57 | 0 | 0 | 425808.0063 | 2834.2113
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 66193300000 | 58299.664 | 27-JAN-15:09 | 34382.155 | 10771.038 | 11171.358 | 0 | 1975.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 60014500000 | 59566.099 | 13-FEB-15:20 | 34382.155 | 10771.038 | 11907.946 | 0 | 2504.959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 68237800000 | 59204.952 | 29-MAR-14:00 | 34382.155 | 10771.038 | 11836.265 | 0 | 2215.494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 65160300000 | 60001.55 | 13-APR-15:39 | 34382.155 | 10771.038 | 12034.663 | 0 | 2813.693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 70443400000 | 63229.699 | 30-MAY-14:00 | 34382.155 | 10771.038 | 5360.961 | 0 | 12715.545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 71714200000 | 64278.38 | 30-JUN-14:00 | 34382.155 | 10771.038 | 5635.288 | 0 | 13489.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 80458000000 | 71477.079 | 24-JUL-14:00 | 34382.155 | 10771.038 | 7747.797 | 0 | 18576.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 87306600000 | 79115.299 | 09-AUG-14:00 | 34382.155 | 10771.038 | 9968.307 | 0 | 23993.799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 80321800000 | 74971.578 | 25-SEP-14:00 | 34382.155 | 10771.038 | 8474.652 | 0 | 21343.732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 75165800000 | 66388.746 | 05-OCT-14:00 | 34382.155 | 10771.038 | 6208.589 | 0 | 15026.964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 65794300000 | 62117.38 | 08-NOV-16:00 | 34382.155 | 10771.038 | 11654.547 | 0 | 2142.355 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 66269800000 | 60725.763 | 18-DEC-16:49 | 34382.155 | 10771.038 | 10460.371 | 0 | 1944.916 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 857080000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 60014500000 | 58299.664 |  | 34382.155 | 10771.038 | 5360.961 | 0 | 1944.916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 87306600000 | 79115.299 |  | 34382.155 | 10771.038 | 12034.663 | 0 | 23993.799 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 31710.72 | 343.14 | 0 | 32053.87
Cost per Total Building Area ($/m2) | 13.82 | 0.15 | 0 | 13.97
Cost per Net Conditioned Building Area ($/m2) | 13.82 | 0.15 | 0 | 13.97

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1076.1 | 469.09 | 469.09
Net Site Energy | 1076.1 | 469.09 | 469.09
Total Source Energy | 3526.17 | 1537.13 | 1537.13
Net Source Energy | 3526.17 | 1537.13 | 1537.13
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0.73 | 130 | 0 | 0 | 0 | 0
Cooling | 130.39 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 49.75 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 66.13 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 946.1 | 130 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 8.61 | 27.86 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 18.29 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 21.52
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 11.84 | 6.19 | 0
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 379.89 | 90 | 180
BACK_SPACE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 379.89 | 90 | 0
CORE_RETAIL_WALL_WEST_2 | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 178.43 | 270 | 90 | W
CORE_RETAIL_WALL_EAST_2 | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 178.43 | 90 | 90 | E
CORE_RETAIL_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1600.48 | 180 | 0
POINT_OF_SALE_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 180 | 0
FRONT_RETAIL_WALLL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 36.58 | 90 | 90 | E
FRONT_RETAIL_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 153.22 | 180 | 90 | S
FRONT_RETAIL_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 90 | 0
FRONT_ENTRY_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 12 | 180 | 180
FRONT_ENTRY_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
POINT_OF_SALE_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 38.05 | 38.05 | 3.18 | 0.262 | 0.318 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 38.05 | 38.05 | 3.18 | 0.262 | 0.318 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
FRONT_ENTRY_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 7.83 | 7.83 | 3.18 | 0.262 | 0.318 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 3.18 | 0.262 | 0.318
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 3.18 | 0.262 | 0.318
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 22891.96 | 18282.78 | 4609.18 | 0.8 | 3.79
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 105952.77 | 83339.74 | 22613.04 | 0.79 | 4.1
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20476.81 | 16353.91 | 4122.9 | 0.8 | 3.79
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14480.3 | 11564.77 | 2915.53 | 0.8 | 4.03
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 1564.36 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 27840.18 | 0.8
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 111911.03 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15776.79 | 0.8
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15776.07 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.07 | 6.74 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.38 | 1575.4 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 6.19 | 11612.92 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.24 | 1409.19 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.87 | 996.52 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 16887.8448 | 26.1982 | 102.2222 | 0 | 0.0002 | 509757.561 | 6974.5926
February | 14266.0836 | 22.6558 | 91.2844 | 0 | 0.0002 | 455234.2898 | 5946.354
March | 16057.8345 | 25.5996 | 103.6743 | 0 | 0.0002 | 517026.5623 | 6703.4167
April | 15771.9021 | 25.8052 | 108.0449 | 0 | 0.0002 | 538847.6652 | 6652.7973
May | 17992.0563 | 29.4907 | 123.752 | 0 | 0.0002 | 617184.6934 | 7594.7943
June | 21938.7319 | 35.9779 | 151.0698 | 0 | 0.0003 | 753426.3776 | 9262.6636
July | 23040.8506 | 37.7853 | 158.6589 | 0 | 0.0003 | 791275.6625 | 9727.9847
August | 23176.5906 | 38.0079 | 159.5936 | 0 | 0.0003 | 795937.2828 | 9785.2949
September | 19620.9287 | 32.1769 | 135.1094 | 0 | 0.0003 | 673827.6988 | 8284.0733
October | 16488.1782 | 27.0039 | 113.2034 | 0 | 0.0002 | 564575.0536 | 6957.7143
November | 14947.8281 | 23.9396 | 97.5372 | 0 | 0.0002 | 486424.7906 | 6251.4231
December | 16524.1855 | 25.7946 | 101.5297 | 0 | 0.0002 | 506310.9578 | 6841.0875
Annual Sum or Average | 216713.0149 | 350.4356 | 1445.68 | 0 | 0.0027 | 7209830 | 90982.1964
Minimum of Months | 14266.0836 | 22.6558 | 91.2844 | 0 | 0.0002 | 455234.2898 | 5946.354
Maximum of Months | 23176.5906 | 38.0079 | 159.5936 | 0 | 0.0003 | 795937.2828 | 9785.2949
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 66892400000 | 49980.679 | 18-JAN-16:49 | 34382.155 | 10771.038 | 1413.386 | 0 | 246.815 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 59737700000 | 58493.704 | 27-FEB-15:39 | 34382.155 | 10771.038 | 11283.749 | 0 | 2056.762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 67846300000 | 58912.742 | 21-MAR-15:39 | 34382.155 | 10771.038 | 12005.299 | 0 | 1754.249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 70709800000 | 71565.605 | 21-APR-15:00 | 34382.155 | 10771.038 | 7585.024 | 0 | 18827.388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 80989500000 | 85688.314 | 31-MAY-15:00 | 34382.155 | 10771.038 | 11338.691 | 0 | 29196.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 98867700000 | 105050.531 | 27-JUN-15:00 | 34382.155 | 10771.038 | 15482.019 | 0 | 44415.319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 103834000000 | 103350.76 | 24-JUL-15:00 | 34382.155 | 10771.038 | 15238.388 | 0 | 42959.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 104446000000 | 101907.834 | 04-AUG-15:00 | 34382.155 | 10771.038 | 14942.896 | 0 | 41811.745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 88422400000 | 98145.063 | 01-SEP-14:00 | 34382.155 | 10771.038 | 14204.328 | 0 | 38787.541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 74085800000 | 72540.584 | 03-OCT-15:00 | 34382.155 | 10771.038 | 7856.262 | 0 | 19531.129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 63830600000 | 61640.802 | 10-NOV-16:00 | 34382.155 | 10771.038 | 11672.22 | 0 | 1648.105 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 66440200000 | 50215.581 | 06-DEC-16:30 | 34382.155 | 10771.038 | 1524.552 | 0 | 370.552 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 946103000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 59737700000 | 49980.679 |  | 34382.155 | 10771.038 | 1413.386 | 0 | 246.815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 104446000000 | 105050.531 |  | 34382.155 | 10771.038 | 15482.019 | 0 | 44415.319 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 26572.48 | 986.39 | 0 | 27558.87
Cost per Total Building Area ($/m2) | 11.58 | 0.43 | 0 | 12.01
Cost per Net Conditioned Building Area ($/m2) | 11.58 | 0.43 | 0 | 12.01

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 914.4 | 398.61 | 398.61
Net Site Energy | 914.4 | 398.61 | 398.61
Total Source Energy | 2555.59 | 1114.04 | 1114.04
Net Source Energy | 2555.59 | 1114.04 | 1114.04
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 1.48 | 137.03 | 0 | 0 | 0 | 0
Cooling | 13.74 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 49.78 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 13.27 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 777.37 | 137.03 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 8.61 | 27.86 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 18.29 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 21.52
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 11.84 | 6.19 | 0
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 379.89 | 90 | 180
BACK_SPACE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 379.89 | 90 | 0
CORE_RETAIL_WALL_WEST_2 | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 178.43 | 270 | 90 | W
CORE_RETAIL_WALL_EAST_2 | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 178.43 | 90 | 90 | E
CORE_RETAIL_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1600.48 | 180 | 0
POINT_OF_SALE_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 180 | 0
FRONT_RETAIL_WALLL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 36.58 | 90 | 90 | E
FRONT_RETAIL_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 153.22 | 180 | 90 | S
FRONT_RETAIL_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 90 | 0
FRONT_ENTRY_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 12 | 180 | 180
FRONT_ENTRY_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
POINT_OF_SALE_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 38.05 | 38.05 | 6.49 | 0.391 | 0.39 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 38.05 | 38.05 | 6.49 | 0.391 | 0.39 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
FRONT_ENTRY_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 7.83 | 7.83 | 6.49 | 0.391 | 0.39 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 6.49 | 0.391 | 0.39
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 6.49 | 0.391 | 0.39
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 11449.21 | 9143.97 | 2305.24 | 0.8 | 4.05
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 55356.43 | 44210.71 | 11145.73 | 0.8 | 3.47
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15472.59 | 12357.26 | 3115.32 | 0.8 | 4.03
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12179.11 | 9726.91 | 2452.2 | 0.8 | 4.04
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 1419.95 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 22028.31 | 0.8
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 106850.22 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13579.2 | 0.8
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13580.86 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.06 | 5.65 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.69 | 802.25 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 3.34 | 3657.18 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.93 | 1064.8 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.74 | 838.15 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 7176.129 | 6.2204 | 52.7374 | 0 | 0 | 318162.1708 | 2644.5702
February | 5878.8661 | 5.0711 | 47.6567 | 0 | 0 | 287529.2753 | 2180.0842
March | 6635.7109 | 5.7245 | 53.6925 | 0 | 0 | 323944.9743 | 2460.4445
April | 6079.2498 | 5.2351 | 50.8576 | 0 | 0 | 306847.421 | 2259.2032
May | 6077.8831 | 5.2228 | 52.8357 | 0 | 0 | 318789.2208 | 2264.7651
June | 5816.1645 | 4.9897 | 52.0339 | 0 | 0 | 313957.2724 | 2171.7378
July | 5850.0006 | 5.0131 | 53.3376 | 0 | 0 | 321826.6761 | 2187.426
August | 6085.8779 | 5.218 | 54.997 | 0 | 0 | 331837.3859 | 2274.1263
September | 5887.741 | 5.0456 | 53.6542 | 0 | 0 | 323736.7669 | 2201.4539
October | 6043.0453 | 5.1879 | 53.4267 | 0 | 0 | 322358.7852 | 2254.511
November | 6100.6411 | 5.2553 | 50.722 | 0 | 0 | 306028.2991 | 2266.1931
December | 6882.5056 | 5.9556 | 52.4315 | 0 | 0 | 316324.1657 | 2542.0132
Annual Sum or Average | 74513.8151 | 64.139 | 628.383 | 0 | 0.0003 | 3791340 | 27706.5283
Minimum of Months | 5816.1645 | 4.9897 | 47.6567 | 0 | 0 | 287529.2753 | 2171.7378
Maximum of Months | 7176.129 | 6.2204 | 54.997 | 0 | 0 | 331837.3859 | 2644.5702
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 65235200000 | 49123.952 | 17-JAN-17:19 | 34382.155 | 10771.038 | 213.658 | 0 | 589.817 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 58954300000 | 52143.13 | 15-FEB-15:20 | 34382.155 | 10771.038 | 4486.028 | 0 | 2503.909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 66420900000 | 49279.176 | 01-MAR-17:00 | 34382.155 | 10771.038 | 326.919 | 0 | 631.779 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 62915200000 | 54207.302 | 29-APR-14:00 | 34382.155 | 10771.038 | 2064.417 | 0 | 6989.691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 65363800000 | 54499.94 | 17-MAY-14:09 | 34382.155 | 10771.038 | 2060.876 | 0 | 7285.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 64373000000 | 57156.9 | 16-JUN-14:00 | 34382.155 | 10771.038 | 2658.401 | 0 | 9345.306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 65986600000 | 62641.444 | 03-JUL-14:20 | 34382.155 | 10771.038 | 3742.391 | 0 | 13745.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 68039100000 | 57154.442 | 26-AUG-14:39 | 34382.155 | 10771.038 | 2627.2 | 0 | 9374.049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 66378200000 | 72942.094 | 28-SEP-14:00 | 34382.155 | 10771.038 | 5534.332 | 0 | 22254.569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 66095700000 | 55074.836 | 13-OCT-15:00 | 34382.155 | 10771.038 | 2253.656 | 0 | 7667.988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 62747300000 | 50464.011 | 14-NOV-16:00 | 34382.155 | 10771.038 | 1026.758 | 0 | 1116.776 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 64858300000 | 49141.506 | 07-DEC-16:49 | 34382.155 | 10771.038 | 209.728 | 0 | 611.3 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 777368000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 58954300000 | 49123.952 |  | 34382.155 | 10771.038 | 209.728 | 0 | 589.817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 68039100000 | 72942.094 |  | 34382.155 | 10771.038 | 5534.332 | 0 | 22254.569 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 32541.6 | 1178.55 | 0 | 33720.15
Cost per Total Building Area ($/m2) | 14.19 | 0.51 | 0 | 14.7
Cost per Net Conditioned Building Area ($/m2) | 14.19 | 0.51 | 0 | 14.7

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1164.32 | 507.55 | 507.55
Net Site Energy | 1164.32 | 507.55 | 507.55
Total Source Energy | 3503.05 | 1527.05 | 1527.05
Net Source Energy | 3503.05 | 1527.05 | 1527.05
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 2.7 | 265.93 | 0 | 0 | 0 | 0
Cooling | 106.1 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 49.75 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 40.75 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 898.39 | 265.93 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 8.61 | 27.86 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 18.29 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 21.52
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 11.84 | 6.19 | 0
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 379.89 | 90 | 180
BACK_SPACE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 379.89 | 90 | 0
CORE_RETAIL_WALL_WEST_2 | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 178.43 | 270 | 90 | W
CORE_RETAIL_WALL_EAST_2 | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 178.43 | 90 | 90 | E
CORE_RETAIL_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1600.48 | 180 | 0
POINT_OF_SALE_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 180 | 0
FRONT_RETAIL_WALLL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 36.58 | 90 | 90 | E
FRONT_RETAIL_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 153.22 | 180 | 90 | S
FRONT_RETAIL_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 90 | 0
FRONT_ENTRY_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 12 | 180 | 180
FRONT_ENTRY_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
POINT_OF_SALE_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 38.05 | 38.05 | 3.18 | 0.402 | 0.495 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 38.05 | 38.05 | 3.18 | 0.402 | 0.495 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
FRONT_ENTRY_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 7.83 | 7.83 | 3.18 | 0.402 | 0.495 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 3.18 | 0.402 | 0.495
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 28662.52 | 20114.3 | 8548.22 | 0.7 | 3.52
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 156665.85 | 105919.15 | 50746.7 | 0.68 | 3.51
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 23707.41 | 17089.11 | 6618.29 | 0.72 | 3.57
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20298.59 | 14177.26 | 6121.34 | 0.7 | 3.51
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 2202.03 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 38490.76 | 0.8
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 156280.97 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 22309.95 | 0.8
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 22310.87 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.09 | 8.81 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.28 | 1452.68 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 6.31 | 11835.5 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.13 | 1286.17 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.89 | 1016.13 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 15606.3057 | 26.7402 | 69.4955 | 0 | 0.0003 | 4320.9849 | 6551.1298
February | 13020.3282 | 22.9905 | 61.7415 | 0 | 0.0003 | 3839.1355 | 5527.8912
March | 12848.9863 | 24.0254 | 68.3139 | 0 | 0.0003 | 4248.3132 | 5577.4407
April | 11401.3747 | 21.9603 | 64.1601 | 0 | 0.0003 | 3990.2093 | 5007.7335
May | 12005.3358 | 23.826 | 71.4372 | 0 | 0.0003 | 4443.0061 | 5337.233
June | 14996.8921 | 29.9848 | 90.4628 | 0 | 0.0004 | 5626.3578 | 6687.4709
July | 16500.0339 | 32.9903 | 99.5302 | 0 | 0.0004 | 6190.3102 | 7357.7632
August | 17074.8196 | 34.1395 | 102.9974 | 0 | 0.0004 | 6405.9522 | 7614.074
September | 13300.909 | 26.5903 | 80.2126 | 0 | 0.0003 | 4988.8431 | 5930.863
October | 11996.9433 | 23.5239 | 69.8111 | 0 | 0.0003 | 4341.7864 | 5307.4006
November | 11897.5274 | 22.5285 | 64.813 | 0 | 0.0003 | 4030.6954 | 5190.2312
December | 14225.5255 | 25.2293 | 68.068 | 0 | 0.0003 | 4232.5644 | 6049.6952
Annual Sum or Average | 164874.9813 | 314.5288 | 911.0435 | 0 | 0.0037 | 56658.1586 | 72138.9262
Minimum of Months | 11401.3747 | 21.9603 | 61.7415 | 0 | 0.0003 | 3839.1355 | 5007.7335
Maximum of Months | 17074.8196 | 34.1395 | 102.9974 | 0 | 0.0004 | 6405.9522 | 7614.074
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 68515300000 | 52204.541 | 17-JAN-09:09 | 34382.155 | 10771.038 | 6589.054 | 462.293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 60874900000 | 49481.999 | 21-FEB-09:09 | 34382.155 | 10771.038 | 3946.287 | 382.518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 67363000000 | 52426.487 | 25-MAR-15:00 | 34382.155 | 10771.038 | 1547.924 | 0 | 5725.369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 63270400000 | 57312.505 | 05-APR-15:00 | 34382.155 | 10771.038 | 2618.645 | 0 | 9540.667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 70450100000 | 68950.25 | 15-MAY-15:00 | 34382.155 | 10771.038 | 4931.344 | 0 | 18865.713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 89213800000 | 96840.093 | 30-JUN-14:00 | 34382.155 | 10771.038 | 9968.61 | 0 | 41718.291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 98156100000 | 103037.934 | 25-JUL-14:39 | 34382.155 | 10771.038 | 11117.424 | 0 | 46767.316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 101575000000 | 107671.224 | 09-AUG-14:00 | 34382.155 | 10771.038 | 12244.264 | 0 | 50273.768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 79105100000 | 83998.674 | 09-SEP-15:30 | 34382.155 | 10771.038 | 7707.762 | 0 | 31137.719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 68845100000 | 66021.935 | 12-OCT-15:00 | 34382.155 | 10771.038 | 4302.421 | 0 | 16566.321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 63912300000 | 59775.242 | 04-NOV-16:00 | 34382.155 | 10771.038 | 2517.463 | 0 | 8937.302 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 67113300000 | 49850.314 | 21-DEC-09:09 | 34382.155 | 10771.038 | 4457.974 | 239.147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 898395000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 60874900000 | 49481.999 |  | 34382.155 | 10771.038 | 1547.924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 101575000000 | 107671.224 |  | 34382.155 | 10771.038 | 12244.264 | 462.293 | 50273.768 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 19622.81 | 2565.01 | 0 | 22187.82
Cost per Total Building Area ($/m2) | 8.55 | 1.12 | 0 | 9.67
Cost per Net Conditioned Building Area ($/m2) | 8.55 | 1.12 | 0 | 9.67

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1095.59 | 477.59 | 477.59
Net Site Energy | 1095.59 | 477.59 | 477.59
Total Source Energy | 3138.59 | 1368.18 | 1368.18
Net Source Energy | 3138.59 | 1368.18 | 1368.18
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 1.64 | 223.08 | 0 | 0 | 0 | 0
Cooling | 72.49 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 49.77 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 49.52 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 872.51 | 223.08 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 8.61 | 27.86 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 18.29 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 21.52
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 11.84 | 6.19 | 0
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 379.89 | 90 | 180
BACK_SPACE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 379.89 | 90 | 0
CORE_RETAIL_WALL_WEST_2 | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 178.43 | 270 | 90 | W
CORE_RETAIL_WALL_EAST_2 | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 178.43 | 90 | 90 | E
CORE_RETAIL_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1600.48 | 180 | 0
POINT_OF_SALE_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 180 | 0
FRONT_RETAIL_WALLL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 36.58 | 90 | 90 | E
FRONT_RETAIL_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 153.22 | 180 | 90 | S
FRONT_RETAIL_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 90 | 0
FRONT_ENTRY_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 12 | 180 | 180
FRONT_ENTRY_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
POINT_OF_SALE_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 38.05 | 38.05 | 3.18 | 0.402 | 0.495 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 38.05 | 38.05 | 3.18 | 0.402 | 0.495 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
FRONT_ENTRY_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 7.83 | 7.83 | 3.18 | 0.402 | 0.495 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 3.18 | 0.402 | 0.495
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 21626.3 | 17271.96 | 4354.34 | 0.8 | 3.79
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 98880.94 | 78971.78 | 19909.16 | 0.8 | 4.18
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18393.72 | 14690.24 | 3703.48 | 0.8 | 4.03
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15218.78 | 12154.56 | 3064.22 | 0.8 | 4.03
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 1918.49 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 33214.41 | 0.8
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 130044.58 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 18965.09 | 0.8
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 18965.09 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.1 | 9.28 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.31 | 1488.29 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 5.97 | 11206.03 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.11 | 1265.83 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.92 | 1047.34 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 20545.2828 | 33.7497 | 81.8195 | 0 | 0.0003 | 85065.1305 | 8591.957
February | 17818.0581 | 29.7114 | 73.3497 | 0 | 0.0003 | 76262.552 | 7494.7753
March | 19485.1892 | 32.9096 | 82.4763 | 0 | 0.0003 | 85754.5845 | 8237.0427
April | 17743.9308 | 30.5831 | 78.4317 | 0 | 0.0003 | 81553.3647 | 7561.2249
May | 19672.7442 | 34.4509 | 89.8979 | 0 | 0.0004 | 93479.5001 | 8436.4399
June | 21727.8682 | 38.1221 | 99.6805 | 0 | 0.0004 | 103652.3966 | 9324.8514
July | 23388.9067 | 41.0367 | 107.3024 | 0 | 0.0004 | 111577.9118 | 10037.739
August | 23679.3749 | 41.5464 | 108.635 | 0 | 0.0004 | 112963.6043 | 10162.3983
September | 20670.594 | 36.2669 | 94.8291 | 0 | 0.0004 | 98607.655 | 8871.0878
October | 18402.2695 | 31.8747 | 82.1909 | 0 | 0.0003 | 85463.2917 | 7857.1543
November | 18625.6173 | 31.3299 | 78.1458 | 0 | 0.0003 | 81251.0348 | 7861.1288
December | 20554.3768 | 33.7277 | 81.6559 | 0 | 0.0003 | 84894.7953 | 8592.1393
Annual Sum or Average | 242314.2125 | 415.3092 | 1058.4146 | 0 | 0.0041 | 1100530 | 103027.9388
Minimum of Months | 17743.9308 | 29.7114 | 73.3497 | 0 | 0.0003 | 76262.552 | 7494.7753
Maximum of Months | 23679.3749 | 41.5464 | 108.635 | 0 | 0.0004 | 112963.6043 | 10162.3983
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 67440700000 | 49789.163 | 26-JAN-17:30 | 34382.155 | 10771.038 | 393.952 | 0 | 1074.734 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 60461900000 | 58226.203 | 14-FEB-16:40 | 34382.155 | 10771.038 | 10612.519 | 0 | 2460.491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 67987300000 | 57857.889 | 02-MAR-16:00 | 34382.155 | 10771.038 | 10372.607 | 0 | 2332.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 64656500000 | 59220.078 | 08-APR-15:50 | 34382.155 | 10771.038 | 11934.134 | 0 | 2132.751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 74111700000 | 67510.597 | 31-MAY-15:00 | 34382.155 | 10771.038 | 6783.926 | 0 | 15573.478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 82176900000 | 82216.381 | 29-JUN-14:00 | 34382.155 | 10771.038 | 10833.033 | 0 | 26230.154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 88460300000 | 87605.431 | 31-JUL-14:00 | 34382.155 | 10771.038 | 12302.96 | 0 | 30149.278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 89558900000 | 85037.021 | 01-AUG-14:00 | 34382.155 | 10771.038 | 11445.614 | 0 | 28438.213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 78177300000 | 73644.378 | 02-SEP-15:50 | 34382.155 | 10771.038 | 8586.024 | 0 | 19905.161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 67756300000 | 59898.836 | 16-OCT-15:39 | 34382.155 | 10771.038 | 11974.848 | 0 | 2770.795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 64416800000 | 55370.919 | 10-NOV-15:20 | 34382.155 | 10771.038 | 8237.457 | 0 | 1980.269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 67305600000 | 49658.413 | 05-DEC-16:49 | 34382.155 | 10771.038 | 358.878 | 0 | 979.058 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 872510000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 60461900000 | 49658.413 |  | 34382.155 | 10771.038 | 358.878 | 0 | 979.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 89558900000 | 87605.431 |  | 34382.155 | 10771.038 | 12302.96 | 0 | 30149.278 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 9142.55 | 1528.96 | 0 | 10671.51
Cost per Total Building Area ($/m2) | 3.99 | 0.67 | 0 | 4.65
Cost per Net Conditioned Building Area ($/m2) | 3.99 | 0.67 | 0 | 4.65

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1036.3 | 451.75 | 451.75
Net Site Energy | 1036.3 | 451.75 | 451.75
Total Source Energy | 1646.77 | 717.86 | 717.86
Net Source Energy | 1646.77 | 717.86 | 717.86
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 2.75 | 243.8 | 0 | 0 | 0 | 0
Cooling | 17.47 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 49.67 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 23.52 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 792.51 | 243.8 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 8.61 | 27.86 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 18.29 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 21.52
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 11.84 | 6.19 | 0
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 379.89 | 90 | 180
BACK_SPACE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 379.89 | 90 | 0
CORE_RETAIL_WALL_WEST_2 | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 178.43 | 270 | 90 | W
CORE_RETAIL_WALL_EAST_2 | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 178.43 | 90 | 90 | E
CORE_RETAIL_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1600.48 | 180 | 0
POINT_OF_SALE_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 180 | 0
FRONT_RETAIL_WALLL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 36.58 | 90 | 90 | E
FRONT_RETAIL_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 153.22 | 180 | 90 | S
FRONT_RETAIL_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 90 | 0
FRONT_ENTRY_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 12 | 180 | 180
FRONT_ENTRY_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
POINT_OF_SALE_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 38.05 | 38.05 | 3.18 | 0.402 | 0.495 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 38.05 | 38.05 | 3.18 | 0.402 | 0.495 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
FRONT_ENTRY_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 7.83 | 7.83 | 3.18 | 0.402 | 0.495 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 3.18 | 0.402 | 0.495
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16016.8 | 12791.9 | 3224.9 | 0.8 | 4.04
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 68385.91 | 54616.77 | 13769.14 | 0.8 | 4.32
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17029.86 | 13600.99 | 3428.87 | 0.8 | 4.03
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13699.56 | 10911.71 | 2787.85 | 0.8 | 4.02
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 1748.53 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 30596.28 | 0.8
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 127424.99 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 17735.89 | 0.8
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 17735.99 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.08 | 7.06 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.97 | 1102.26 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 4.13 | 7750.08 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.03 | 1171.97 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.82 | 937.26 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 5716.2554 | 7.4334 | 14.3558 | 0 | 0.0001 | 189591.492 | 2218.8111
February | 4523.672 | 6.1095 | 12.8096 | 0 | 0.0001 | 169210.1194 | 1780.203
March | 4885.846 | 6.6952 | 14.4516 | 0 | 0.0001 | 190915.385 | 1933.0701
April | 4057.9293 | 5.79 | 13.4668 | 0 | 0.0001 | 177939.4645 | 1630.0661
May | 3657.6822 | 5.5289 | 14.1175 | 0 | 0.0001 | 186577.8731 | 1502.4832
June | 3363.0135 | 5.2607 | 14.1121 | 0 | 0.0001 | 186526.6859 | 1400.4284
July | 3398.8151 | 5.4301 | 14.9861 | 0 | 0.0001 | 198090.0649 | 1427.4771
August | 3532.9537 | 5.6709 | 15.7466 | 0 | 0.0001 | 208145.4305 | 1486.6504
September | 3420.9293 | 5.331 | 14.2254 | 0 | 0.0001 | 188021.0637 | 1422.3683
October | 3867.78 | 5.6898 | 13.9284 | 0 | 0.0001 | 184060.6967 | 1572.0111
November | 4696.7227 | 6.404 | 13.6875 | 0 | 0.0001 | 180816.0369 | 1854.8099
December | 5668.0502 | 7.3855 | 14.3292 | 0 | 0.0001 | 189242.717 | 2201.6844
Annual Sum or Average | 50789.6493 | 72.729 | 170.2168 | 0 | 0.0007 | 2249140 | 20430.063
Minimum of Months | 3363.0135 | 5.2607 | 12.8096 | 0 | 0.0001 | 169210.1194 | 1400.4284
Maximum of Months | 5716.2554 | 7.4334 | 15.7466 | 0 | 0.0001 | 208145.4305 | 2218.8111
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 66804600000 | 48944.833 | 09-JAN-17:30 | 34382.155 | 10771.038 | 308.585 | 315.771 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 59623000000 | 48813.359 | 21-FEB-17:40 | 34382.155 | 10771.038 | 129.096 | 0 | 363.785 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 67271100000 | 55228.59 | 29-MAR-15:39 | 34382.155 | 10771.038 | 7960.025 | 0 | 2115.372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 62698900000 | 55455.874 | 29-APR-13:00 | 34382.155 | 10771.038 | 8351.143 | 0 | 1951.538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 65742700000 | 56317.226 | 04-MAY-14:00 | 34382.155 | 10771.038 | 3544.833 | 0 | 7619.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 65724700000 | 60829.85 | 28-JUN-14:00 | 34382.155 | 10771.038 | 4885.96 | 0 | 10790.697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 69799200000 | 68349.698 | 24-JUL-14:00 | 34382.155 | 10771.038 | 6998.236 | 0 | 16198.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 73342300000 | 66273.103 | 07-AUG-14:00 | 34382.155 | 10771.038 | 6483.829 | 0 | 14636.081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 66251300000 | 79233.664 | 02-SEP-15:00 | 34382.155 | 10771.038 | 9903.465 | 0 | 24177.006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 64855800000 | 54793.506 | 17-OCT-13:50 | 34382.155 | 10771.038 | 7537.585 | 0 | 2102.728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 63712500000 | 51342.069 | 04-NOV-16:49 | 34382.155 | 10771.038 | 1700.372 | 0 | 1321.22 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 66681700000 | 49050.918 | 13-DEC-17:00 | 34382.155 | 10771.038 | 404.352 | 326.089 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 792508000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 59623000000 | 48813.359 |  | 34382.155 | 10771.038 | 129.096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 73342300000 | 79233.664 |  | 34382.155 | 10771.038 | 9903.465 | 326.089 | 24177.006 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 15920.59 | 2055.89 | 0 | 17976.48
Cost per Total Building Area ($/m2) | 6.94 | 0.9 | 0 | 7.84
Cost per Net Conditioned Building Area ($/m2) | 6.94 | 0.9 | 0 | 7.84

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1241.41 | 541.16 | 541.16
Net Site Energy | 1241.41 | 541.16 | 541.16
Total Source Energy | 3481.16 | 1517.51 | 1517.51
Net Source Energy | 3481.16 | 1517.51 | 1517.51
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 4.25 | 375.26 | 0 | 0 | 0 | 0
Cooling | 73.15 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 49.76 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 39.89 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 866.15 | 375.26 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 8.61 | 27.86 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 18.29 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 21.52
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 11.84 | 6.19 | 0
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 379.89 | 90 | 180
BACK_SPACE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 379.89 | 90 | 0
CORE_RETAIL_WALL_WEST_2 | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 178.43 | 270 | 90 | W
CORE_RETAIL_WALL_EAST_2 | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 178.43 | 90 | 90 | E
CORE_RETAIL_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1600.48 | 180 | 0
POINT_OF_SALE_WALL_SOUTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 180 | 0
FRONT_RETAIL_WALLL_EAST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 36.58 | 90 | 90 | E
FRONT_RETAIL_WALL_SOUTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 153.22 | 180 | 90 | S
FRONT_RETAIL_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 90 | 0
FRONT_ENTRY_WALL_SOUTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 12 | 180 | 180
FRONT_ENTRY_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
POINT_OF_SALE_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 38.05 | 38.05 | 3.18 | 0.402 | 0.495 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 38.05 | 38.05 | 3.18 | 0.402 | 0.495 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
FRONT_ENTRY_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 7.83 | 7.83 | 3.18 | 0.402 | 0.495 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 3.18 | 0.402 | 0.495
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 35368.88 | 24343.36 | 11025.52 | 0.69 | 3.46
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 144707.49 | 97834.3 | 46873.18 | 0.68 | 3.51
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 22645.05 | 16188.49 | 6456.56 | 0.71 | 3.55
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19652.48 | 13740.85 | 5911.63 | 0.7 | 3.51
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 2783.84 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 47641.31 | 0.8
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 198317.65 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 28045.27 | 0.8
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 28045.98 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.12 | 11.33 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.5 | 1635.12 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 5.83 | 10932.09 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.06 | 1203.3 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.87 | 986.57 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 28921.9161 | 47.779 | 129.1655 | 0 | 0.0004 | 29729.0213 | 12068.0799
February | 24403.8071 | 41.2279 | 114.4595 | 0 | 0.0004 | 26345.7008 | 10270.1065
March | 25468.9156 | 44.2021 | 126.4979 | 0 | 0.0004 | 29118.4362 | 10830.6746
April | 22646.2055 | 40.2134 | 117.9348 | 0 | 0.0004 | 27148.5994 | 9717.3429
May | 23856.7518 | 43.1403 | 128.8987 | 0 | 0.0004 | 29673.5472 | 10311.0989
June | 27974.5437 | 50.9362 | 153.2431 | 0 | 0.0005 | 35278.3051 | 12124.273
July | 31434.349 | 57.2387 | 172.2128 | 0 | 0.0005 | 39645.3285 | 13624.0365
August | 31191.1304 | 56.7956 | 170.8792 | 0 | 0.0005 | 39338.3209 | 13518.6047
September | 25211.6069 | 45.8713 | 137.9034 | 0 | 0.0004 | 31746.8763 | 10923.5438
October | 23231.522 | 41.6807 | 123.5482 | 0 | 0.0004 | 28441.3893 | 10009.4119
November | 23593.2643 | 41.3139 | 119.3821 | 0 | 0.0004 | 27480.9643 | 10068.1411
December | 27580.8424 | 46.2697 | 127.4096 | 0 | 0.0004 | 29326.0155 | 11576.0169
Annual Sum or Average | 315514.8549 | 556.6689 | 1621.5347 | 0 | 0.0049 | 373272.5047 | 135041.3307
Minimum of Months | 22646.2055 | 40.2134 | 114.4595 | 0 | 0.0004 | 26345.7008 | 9717.3429
Maximum of Months | 31434.349 | 57.2387 | 172.2128 | 0 | 0.0005 | 39645.3285 | 13624.0365
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 68984000000 | 50876.809 | 27-JAN-09:09 | 34382.155 | 10771.038 | 5392.427 | 331.189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 61133200000 | 49122.884 | 03-FEB-17:00 | 34382.155 | 10771.038 | 527.979 | 274.428 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 67567100000 | 48649.542 | 07-MAR-17:00 | 34382.155 | 10771.038 | 178.549 | 150.515 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 62996300000 | 58295.887 | 28-APR-14:30 | 34382.155 | 10771.038 | 10654.778 | 0 | 2487.916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 68855200000 | 63791.655 | 30-MAY-15:00 | 34382.155 | 10771.038 | 3794.175 | 0 | 14844.287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 81860600000 | 88494.846 | 08-JUN-12:00 | 34382.155 | 10771.038 | 8400.115 | 0 | 34941.537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 91994000000 | 96107.655 | 13-JUL-14:00 | 34382.155 | 10771.038 | 9748.718 | 0 | 41205.744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 91281600000 | 95403.954 | 04-AUG-15:00 | 34382.155 | 10771.038 | 10010.726 | 0 | 40240.035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 73666200000 | 74699.76 | 05-SEP-14:00 | 34382.155 | 10771.038 | 5886.804 | 0 | 23659.763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 65996100000 | 59091.074 | 28-OCT-13:20 | 34382.155 | 10771.038 | 11166.448 | 0 | 2771.433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 63767500000 | 54708.869 | 02-NOV-16:49 | 34382.155 | 10771.038 | 1372.446 | 0 | 5015.946 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 68048800000 | 49600.131 | 14-DEC-17:00 | 34382.155 | 10771.038 | 871.318 | 408.335 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 866151000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 61133200000 | 48649.542 |  | 34382.155 | 10771.038 | 178.549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 91994000000 | 96107.655 |  | 34382.155 | 10771.038 | 11166.448 | 408.335 | 41205.744 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 12799.94 | 3103.47 | 0 | 15903.41
Cost per Total Building Area ($/m2) | 5.58 | 1.35 | 0 | 6.93
Cost per Net Conditioned Building Area ($/m2) | 5.58 | 1.35 | 0 | 6.93

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1167.88 | 509.1 | 509.1
Net Site Energy | 1167.88 | 509.1 | 509.1
Total Source Energy | 3126.51 | 1362.91 | 1362.91
Net Source Energy | 3126.51 | 1362.91 | 1362.91
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 3.06 | 336.26 | 0 | 0 | 0 | 0
Cooling | 41.59 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 49.73 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 38.15 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 831.62 | 336.26 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 8.61 | 27.86 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 18.29 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 21.52
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 11.84 | 6.19 | 0
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 379.89 | 90 | 180
BACK_SPACE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 379.89 | 90 | 0
CORE_RETAIL_WALL_WEST_2 | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 178.43 | 270 | 90 | W
CORE_RETAIL_WALL_EAST_2 | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 178.43 | 90 | 90 | E
CORE_RETAIL_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1600.48 | 180 | 0
POINT_OF_SALE_WALL_SOUTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 180 | 0
FRONT_RETAIL_WALLL_EAST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 36.58 | 90 | 90 | E
FRONT_RETAIL_WALL_SOUTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 153.22 | 180 | 90 | S
FRONT_RETAIL_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 90 | 0
FRONT_ENTRY_WALL_SOUTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 12 | 180 | 180
FRONT_ENTRY_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
POINT_OF_SALE_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 38.05 | 38.05 | 3.18 | 0.402 | 0.495 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 38.05 | 38.05 | 3.18 | 0.402 | 0.495 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
FRONT_ENTRY_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 7.83 | 7.83 | 3.18 | 0.402 | 0.495 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 3.18 | 0.402 | 0.495
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 26445.38 | 21120.74 | 5324.64 | 0.8 | 3.75
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 80456.8 | 64257.25 | 16199.55 | 0.8 | 4.18
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18778.95 | 14997.9 | 3781.04 | 0.8 | 4.03
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14562.34 | 11630.29 | 2932.05 | 0.8 | 4.03
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 2431.89 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 41367.49 | 0.8
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 167152.41 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 24048.34 | 0.8
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 24047 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.13 | 11.79 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.6 | 1747.14 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 4.86 | 9118.05 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.13 | 1292.34 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.88 | 1002.16 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 21845.958 | 35.0478 | 82.4613 | 0 | 0.0003 | 85726.2899 | 9053.6533
February | 18865.4336 | 30.7575 | 73.8703 | 0 | 0.0003 | 76798.9145 | 7866.6275
March | 20007.0213 | 33.3739 | 82.4277 | 0 | 0.0003 | 85701.1543 | 8416.7277
April | 17925.8496 | 30.5486 | 77.3516 | 0 | 0.0003 | 80428.0096 | 7604.5992
May | 18314.6868 | 31.6173 | 81.2274 | 0 | 0.0003 | 84460.7138 | 7809.3868
June | 18856.8848 | 32.9965 | 86.0308 | 0 | 0.0003 | 89458.1831 | 8084.0507
July | 21670.2238 | 38.0212 | 99.4171 | 0 | 0.0004 | 103378.4492 | 9300.1306
August | 22069.8687 | 38.7221 | 101.2492 | 0 | 0.0004 | 105283.5233 | 9471.6196
September | 18472.9797 | 32.2562 | 83.9087 | 0 | 0.0003 | 87251.1433 | 7912.7526
October | 18491.9284 | 31.6671 | 80.6269 | 0 | 0.0003 | 83834.6575 | 7859.8344
November | 19049.9156 | 31.684 | 77.9792 | 0 | 0.0003 | 81075.3316 | 8004.927
December | 21828.7028 | 35.0016 | 82.2956 | 0 | 0.0003 | 85553.8952 | 9044.6798
Annual Sum or Average | 237399.4531 | 401.6937 | 1008.8457 | 0 | 0.004 | 1048950 | 100428.9892
Minimum of Months | 17925.8496 | 30.5486 | 73.8703 | 0 | 0.0003 | 76798.9145 | 7604.5992
Maximum of Months | 22069.8687 | 38.7221 | 101.2492 | 0 | 0.0004 | 105283.5233 | 9471.6196
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 67964800000 | 50458.627 | 06-JAN-09:09 | 34382.155 | 10771.038 | 5149.527 | 155.907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 60887100000 | 50565.412 | 15-FEB-09:09 | 34382.155 | 10771.038 | 4571.801 | 840.418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 67944900000 | 56269.681 | 27-MAR-15:09 | 34382.155 | 10771.038 | 8859.408 | 0 | 2257.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 63764300000 | 56462.052 | 27-APR-13:30 | 34382.155 | 10771.038 | 9525.865 | 0 | 1782.994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 66961500000 | 60876.892 | 23-MAY-15:00 | 34382.155 | 10771.038 | 4857.047 | 0 | 10866.652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 70923500000 | 72529.386 | 27-JUN-15:00 | 34382.155 | 10771.038 | 8172.794 | 0 | 19203.399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 81959700000 | 82201.26 | 17-JUL-15:00 | 34382.155 | 10771.038 | 10879.572 | 0 | 26168.495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 83470000000 | 81839.359 | 30-AUG-13:00 | 34382.155 | 10771.038 | 10528.9 | 0 | 26157.265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 69173800000 | 71614.591 | 02-SEP-15:50 | 34382.155 | 10771.038 | 7982.937 | 0 | 18478.462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 66465100000 | 58463.751 | 05-OCT-14:00 | 34382.155 | 10771.038 | 4067.413 | 0 | 9243.144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 64277500000 | 50960.847 | 04-NOV-16:00 | 34382.155 | 10771.038 | 1329.563 | 0 | 1310.807 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 67828200000 | 50627.088 | 11-DEC-09:09 | 34382.155 | 10771.038 | 4840.967 | 632.927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 831620000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 60887100000 | 50458.627 |  | 34382.155 | 10771.038 | 1329.563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 83470000000 | 82201.26 |  | 34382.155 | 10771.038 | 10879.572 | 840.418 | 26168.495 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 8723.12 | 2314.82 | 0 | 11037.94
Cost per Total Building Area ($/m2) | 3.8 | 1.01 | 0 | 4.81
Cost per Net Conditioned Building Area ($/m2) | 3.8 | 1.01 | 0 | 4.81

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1416.87 | 617.65 | 617.65
Net Site Energy | 1416.87 | 617.65 | 617.65
Total Source Energy | 3565.33 | 1554.2 | 1554.2
Net Source Energy | 3565.33 | 1554.2 | 1554.2
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 5.76 | 556.28 | 0 | 0 | 0 | 0
Cooling | 62.87 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 49.73 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 43.14 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 860.6 | 556.28 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 8.61 | 27.86 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 18.29 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 21.52
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 11.84 | 6.19 | 0
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 379.89 | 90 | 180
BACK_SPACE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 379.89 | 90 | 0
CORE_RETAIL_WALL_WEST_2 | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 178.43 | 270 | 90 | W
CORE_RETAIL_WALL_EAST_2 | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 178.43 | 90 | 90 | E
CORE_RETAIL_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1600.48 | 180 | 0
POINT_OF_SALE_WALL_SOUTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 180 | 0
FRONT_RETAIL_WALLL_EAST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 36.58 | 90 | 90 | E
FRONT_RETAIL_WALL_SOUTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 153.22 | 180 | 90 | S
FRONT_RETAIL_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 90 | 0
FRONT_ENTRY_WALL_SOUTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 12 | 180 | 180
FRONT_ENTRY_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
POINT_OF_SALE_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 38.05 | 38.05 | 3.18 | 0.402 | 0.495 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 38.05 | 38.05 | 3.18 | 0.402 | 0.495 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
FRONT_ENTRY_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 7.83 | 7.83 | 3.18 | 0.402 | 0.495 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 3.18 | 0.402 | 0.495
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 36651.47 | 25796.48 | 10854.99 | 0.7 | 3.49
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 142366.7 | 96251.74 | 46114.96 | 0.68 | 3.51
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 23165.06 | 16315.76 | 6849.3 | 0.7 | 3.52
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18817.93 | 13411.76 | 5406.17 | 0.71 | 3.76
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 3095.66 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 52381.37 | 0.8
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 222381.75 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 31109.62 | 0.8
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 31110.63 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.14 | 12.69 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.64 | 1796.9 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 5.73 | 10755.25 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.04 | 1185.17 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.87 | 992.3 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 24376.724 | 36.5004 | 46.9147 | 0 | 0.0004 | 30809.7349 | 9810.738
February | 19223.6083 | 30.0459 | 41.1051 | 0 | 0.0003 | 27001.6756 | 7857.3878
March | 17848.1317 | 29.8812 | 44.6277 | 0 | 0.0003 | 29325.902 | 7484.9279
April | 14895.4013 | 26.1628 | 41.2336 | 0 | 0.0003 | 27100.9908 | 6363.7477
May | 15593.2066 | 28.2081 | 45.8342 | 0 | 0.0003 | 30127.9626 | 6740.2158
June | 17717.03 | 32.3288 | 52.9845 | 0 | 0.0004 | 34829.0835 | 7684.8889
July | 19204.0237 | 35.0437 | 57.4365 | 0 | 0.0004 | 37755.6061 | 8330.0307
August | 19632.0017 | 35.8248 | 58.7168 | 0 | 0.0004 | 38597.1987 | 8515.6803
September | 14975.8639 | 27.1992 | 44.3708 | 0 | 0.0003 | 29166.4581 | 6483.6779
October | 15390.3755 | 27.1171 | 42.8803 | 0 | 0.0003 | 28183.5885 | 6583.3302
November | 16953.1879 | 28.4026 | 42.4542 | 0 | 0.0003 | 27897.7413 | 7111.5034
December | 21815.2946 | 33.836 | 45.7981 | 0 | 0.0003 | 30083.1263 | 8891.7898
Annual Sum or Average | 217624.8493 | 370.5506 | 564.3564 | 0 | 0.0042 | 370879.0684 | 91857.9182
Minimum of Months | 14895.4013 | 26.1628 | 41.1051 | 0 | 0.0003 | 27001.6756 | 6363.7477
Maximum of Months | 24376.724 | 36.5004 | 58.7168 | 0 | 0.0004 | 38597.1987 | 9810.738
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 71491700000 | 51926.676 | 06-JAN-09:09 | 34382.155 | 10771.038 | 6174.042 | 599.441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 62655400000 | 50552.957 | 04-FEB-10:09 | 34382.155 | 10771.038 | 4704.955 | 694.809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 68048500000 | 49358.085 | 01-MAR-17:00 | 34382.155 | 10771.038 | 622.799 | 414.809 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 62885800000 | 56700.772 | 14-APR-16:00 | 34382.155 | 10771.038 | 9716.408 | 0 | 1831.171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 69909700000 | 80621.623 | 27-MAY-14:00 | 34382.155 | 10771.038 | 6780.562 | 0 | 28687.868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 80818300000 | 89635.469 | 29-JUN-14:00 | 34382.155 | 10771.038 | 8719.696 | 0 | 35762.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 87609000000 | 96517.471 | 15-JUL-14:00 | 34382.155 | 10771.038 | 10183.159 | 0 | 41181.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 89561900000 | 89428.511 | 25-AUG-15:00 | 34382.155 | 10771.038 | 8841.456 | 0 | 35433.862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 67678600000 | 69019.992 | 14-SEP-14:00 | 34382.155 | 10771.038 | 4844.805 | 0 | 19021.994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 65397900000 | 58059.105 | 07-OCT-15:39 | 34382.155 | 10771.038 | 2715.228 | 0 | 10190.683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 64734600000 | 49883.206 | 02-NOV-16:00 | 34382.155 | 10771.038 | 297.519 | 0 | 1265.209 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 69805600000 | 50854.4 | 30-DEC-17:00 | 34382.155 | 10771.038 | 2192.817 | 341.106 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 860597000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 62655400000 | 49358.085 |  | 34382.155 | 10771.038 | 297.519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 89561900000 | 96517.471 |  | 34382.155 | 10771.038 | 10183.159 | 694.809 | 41181.12 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 15141.59 | 4397.66 | 0 | 19539.25
Cost per Total Building Area ($/m2) | 6.6 | 1.92 | 0 | 8.52
Cost per Net Conditioned Building Area ($/m2) | 6.6 | 1.92 | 0 | 8.52

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1339.09 | 583.74 | 583.74
Net Site Energy | 1339.09 | 583.74 | 583.74
Total Source Energy | 3406.4 | 1484.92 | 1484.92
Net Source Energy | 3406.4 | 1484.92 | 1484.92
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 5.09 | 523.61 | 0 | 0 | 0 | 0
Cooling | 25.72 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 49.71 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 35.86 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 815.48 | 523.61 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 8.61 | 27.86 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 18.29 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 21.52
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 11.84 | 6.19 | 0
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 379.89 | 90 | 180
BACK_SPACE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 379.89 | 90 | 0
CORE_RETAIL_WALL_WEST_2 | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 178.43 | 270 | 90 | W
CORE_RETAIL_WALL_EAST_2 | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 178.43 | 90 | 90 | E
CORE_RETAIL_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1600.48 | 180 | 0
POINT_OF_SALE_WALL_SOUTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 180 | 0
FRONT_RETAIL_WALLL_EAST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 36.58 | 90 | 90 | E
FRONT_RETAIL_WALL_SOUTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 153.22 | 180 | 90 | S
FRONT_RETAIL_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 90 | 0
FRONT_ENTRY_WALL_SOUTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 12 | 180 | 180
FRONT_ENTRY_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
POINT_OF_SALE_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 38.05 | 38.05 | 3.18 | 0.402 | 0.495 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 38.05 | 38.05 | 3.18 | 0.402 | 0.495 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
FRONT_ENTRY_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 7.83 | 7.83 | 3.18 | 0.402 | 0.495 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 3.18 | 0.402 | 0.495
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 30092.2 | 24033.29 | 6058.91 | 0.8 | 3.75
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 76052.18 | 60739.47 | 15312.71 | 0.8 | 4.18
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18574.65 | 14834.74 | 3739.91 | 0.8 | 4.03
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15259.78 | 12187.3 | 3072.48 | 0.8 | 4.03
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 3007.14 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 50684.09 | 0.8
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 211293.77 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 29841.62 | 0.8
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 29843.4 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.15 | 13.8 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.82 | 1988.07 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 4.59 | 8618.88 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.12 | 1278.28 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.92 | 1050.16 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 23452.8105 | 35.6919 | 52.1975 | 0 | 0.0004 | 1237460 | 9509.363
February | 19427.9651 | 30.3803 | 46.1823 | 0 | 0.0003 | 1095020 | 7956.071
March | 18870.0518 | 31.101 | 50.6175 | 0 | 0.0004 | 1200480 | 7881.5896
April | 16395.2508 | 27.7702 | 46.6845 | 0 | 0.0003 | 1107330 | 6920.2364
May | 16305.4932 | 28.2294 | 48.6396 | 0 | 0.0003 | 1153790 | 6941.4378
June | 16425.645 | 28.9275 | 50.7701 | 0 | 0.0004 | 1204400 | 7039.9539
July | 18128.7896 | 32.1762 | 56.9361 | 0 | 0.0004 | 1350710 | 7794.0149
August | 17931.1501 | 31.8047 | 56.2405 | 0 | 0.0004 | 1334210 | 7707.0445
September | 15870.6143 | 27.808 | 48.541 | 0 | 0.0003 | 1151500 | 6788.3439
October | 16817.7542 | 28.6865 | 48.6132 | 0 | 0.0003 | 1153100 | 7117.9644
November | 17965.7888 | 29.5623 | 48.0174 | 0 | 0.0003 | 1138800 | 7499.2356
December | 22223.8653 | 34.3967 | 51.5423 | 0 | 0.0004 | 1222040 | 9066.6596
Annual Sum or Average | 219815.1786 | 366.5347 | 604.982 | 0 | 0.0042 | 14348900 | 92221.9146
Minimum of Months | 15870.6143 | 27.7702 | 46.1823 | 0 | 0.0003 | 1095020 | 6788.3439
Maximum of Months | 23452.8105 | 35.6919 | 56.9361 | 0 | 0.0004 | 1350710 | 9509.363
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 70328000000 | 51887.825 | 06-JAN-09:09 | 34382.155 | 10771.038 | 5777.492 | 957.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 62232700000 | 50654.968 | 27-FEB-09:09 | 34382.155 | 10771.038 | 5160.482 | 341.293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 68226100000 | 49341.162 | 03-MAR-09:09 | 34382.155 | 10771.038 | 3534.378 | 653.592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 62932000000 | 49261.501 | 14-APR-15:50 | 34382.155 | 10771.038 | 2663.258 | 0 | 1445.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 65572800000 | 55963.413 | 15-MAY-15:30 | 34382.155 | 10771.038 | 9180.111 | 0 | 1630.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 68449200000 | 75049.115 | 30-JUN-15:00 | 34382.155 | 10771.038 | 8736.247 | 0 | 21159.675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 76764300000 | 78905.559 | 21-JUL-15:00 | 34382.155 | 10771.038 | 9908.87 | 0 | 23843.496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 75826300000 | 70909.002 | 09-AUG-15:00 | 34382.155 | 10771.038 | 7628.592 | 0 | 18127.217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 65442700000 | 62118.066 | 02-SEP-15:00 | 34382.155 | 10771.038 | 5143.931 | 0 | 11820.942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 65533600000 | 52703.583 | 05-OCT-15:09 | 34382.155 | 10771.038 | 5243.291 | 0 | 2307.099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 64721000000 | 48806.677 | 27-NOV-17:00 | 34382.155 | 10771.038 | 263.182 | 223.018 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 69451700000 | 51976.101 | 11-DEC-09:09 | 34382.155 | 10771.038 | 6168.522 | 654.386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 815480000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 62232700000 | 48806.677 |  | 34382.155 | 10771.038 | 263.182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 76764300000 | 78905.559 |  | 34382.155 | 10771.038 | 9908.87 | 957.14 | 23843.496 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 17362.39 | 4205.13 | 0 | 21567.52
Cost per Total Building Area ($/m2) | 7.57 | 1.83 | 0 | 9.4
Cost per Net Conditioned Building Area ($/m2) | 7.57 | 1.83 | 0 | 9.4

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1589.18 | 692.76 | 692.76
Net Site Energy | 1589.18 | 692.76 | 692.76
Total Source Energy | 3638.18 | 1585.96 | 1585.96
Net Source Energy | 3638.18 | 1585.96 | 1585.96
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 7.29 | 777.76 | 0 | 0 | 0 | 0
Cooling | 19.28 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 49.69 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 36.07 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 811.43 | 777.76 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 8.61 | 27.86 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 18.29 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 21.52
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 11.84 | 6.19 | 0
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 379.89 | 90 | 180
BACK_SPACE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 379.89 | 90 | 0
CORE_RETAIL_WALL_WEST_2 | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 178.43 | 270 | 90 | W
CORE_RETAIL_WALL_EAST_2 | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 178.43 | 90 | 90 | E
CORE_RETAIL_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1600.48 | 180 | 0
POINT_OF_SALE_WALL_SOUTH | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 180 | 0
FRONT_RETAIL_WALLL_EAST | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 36.58 | 90 | 90 | E
FRONT_RETAIL_WALL_SOUTH | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 153.22 | 180 | 90 | S
FRONT_RETAIL_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 90 | 0
FRONT_ENTRY_WALL_SOUTH | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 12 | 180 | 180
FRONT_ENTRY_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
POINT_OF_SALE_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 38.05 | 38.05 | 3.18 | 0.501 | 0.49 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 38.05 | 38.05 | 3.18 | 0.501 | 0.49 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
FRONT_ENTRY_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 7.83 | 7.83 | 3.18 | 0.501 | 0.49 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 3.18 | 0.501 | 0.49
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 3.18 | 0.501 | 0.49
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 34111.47 | 25166.97 | 8944.5 | 0.74 | 3.58
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 95768.35 | 67491.79 | 28276.56 | 0.7 | 3.64
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18253.37 | 13988.54 | 4264.83 | 0.77 | 3.93
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17064.58 | 12725.86 | 4338.72 | 0.75 | 3.85
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 3222.53 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 53937.87 | 0.8
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 232058.55 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 32279.09 | 0.8
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 32279.68 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.15 | 13.5 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.72 | 1880.5 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 4.31 | 8080.88 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.01 | 1145.81 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.88 | 1005.36 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 25360.6604 | 37.4199 | 47.0052 | 0 | 0.0004 | 30865.9631 | 10153.8022
February | 21684.2834 | 32.511 | 41.8703 | 0 | 0.0003 | 27497.1873 | 8731.1606
March | 19980.2705 | 32.0481 | 45.3916 | 0 | 0.0003 | 29821.717 | 8245.0021
April | 15944.664 | 27.1813 | 41.4537 | 0 | 0.0003 | 27242.3055 | 6733.2157
May | 15343.6932 | 27.0216 | 42.707 | 0 | 0.0003 | 28069.6566 | 6562.0934
June | 14738.3873 | 26.6517 | 43.289 | 0 | 0.0003 | 28454.9017 | 6369.7612
July | 16260.7784 | 29.6334 | 48.5051 | 0 | 0.0004 | 31884.4867 | 7049.5817
August | 16093.738 | 29.2327 | 47.6934 | 0 | 0.0003 | 31350.5506 | 6967.9626
September | 14577.6794 | 26.0433 | 41.7821 | 0 | 0.0003 | 27463.238 | 6269.928
October | 15993.0785 | 27.6887 | 42.963 | 0 | 0.0003 | 28236.0389 | 6794.2745
November | 18622.9312 | 30.1142 | 43.1001 | 0 | 0.0003 | 28317.3486 | 7708.1371
December | 23785.6655 | 35.8125 | 46.4193 | 0 | 0.0004 | 30485.5224 | 9591.7086
Annual Sum or Average | 218385.8298 | 361.3586 | 532.1798 | 0 | 0.004 | 349688.9165 | 91176.6278
Minimum of Months | 14577.6794 | 26.0433 | 41.4537 | 0 | 0.0003 | 27242.3055 | 6269.928
Maximum of Months | 25360.6604 | 37.4199 | 48.5051 | 0 | 0.0004 | 31884.4867 | 10153.8022
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 71622100000 | 51673.231 | 09-JAN-17:00 | 34382.155 | 10771.038 | 2791.464 | 561.289 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 63805200000 | 51299.34 | 01-FEB-17:00 | 34382.155 | 10771.038 | 2627.559 | 351.304 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 69199000000 | 49723.844 | 09-MAR-17:00 | 34382.155 | 10771.038 | 1068.762 | 334.605 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 63213700000 | 48350.862 | 03-APR-08:09 | 34382.155 | 10771.038 | 2888.86 | 308.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 65133500000 | 55732.577 | 27-MAY-14:20 | 34382.155 | 10771.038 | 8386.308 | 0 | 2193.076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 66027500000 | 66267.966 | 14-JUN-14:00 | 34382.155 | 10771.038 | 4967.073 | 0 | 16147.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 73985500000 | 81299.493 | 08-JUL-15:30 | 34382.155 | 10771.038 | 8411.924 | 0 | 27734.376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 72746600000 | 77986.419 | 12-AUG-14:00 | 34382.155 | 10771.038 | 7482.423 | 0 | 25350.803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 63726400000 | 60911.214 | 07-SEP-14:00 | 34382.155 | 10771.038 | 3787.302 | 0 | 11970.718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 65519600000 | 54604.156 | 07-OCT-15:30 | 34382.155 | 10771.038 | 2272.679 | 0 | 7178.285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 65708300000 | 50301.86 | 24-NOV-17:00 | 34382.155 | 10771.038 | 1622.435 | 358.947 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 70739400000 | 50883.218 | 30-DEC-17:00 | 34382.155 | 10771.038 | 2257.27 | 305.471 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 811427000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 63213700000 | 48350.862 |  | 34382.155 | 10771.038 | 1068.762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 73985500000 | 81299.493 |  | 34382.155 | 10771.038 | 8411.924 | 561.289 | 27734.376 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 13864 | 6137.89 | 0 | 20001.89
Cost per Total Building Area ($/m2) | 6.04 | 2.68 | 0 | 8.72
Cost per Net Conditioned Building Area ($/m2) | 6.04 | 2.68 | 0 | 8.72

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2299.98 | 1002.61 | 1002.61
Net Site Energy | 2299.98 | 1002.61 | 1002.61
Total Source Energy | 4540.68 | 1979.38 | 1979.38
Net Source Energy | 4540.68 | 1979.38 | 1979.38
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 13.29 | 1481.79 | 0 | 0 | 0 | 0
Cooling | 6.15 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 49.38 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 50.27 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 818.19 | 1481.79 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 8.61 | 27.86 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 18.29 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 21.52
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 11.84 | 6.19 | 0
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 379.89 | 90 | 180
BACK_SPACE_ROOF | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 379.89 | 90 | 0
CORE_RETAIL_WALL_WEST_2 | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 178.43 | 270 | 90 | W
CORE_RETAIL_WALL_EAST_2 | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 178.43 | 90 | 90 | E
CORE_RETAIL_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 1600.48 | 180 | 0
POINT_OF_SALE_WALL_SOUTH | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 150.81 | 180 | 0
FRONT_RETAIL_WALLL_EAST | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 36.58 | 90 | 90 | E
FRONT_RETAIL_WALL_SOUTH | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 153.22 | 180 | 90 | S
FRONT_RETAIL_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 150.81 | 90 | 0
FRONT_ENTRY_WALL_SOUTH | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | UNHEATED - 4IN SLAB WITHOUT CARPET_EXT-SLAB | 0.3 | 3.12 | 12.9 | 12 | 180 | 180
FRONT_ENTRY_ROOF | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 12 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
POINT_OF_SALE_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 38.05 | 38.05 | 2.58 | 0.504 | 0.49 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 38.05 | 38.05 | 2.58 | 0.504 | 0.49 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
FRONT_ENTRY_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 7.83 | 7.83 | 2.58 | 0.504 | 0.49 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 2.58 | 0.504 | 0.49
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 2.58 | 0.504 | 0.49
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 34823.69 | 27812.13 | 7011.57 | 0.8 | 3.74
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 87240.08 | 69674.75 | 17565.33 | 0.8 | 4.18
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17307.18 | 13822.47 | 3484.71 | 0.8 | 4.04
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17307.18 | 13822.47 | 3484.71 | 0.8 | 4.04
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 4019.93 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 69137.07 | 0.78
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 300708.09 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 40756.78 | 0.8
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 40756.78 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.18 | 16.25 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.1 | 2300.66 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 5.27 | 9886.79 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.05 | 1191.06 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.05 | 1191.06 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 33155.5957 | 35.3972 | 110.9736 | 0 | 0.0004 | 22254.8197 | 12290.7465
February | 27568.7764 | 29.671 | 97.2607 | 0 | 0.0004 | 19506.3483 | 10256.3964
March | 22764.4837 | 25.5308 | 101.869 | 0 | 0.0004 | 20436.8926 | 8627.6257
April | 15929.6796 | 18.7632 | 90.0667 | 0 | 0.0003 | 18073.4551 | 6175.4271
May | 13474.9176 | 16.5268 | 89.8898 | 0 | 0.0003 | 18040.4626 | 5324.5831
June | 12576.0644 | 15.6387 | 88.378 | 0 | 0.0003 | 17737.7494 | 5002.3883
July | 12741.3022 | 15.9005 | 90.7186 | 0 | 0.0003 | 18207.6975 | 5076.7905
August | 13323.9996 | 16.5291 | 92.8042 | 0 | 0.0003 | 18625.9837 | 5293.7907
September | 13683.4542 | 16.6684 | 88.8928 | 0 | 0.0003 | 17840.0036 | 5389.42
October | 17587.9378 | 20.5472 | 95.9015 | 0 | 0.0003 | 19243.6629 | 6792.2346
November | 24868.068 | 27.4201 | 101.4523 | 0 | 0.0004 | 20351.0377 | 9352.5686
December | 29728.0571 | 32.197 | 109.1064 | 0 | 0.0004 | 21883.3331 | 11090.8112
Annual Sum or Average | 237402.3364 | 270.79 | 1157.3134 | 0 | 0.0041 | 232201.4463 | 90672.7825
Minimum of Months | 12576.0644 | 15.6387 | 88.378 | 0 | 0.0003 | 17737.7494 | 5002.3883
Maximum of Months | 33155.5957 | 35.3972 | 110.9736 | 0 | 0.0004 | 22254.8197 | 12290.7465
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 78417300000 | 57261.509 | 13-JAN-09:09 | 34382.155 | 10771.038 | 7526.772 | 1414.26 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 68732700000 | 56684.153 | 03-FEB-09:09 | 34382.155 | 10771.038 | 7071.28 | 1292.395 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 72011600000 | 51460.592 | 14-MAR-08:09 | 34382.155 | 10771.038 | 5424.295 | 883.104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 63683800000 | 49033.239 | 03-APR-08:09 | 34382.155 | 10771.038 | 3288.117 | 591.929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 63567500000 | 51692.542 | 25-MAY-14:39 | 34382.155 | 10771.038 | 4273.462 | 0 | 2265.888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 62500900000 | 58023.503 | 09-JUN-14:50 | 34382.155 | 10771.038 | 10288.795 | 0 | 2581.515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 64156800000 | 59230.318 | 29-JUL-15:00 | 34382.155 | 10771.038 | 4145.049 | 0 | 9932.076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 65630700000 | 58577.017 | 12-AUG-14:50 | 34382.155 | 10771.038 | 10441.182 | 0 | 2982.642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 62861200000 | 47604.283 | 09-SEP-15:50 | 34382.155 | 10771.038 | 637.302 | 0 | 1813.788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 67807100000 | 52747.151 | 27-OCT-08:09 | 34382.155 | 10771.038 | 3653.833 | 772.84 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 71709100000 | 53909.197 | 09-NOV-09:09 | 34382.155 | 10771.038 | 4661.67 | 927.05 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 77108300000 | 56335.947 | 29-DEC-09:09 | 34382.155 | 10771.038 | 6744.713 | 1270.756 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 818187000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 62500900000 | 47604.283 |  | 34382.155 | 10771.038 | 637.302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 78417300000 | 59230.318 |  | 34382.155 | 10771.038 | 10441.182 | 1414.26 | 9932.076 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 22450.41 | 6089.74 | 0 | 28540.15
Cost per Total Building Area ($/m2) | 9.79 | 2.65 | 0 | 12.44
Cost per Net Conditioned Building Area ($/m2) | 9.79 | 2.65 | 0 | 12.44

## Picture
DOE Commercial Building Benchmark - Retail
Back_Space
Core_Retail
Front_Entry
Point_of_Sale
Front_Retail

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | 11.15 | 70.85 | 3694.32
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | 9.85
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 5.25
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | 7.2 | 46.3 | 2414.21
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | 7.5
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 2.8
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | 13.7 | 89.4 | 4661.57
|  |  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15 | 12.15
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 8.75
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.22 | 0.64 | 0.74 | 0.68 | 0.68 | 0.71 | 0.72 | 0.72 | 0.73 | 0.68 | 0.68 | 0.58 | 0.54 | 0 | 0 | 0 | 8.44 | 52.69 | 2747.41
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.21 | 0.56 | 0.66 | 0.68 | 0.68 | 0.69 | 0.7 | 0.69 | 0.66 | 0.58 | 0.47 | 0.43 | 0.43 | 0.08 | 0 | 0 | 7.61
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.13 | 0.35 | 0.37 | 0.37 | 0.39 | 0.41 | 0.38 | 0.34 | 0.03 | 0 | 0 | 0 | 0 | 0 | 2.88
INFIL_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 9 | 68 | 3545.71
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 15
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 16.5 | 118 | 6152.86
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19.5
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0.23 | 0.13 | 0.08 | 6.62 | 44.59 | 2325.05
|  |  | Sat, WinterDesign | 0.11 | 0.1 | 0.08 | 0.06 | 0.06 | 0.06 | 0.07 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0.16 | 0.13 | 6.9
|  |  | Sun, Hol, Other | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07 | 0.1 | 0.12 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.1 | 0.06 | 4.59
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 102 | 5318.57
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 11
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 102 | 5318.57
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 11
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 455.4 | 3171.6 | 165376.29
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8
|  |  | Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 433.8
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 630 | 4428 | 230888.57
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 654
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 102 | 5318.57
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 11
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FRONT_ENTRY_COOLING | Temperature | Through 12/31 | All | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400 | 16800 | 876000