## BuildingSummary
Building Summary Small Hotel new construction version 1.1_3.1
|  | Value | Data Source
Program
| Building Name | Small Hotel
| Available Fuel Types | gas, electricity
| Principal Building Activity | Lodging
Form
| Total Floor Area (m2) | 4013.63 | PNNL - 17875 Technical Support Document: The Development of the Advanced Energy Design Guide for Highway Lodging Buildings
| Building Shape | Rectangle
| Aspect Ratio | 3
| Number of Floors | 4
Window Fraction (Window to Wall Ratio)
| South | 0.1524
| East | 0.0313
| North | 0.1139
| West | 0.0395
| Total | 0.1087
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | core zone with four perimeter zones on each floor
| Floor to Ceiling Height (m) | 3.35 1st floor, 2.74 upper floors
| Floor to Floor Height (m) | 3.35 1st floor, 2.74 upper floors
| Roof type | Insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel frame | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1694.66
| Net Dimensions - Total Area (m2) | 1510.43
| Wall to Skin Ratio | 0.62811
Roof
| Construction Type | Insulation entirely above deck | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1003.3894
| Net Dimensions - Total Area (m2) | 1003.3894
| Roof to Skin Ratio | 0.37189
Window Dimensions (m2)
| South | 96.83
| East | 6.62
| North | 72.38
| West | 8.38
| Total Area (m2) | 184.21
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab w/carpet
| Dimensions - Total Area (m2) | 1661
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
Dimensions - Total Area (m2)
Internal Mass
| Construction | 15 cm wood
Dimensions - Total Area (m2)
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) |  | See Benchmark Technical Report
HVAC
| System Type | MZ-VAV | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | PACU | 2003 CBECS
| Fan Control | Variable | 2003 CBECS
Service Water Heating
| SWH Type | gas water heater
| Fuel | gas
| Thermal Efficiency (%) | 80
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 3470.09

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
REARSTAIRSFLR1 | Yes | 1 | 20.07 | 67.3 | 3.3533 | 35.77 | 0 |  | 0 | 6.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57847
CORRIDORFLR1 | Yes | 1 | 150.51 | 504.62 | 3.3527 | 32.7 | 9.82 |  | 0 | 5.38 | 0 | 0 | 0 | 0 | 0.25 | 37.6275 | 0 | 0.070528
REARSTORAGEFLR1 | No | 1 | 20.07 | 67.3 | 3.3533 | 35.77 | 0 |  | 0 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57847
FRONTLOUNGEFLR1 | Yes | 1 | 163.06 | 546.7 | 3.3528 | 94.02 | 14.83 | 3.08 | 52.9416 | 11.8 | 15.4333 | 0 | 0 | 8 | 0 | 423.5325 | 0 | 0.18717
RESTROOMFLR1 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 0 | 32.61 | 1 | 9.7 | 10.7631 | 0 | 0 | 0 | 0 | 0 | 200 | 0.13229
MEETINGROOMFLR1 | Yes | 1 | 80.27 | 269.14 | 3.3529 | 32.7 | 4.94 | 1.87 | 42.9251 | 14 | 12.9 | 0 | 0 | 10 | 0 | 429.2513 | 0 | 0.13223
MECHANICALROOMFLR1 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 0 |  | 0 | 16.16 | 0 | 0 | 0 | 0 | 0.25 | 8.1525 | 0 | 0.13229
GUESTROOM101 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 1.64 | 21.74 | 1.5 | 26.9 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.13229
GUESTROOM102 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 1.64 | 21.74 | 1.5 | 26.9 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.13229
GUESTROOM103 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 1.65 | 21.74 | 1.5 | 26.9 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.13229
GUESTROOM104 | Yes | 1 | 32.61 | 109.33 | 3.3527 | 13.29 | 1.65 | 21.74 | 1.5 | 26.9 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.1323
GUESTROOM105 | Yes | 1 | 32.61 | 109.33 | 3.3527 | 13.29 | 1.64 | 21.74 | 1.5 | 26.9 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.1323
EMPLOYEELOUNGEFLR1 | Yes | 1 | 32.61 | 109.33 | 3.3527 | 13.29 | 1.64 | 2.96 | 11.0169 | 12.9 | 77.1567 | 0 | 0 | 8 | 0 | 88.1351 | 0 | 0.1323
LAUNDRYROOMFLR1 | Yes | 1 | 97.83 | 327.99 | 3.3527 | 39.86 | 4.94 | 8.89 | 11.0045 | 7.5 | 437.5594 | 184.2477 | 255.5145 | 13 | 0 | 143.0585 | 0 | 0.13227
ELEVATORCOREFLR1 | No | 1 | 15.05 | 50.46 | 3.3528 | 6.13 | 0 |  | 0 | 0 | 128.3696 | 0 | 0 | 0 | 5 | 75.25 | 0 | 0.13222
EXERCISECENTERFLR1 | Yes | 1 | 32.61 | 109.33 | 3.3527 | 13.29 | 1.65 | 2.96 | 11.0169 | 9.7 | 11.4999 | 0 | 0 | 10 | 0 | 110.1689 | 0 | 0.1323
FRONTOFFICEFLR1 | Yes | 1 | 130.44 | 437.33 | 3.3527 | 53.14 | 6.58 | 13.04 | 10.0031 | 11.84 | 12.9 | 0 | 0 | 10 | 0 | 100.0307 | 0 | 0.13225
FRONTSTAIRSFLR1 | Yes | 1 | 20.07 | 67.28 | 3.3523 | 35.77 | 0 |  | 0 | 6.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57864
FRONTSTORAGEFLR1 | No | 1 | 12.54 | 42.05 | 3.3533 | 5.11 | 0 |  | 0 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13226
REARSTAIRSFLR2 | Yes | 1 | 20.07 | 55.06 | 2.7434 | 29.27 | 0 |  | 0 | 6.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57858
CORRIDORFLR2 | Yes | 1 | 125.42 | 344.05 | 2.7432 | 18.39 | 2.62 |  | 0 | 5.38 | 0 | 0 | 0 | 0 | 0.25 | 31.355 | 0 | 0.058175
REARSTORAGEFLR2 | No | 1 | 20.07 | 55.07 | 2.7439 | 29.27 | 0 |  | 0 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57847
GUESTROOM201 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 33.45 | 1.64 | 21.74 | 1.5 | 26.9 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.40695
GUESTROOM202_205 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 26.9 | 14.3 | 0 | 26.4978 | 0 | 0 | 56.628 | 0 | 0.13224
GUESTROOM206_208 | Yes | 1 | 105.36 | 289.02 | 2.7432 | 35.12 | 6.7 | 23.41 | 4.5006 | 26.9 | 14.3 | 0 | 19.8734 | 0 | 0 | 42.471 | 0 | 0.13225
GUESTROOM209_212 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 26.9 | 14.3 | 0 | 26.4978 | 0 | 0 | 56.628 | 0 | 0.13224
GUESTROOM213 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 10.87 | 1.65 | 21.74 | 1.5 | 26.9 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.13224
GUESTROOM214 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 26.9 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.13226
GUESTROOM215_218 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 26.9 | 14.3 | 0 | 26.4978 | 0 | 0 | 56.628 | 0 | 0.13226
ELEVATORCOREFLR2 | No | 1 | 15.05 | 41.29 | 2.7435 | 5.02 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13232
GUESTROOM219 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 26.9 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.13226
GUESTROOM220_223 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 26.9 | 14.3 | 0 | 26.4978 | 0 | 0 | 56.628 | 0 | 0.13226
GUESTROOM224 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.64 | 21.74 | 1.5 | 26.9 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.13226
FRONTSTORAGEFLR2 | No | 1 | 12.54 | 34.41 | 2.744 | 4.18 | 0 |  | 0 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13221
FRONTSTAIRSFLR2 | Yes | 1 | 20.07 | 55.05 | 2.7429 | 29.26 | 0 |  | 0 | 6.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57849
REARSTAIRSFLR3 | Yes | 1 | 20.07 | 55.06 | 2.7434 | 29.27 | 0 |  | 0 | 6.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57858
CORRIDORFLR3 | Yes | 1 | 125.42 | 344.05 | 2.7432 | 18.39 | 2.62 |  | 0 | 5.38 | 0 | 0 | 0 | 0 | 0.25 | 31.355 | 0 | 0.058175
REARSTORAGEFLR3 | No | 1 | 20.07 | 55.07 | 2.7439 | 29.27 | 0 |  | 0 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57847
GUESTROOM301 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 33.45 | 1.64 | 21.74 | 1.5 | 26.9 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.40695
GUESTROOM302_305 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 26.9 | 14.3 | 0 | 26.4978 | 0 | 0 | 56.628 | 0 | 0.13224
GUESTROOM306_308 | Yes | 1 | 105.36 | 289.02 | 2.7432 | 35.12 | 6.7 | 23.41 | 4.5006 | 26.9 | 14.3 | 0 | 19.8734 | 0 | 0 | 42.471 | 0 | 0.13225
GUESTROOM309_312 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 26.9 | 14.3 | 0 | 26.4978 | 0 | 0 | 56.628 | 0 | 0.13224
GUESTROOM313 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 10.87 | 1.65 | 21.74 | 1.5 | 26.9 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.13224
GUESTROOM314 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 26.9 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.13226
GUESTROOM315_318 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 26.9 | 14.3 | 0 | 26.4978 | 0 | 0 | 56.628 | 0 | 0.13226
ELEVATORCOREFLR3 | No | 1 | 15.05 | 41.29 | 2.7435 | 5.02 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13232
GUESTROOM319 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 26.9 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.13226
GUESTROOM320_323 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 26.9 | 14.3 | 0 | 26.4978 | 0 | 0 | 56.628 | 0 | 0.13226
GUESTROOM324 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.64 | 21.74 | 1.5 | 26.9 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.13226
FRONTSTORAGEFLR3 | No | 1 | 12.54 | 34.41 | 2.744 | 4.18 | 0 |  | 0 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13221
FRONTSTAIRSFLR3 | Yes | 1 | 20.07 | 55.05 | 2.7429 | 29.26 | 0 |  | 0 | 6.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57849
REARSTAIRSFLR4 | Yes | 1 | 20.07 | 55.06 | 2.7434 | 29.27 | 0 |  | 0 | 6.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9753
CORRIDORFLR4 | Yes | 1 | 125.42 | 344.05 | 2.7432 | 18.39 | 2.62 |  | 0 | 5.38 | 0 | 0 | 0 | 0 | 0.25 | 31.355 | 0 | 0.45493
REARSTORAGEFLR4 | No | 1 | 20.07 | 55.07 | 2.7439 | 29.27 | 0 |  | 0 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97512
GUESTROOM401 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 33.45 | 1.64 | 21.74 | 1.5 | 26.9 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.80368
GUESTROOM402_405 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 26.9 | 14.3 | 0 | 26.4978 | 0 | 0 | 56.628 | 0 | 0.52901
GUESTROOM406_408 | Yes | 1 | 105.36 | 289.02 | 2.7432 | 35.12 | 6.7 | 23.41 | 4.5006 | 26.9 | 14.3 | 0 | 19.8734 | 0 | 0 | 42.471 | 0 | 0.52901
GUESTROOM409_412 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 26.9 | 14.3 | 0 | 26.4978 | 0 | 0 | 56.628 | 0 | 0.52901
GUESTROOM413 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 10.87 | 1.65 | 21.74 | 1.5 | 26.9 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.52898
GUESTROOM414 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 26.9 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.52903
GUESTROOM415_418 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 26.9 | 14.3 | 0 | 26.4978 | 0 | 0 | 56.628 | 0 | 0.52902
ELEVATORCOREFLR4 | No | 1 | 15.05 | 41.29 | 2.7435 | 5.02 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52903
GUESTROOM419 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 26.9 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.52903
GUESTROOM420_423 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 26.9 | 14.3 | 0 | 26.4978 | 0 | 0 | 56.628 | 0 | 0.52902
GUESTROOM424 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.64 | 21.74 | 1.5 | 26.9 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.52903
FRONTSTORAGEFLR4 | No | 1 | 12.54 | 34.41 | 2.744 | 4.18 | 0 |  | 0 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52884
FRONTSTAIRSFLR4 | Yes | 1 | 20.07 | 55.05 | 2.7429 | 29.26 | 0 |  | 0 | 6.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97528
Total Conditioned Zones |  |  | 4013.63 | 11621.75 |  | 1694.66 | 184.23 |  | 255.4127
Data Source | [7 empty] | 1 |  | 2 | 4 |  | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] PNNL - 17875 Technical Support Document: The Development of the Advanced Energy Design Guide for Highway Lodging Buildings

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7A | 8A
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fabric
Exterior walls
| Construction Type | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame
| R-value (m2·K / W) | 1.4205 | 1.4205 | 1.4205 | 2.0964 | 2.0964 | 2.0964 | 2.0964 | 2.7473 | 2.7473 | 2.7473 | 2.7473 | 2.7473 | 2.7473 | 2.7473 | 2.7473 | 3.1949
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 3.663
Window
| U-Factor (W / m2·K) | 6.49 | 6.49 | 6.49 | 3.18 | 3.18 | 3.18 | 6.49 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 2.58
| SHGC | 0.25 | 0.391 | 0.391 | 0.402 | 0.402 | 0.402 | 0.61 | 0.402 | 0.402 | 0.402 | 0.501 | 0.501 | 0.501 | 0.501 | 0.501 | 0.504
| Visible transmittance | 0.25 | 0.39 | 0.39 | 0.495 | 0.495 | 0.495 | 0.61 | 0.495 | 0.495 | 0.495 | 0.622 | 0.622 | 0.622 | 0.622 | 0.49 | 0.49
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| GUESTROOM101 PTAC DXCOIL | 1.8596 | 2.0136 | 2.0007 | 1.8757 | 1.7038 | 1.7369 | 1.746 | 1.8343 | 1.779 | 1.5953 | 1.846 | 1.8399 | 1.8193 | 1.8298 | 1.5987 | 1.5281
| GUESTROOM102 PTAC DXCOIL | 1.885 | 2.0469 | 2.046 | 1.907 | 1.7415 | 1.7763 | 1.7927 | 1.8661 | 1.8201 | 1.6351 | 1.8798 | 1.8845 | 1.8544 | 1.8765 | 1.6402 | 1.5741
| GUESTROOM103 PTAC DXCOIL | 2.0458 | 2.2239 | 2.2862 | 2.0298 | 1.8442 | 1.9291 | 1.8128 | 1.9572 | 1.9178 | 1.6735 | 1.9519 | 1.9443 | 1.9263 | 1.9278 | 1.674 | 1.575
| GUESTROOM104 PTAC DXCOIL | 2.0776 | 2.0944 | 2.0356 | 1.8343 | 1.4701 | 1.7874 | 1.1827 | 1.7307 | 1.8103 | 1.2481 | 1.6777 | 1.7116 | 1.6184 | 1.6152 | 1.3791 | 1.1945
| GUESTROOM105 PTAC DXCOIL | 2.0638 | 2.0608 | 1.9388 | 1.8518 | 1.5421 | 1.763 | 1.311 | 1.77 | 1.8982 | 1.3671 | 1.7314 | 1.8392 | 1.6756 | 1.743 | 1.5168 | 1.3568
| GUESTROOM201 PTAC DXCOIL | 2.7237 | 2.91 | 3.2755 | 2.5121 | 2.3373 | 2.8592 | 2.5459 | 2.2924 | 2.6784 | 2.2703 | 2.31 | 2.6487 | 2.3393 | 2.5763 | 2.2786 | 2.3158
| GUESTROOM202_205 PTAC DXCOIL | 8.1333 | 8.8335 | 9.5737 | 8.4467 | 7.9761 | 8.7968 | 9.139 | 8.3982 | 9.067 | 8.3032 | 8.5357 | 9.3984 | 8.4718 | 9.3884 | 8.437 | 8.7749
| GUESTROOM206_208 PTAC DXCOIL | 6.3768 | 6.9913 | 7.6578 | 6.7171 | 6.499 | 7.1446 | 7.6279 | 6.7179 | 7.3554 | 6.825 | 6.8536 | 7.6893 | 6.9418 | 7.7326 | 6.9444 | 7.3065
| GUESTROOM209_212 PTAC DXCOIL | 7.9547 | 8.6383 | 9.3255 | 8.2513 | 7.7299 | 8.5213 | 8.8481 | 8.1962 | 8.7863 | 8.0329 | 8.325 | 9.1001 | 8.2571 | 9.0855 | 8.1636 | 8.4715
| GUESTROOM213 PTAC DXCOIL | 2.263 | 2.4682 | 2.7649 | 2.3127 | 2.1837 | 2.521 | 2.4126 | 2.2673 | 2.4909 | 2.2126 | 2.2851 | 2.5274 | 2.2974 | 2.5134 | 2.2508 | 2.3104
| GUESTROOM214 PTAC DXCOIL | 2.3379 | 2.3817 | 2.6406 | 2.1745 | 1.8438 | 2.4539 | 1.7247 | 2.0549 | 2.4285 | 1.7745 | 2.0341 | 2.3182 | 2.0709 | 2.2286 | 1.9753 | 1.9019
| GUESTROOM215_218 PTAC DXCOIL | 8.7442 | 8.8297 | 9.1371 | 8.1302 | 7.1213 | 8.775 | 6.9216 | 7.9101 | 9.2215 | 7.02 | 7.8197 | 9.0114 | 7.8537 | 8.6203 | 7.7323 | 7.5007
| GUESTROOM219 PTAC DXCOIL | 2.5652 | 2.5876 | 2.8012 | 2.5125 | 2.2653 | 2.7155 | 2.2091 | 2.3901 | 2.8756 | 2.2344 | 2.4098 | 2.8196 | 2.4531 | 2.7037 | 2.4241 | 2.3735
| GUESTROOM220_223 PTAC DXCOIL | 8.2228 | 8.3015 | 8.4703 | 7.6046 | 6.4775 | 8.0539 | 6.2519 | 7.3849 | 8.4141 | 6.353 | 7.298 | 8.2041 | 7.1792 | 7.8541 | 7.0308 | 6.8013
| GUESTROOM224 PTAC DXCOIL | 2.3072 | 2.3346 | 2.5333 | 2.1386 | 1.855 | 2.3725 | 1.7572 | 2.0454 | 2.4005 | 1.7918 | 2.0191 | 2.3092 | 2.0442 | 2.2082 | 1.9724 | 1.8887
| GUESTROOM301 PTAC DXCOIL | 2.7123 | 2.882 | 3.2798 | 2.496 | 2.3028 | 2.8606 | 2.5023 | 2.277 | 2.6661 | 2.2405 | 2.2848 | 2.6235 | 2.3131 | 2.5422 | 2.2493 | 2.2966
| GUESTROOM302_305 PTAC DXCOIL | 8.1273 | 8.824 | 9.6271 | 8.4418 | 7.9322 | 8.8687 | 9.118 | 8.3916 | 9.0949 | 8.2976 | 8.522 | 9.3979 | 8.4532 | 9.3801 | 8.4405 | 8.8088
| GUESTROOM306_308 PTAC DXCOIL | 6.4775 | 7.1093 | 7.8659 | 6.8425 | 6.6353 | 7.3914 | 7.8291 | 6.8512 | 7.5646 | 7.0152 | 6.9878 | 7.8922 | 7.1159 | 7.9389 | 7.1417 | 7.561
| GUESTROOM309_312 PTAC DXCOIL | 8.1183 | 8.8135 | 9.6123 | 8.4342 | 7.9221 | 8.8579 | 9.1056 | 8.3847 | 9.0856 | 8.2865 | 8.5143 | 9.387 | 8.4451 | 9.3683 | 8.4302 | 8.7958
| GUESTROOM313 PTAC DXCOIL | 2.3121 | 2.5245 | 2.8652 | 2.3727 | 2.2412 | 2.64 | 2.4871 | 2.3316 | 2.5903 | 2.2883 | 2.3446 | 2.6152 | 2.3706 | 2.5992 | 2.3322 | 2.4098
| GUESTROOM314 PTAC DXCOIL | 2.3917 | 2.4426 | 2.7643 | 2.2562 | 1.9056 | 2.5829 | 1.7911 | 2.1182 | 2.5357 | 1.8507 | 2.1137 | 2.4117 | 2.1503 | 2.3206 | 2.0618 | 1.9965
| GUESTROOM315_318 PTAC DXCOIL | 8.4916 | 8.5907 | 8.9309 | 7.8934 | 6.7969 | 8.547 | 6.6075 | 7.6749 | 8.89 | 6.7267 | 7.5857 | 8.6538 | 7.5516 | 8.2938 | 7.4424 | 7.2348
| GUESTROOM319 PTAC DXCOIL | 2.2222 | 2.252 | 2.3835 | 2.0681 | 1.8096 | 2.2778 | 1.7568 | 2.0017 | 2.3567 | 1.7878 | 1.9848 | 2.2915 | 2.0011 | 2.1954 | 1.9681 | 1.904
| GUESTROOM320_323 PTAC DXCOIL | 8.3912 | 8.4871 | 8.794 | 7.7944 | 6.684 | 8.4098 | 6.4964 | 7.5779 | 8.7404 | 6.6117 | 7.4911 | 8.5095 | 7.4275 | 8.154 | 7.3171 | 7.1103
| GUESTROOM324 PTAC DXCOIL | 2.3502 | 2.3847 | 2.6452 | 2.203 | 1.8995 | 2.4861 | 1.8135 | 2.0949 | 2.4852 | 1.8505 | 2.0734 | 2.3799 | 2.1051 | 2.2771 | 2.0391 | 1.9644
| GUESTROOM401 PTAC DXCOIL | 3.3379 | 3.5739 | 4.1616 | 3.1564 | 2.7964 | 3.6467 | 2.841 | 2.8149 | 3.3618 | 2.6526 | 2.8056 | 3.2035 | 2.7797 | 3.0655 | 2.6646 | 2.4476
| GUESTROOM402_405 PTAC DXCOIL | 10.2469 | 11.0523 | 12.136 | 10.5185 | 9.6151 | 11.6152 | 10.2534 | 10.3559 | 11.5369 | 9.7812 | 10.3459 | 11.406 | 10.1803 | 11.2722 | 9.9479 | 9.4029
| GUESTROOM406_408 PTAC DXCOIL | 8.2153 | 8.9445 | 9.9977 | 8.5245 | 7.9947 | 9.605 | 8.7562 | 8.4504 | 9.5147 | 8.2164 | 8.487 | 9.509 | 8.5516 | 9.4739 | 8.3668 | 8.0584
| GUESTROOM409_412 PTAC DXCOIL | 10.2691 | 11.0796 | 12.135 | 10.5247 | 9.6218 | 11.6242 | 10.2595 | 10.3649 | 11.5465 | 9.7894 | 10.3543 | 11.4169 | 10.1906 | 11.2825 | 9.9573 | 9.4117
| GUESTROOM413 PTAC DXCOIL | 2.9028 | 3.1424 | 3.6495 | 2.9632 | 2.7115 | 3.4278 | 2.7935 | 2.8723 | 3.305 | 2.7038 | 2.8483 | 3.1771 | 2.863 | 3.1253 | 2.7473 | 2.5689
| GUESTROOM414 PTAC DXCOIL | 3.0398 | 3.1579 | 3.7176 | 2.986 | 2.4367 | 3.4764 | 2.166 | 2.7772 | 3.3392 | 2.2988 | 2.7233 | 3.0826 | 2.7015 | 2.9091 | 2.5342 | 2.2461
| GUESTROOM415_418 PTAC DXCOIL | 10.797 | 11.114 | 12.2063 | 10.2853 | 8.6539 | 11.6112 | 7.9238 | 9.78 | 11.6622 | 8.3033 | 9.536 | 10.9865 | 9.4799 | 10.3516 | 9.1141 | 8.078
| GUESTROOM419 PTAC DXCOIL | 2.8081 | 2.894 | 3.2428 | 2.7085 | 2.2705 | 3.0697 | 2.0568 | 2.5352 | 3.059 | 2.1652 | 2.497 | 2.8689 | 2.4781 | 2.7014 | 2.3718 | 2.0717
| GUESTROOM420_423 PTAC DXCOIL | 10.7254 | 11.0433 | 12.1104 | 10.2026 | 8.585 | 11.5199 | 7.8603 | 9.7178 | 11.5656 | 8.2354 | 9.4764 | 10.8971 | 9.4013 | 10.2649 | 9.0372 | 8.0017
| GUESTROOM424 PTAC DXCOIL | 2.9974 | 3.1009 | 3.599 | 2.9331 | 2.4314 | 3.3757 | 2.1877 | 2.7314 | 3.2818 | 2.2984 | 2.6811 | 3.0459 | 2.6607 | 2.8672 | 2.5149 | 2.2073
| PSZ-HEATCOOL:1_COOLC DXCOIL | 13.1932 | 13.7776 | 12.603 | 13.5784 | 8.1557 | 9.7866 | 7.1223 | 12.778 | 9.5847 | 7.5166 | 12.8661 | 9.5725 | 13.1055 | 9.1776 | 10.7292 | 7.0163
| PSZ-HEATCOOL:2_COOLC DXCOIL | 19.3496 | 21.0948 | 21.6663 | 21.0423 | 14.9166 | 18.3957 | 15.0195 | 20.5446 | 15.3629 | 15.344 | 21.3415 | 15.9167 | 21.9279 | 15.816 | 18.3986 | 13.8973
| PSZ-HEATCOOL:3_COOLC DXCOIL | 1.9387 | 2.0077 | 1.7113 | 1.8144 | 1.3238 | 1.4307 | 1.2629 | 1.7571 | 1.3745 | 1.2018 | 1.7541 | 1.3864 | 1.6732 | 1.3534 | 1.3481 | 1.0961
| PSZ-HEATCOOL:4_COOLC DXCOIL | 10.3472 | 10.9806 | 11.596 | 11.072 | 8.1179 | 11.0963 | 7.5166 | 10.7381 | 8.1498 | 8.685 | 11.0348 | 8.3441 | 11.2734 | 8.1656 | 10.8972 | 7.0445
| PSZ-HEATCOOL:5_COOLC DXCOIL | 2.2108 | 2.2108 | 2.2108 | 2.2108 | 1.6324 | 2.2108 | 1.4738 | 2.2108 | 1.4738 | 1.7398 | 2.2108 | 1.4738 | 2.2108 | 1.4738 | 2.2108 | 1.4738
| PSZ-HEATCOOL:6_COOLC DXCOIL | 7.4158 | 7.2507 | 6.2814 | 6.7893 | 5.1332 | 5.7092 | 4.857 | 6.6362 | 6.2668 | 4.9823 | 6.634 | 6.2151 | 6.3197 | 5.8967 | 5.5746 | 5.0012
| PSZ-HEATCOOL:7_COOLC DXCOIL | 27.0743 | 26.6448 | 25.9052 | 26.1383 | 24.7539 | 26.5011 | 23.6415 | 25.6582 | 29.6222 | 24.2958 | 25.7002 | 29.4727 | 25.3794 | 27.8421 | 25.2824 | 23.9594
| PSZ-HEATCOOL:8_COOLC DXCOIL | 3.414 | 3.4932 | 3.2794 | 3.4569 | 2.1862 | 2.4773 | 1.7937 | 3.211 | 2.4485 | 1.8667 | 3.2004 | 2.4183 | 3.3166 | 2.3608 | 2.8173 | 1.911
| PSZ-HEATCOOL:9_COOLC DXCOIL | 9.0655 | 8.8858 | 7.5347 | 7.8895 | 5.4731 | 6.2847 | 4.5131 | 7.5944 | 6.6359 | 4.748 | 7.4487 | 6.3847 | 7.0699 | 6.0175 | 5.7097 | 4.5319
| PSZ-HEATCOOL:10_COOLC DXCOIL | 8.5025 | 8.5025 | 8.5025 | 8.5025 | 6.2134 | 8.1614 | 5.6679 | 8.5025 | 5.6679 | 6.6339 | 8.5025 | 5.6679 | 8.5025 | 5.6679 | 8.5025 | 5.6679
| PSZ-HEATCOOL:11_COOLC DXCOIL | 8.5025 | 8.5025 | 8.5025 | 8.5025 | 6.1082 | 7.8923 | 5.6679 | 8.5025 | 5.6679 | 6.5767 | 8.5025 | 5.6679 | 8.5025 | 5.6679 | 8.5025 | 5.6679
| PSZ-HEATCOOL:12_COOLC DXCOIL | 9.5711 | 10.6032 | 12.0208 | 10.0658 | 6.0529 | 9.9169 | 5.6679 | 9.3193 | 7.4111 | 6.3956 | 9.2278 | 6.9104 | 9.0319 | 6.5117 | 8.5025 | 5.6679
Heating (kW)
| REARSTAIRSFLR1 UNIT HEATER COIL | 0 | 0.11264 | 0 | 0.14041 | 0 | 0 | 0 | 0.19443 | 0.08668 | 0 | 0.50008 | 0.35532 | 0.68087 | 0.65208 | 0.77046 | 1.2044
| REARSTORAGEFLR1 UNIT HEATER COIL | 0 | 0.06344 | 0 | 0.05411 | 0 | 0 | 0 | 0.06638 | 0 | 0 | 0.2811 | 0.20524 | 0.4057 | 0.40433 | 0.47164 | 0.73751
| GUESTROOM101 PTAC HEAT COIL | 0.55593 | 0.81148 | 0.68686 | 0.84742 | 0.57819 | 0.73416 | 0.63909 | 0.95072 | 0.81984 | 0.76215 | 1.238 | 1.0654 | 1.4039 | 1.3473 | 1.4823 | 1.8866
| GUESTROOM102 PTAC HEAT COIL | 0.55593 | 0.83454 | 0.707 | 0.86842 | 0.57819 | 0.75303 | 0.63909 | 0.97213 | 0.84086 | 0.76913 | 1.2612 | 1.0881 | 1.428 | 1.3715 | 1.507 | 1.9115
| GUESTROOM103 PTAC HEAT COIL | 0.55593 | 1.0477 | 0.90137 | 1.079 | 0.57819 | 0.94935 | 0.76715 | 1.1788 | 1.0466 | 0.94792 | 1.4795 | 1.3051 | 1.6532 | 1.5988 | 1.7355 | 2.1478
| GUESTROOM104 PTAC HEAT COIL | 0.55593 | 1.0377 | 0.89626 | 1.0783 | 0.57819 | 0.95888 | 0.76265 | 1.1793 | 1.0461 | 0.96494 | 1.4775 | 1.3043 | 1.6483 | 1.5939 | 1.73 | 2.1469
| GUESTROOM105 PTAC HEAT COIL | 0.55593 | 0.82647 | 0.70249 | 0.86799 | 0.57819 | 0.75468 | 0.63909 | 0.97284 | 0.84046 | 0.76877 | 1.2633 | 1.091 | 1.4298 | 1.3736 | 1.5092 | 1.92
| FRONTSTAIRSFLR1 UNIT HEATER COIL | 0 | 0.20024 | 0.04007 | 0.23817 | 0 | 0.09665 | 0 | 0.29179 | 0.18299 | 0.07678 | 0.61134 | 0.46123 | 0.79714 | 0.76654 | 0.89024 | 1.3392
| FRONTSTORAGEFLR1 UNIT HEATER COIL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| REARSTAIRSFLR2 UNIT HEATER COIL | 0 | 0.22384 | 0.03801 | 0.22248 | 0 | 0.05933 | 0 | 0.25425 | 0.14397 | 0.07772 | 0.50706 | 0.3754 | 0.65257 | 0.62165 | 0.72205 | 1.0588
| REARSTORAGEFLR2 UNIT HEATER COIL | 0 | 0.20429 | 0.06553 | 0.17518 | 0 | 0.05875 | 0 | 0.1758 | 0.11283 | 0.04634 | 0.35032 | 0.27558 | 0.45407 | 0.44722 | 0.50637 | 0.70452
| GUESTROOM201 PTAC HEAT COIL | 0.70684 | 1.3124 | 1.0066 | 1.2693 | 0.6436 | 0.99968 | 0.87367 | 1.3488 | 1.1342 | 1.063 | 1.7525 | 1.5004 | 1.9792 | 1.8996 | 2.0854 | 2.574
| GUESTROOM202_205 PTAC HEAT COIL | 2.2237 | 3.3033 | 2.5271 | 3.292 | 2.3128 | 2.6774 | 2.5564 | 3.6438 | 3.0132 | 3.0486 | 4.7208 | 3.9713 | 5.3147 | 5.0361 | 5.5848 | 6.9439
| GUESTROOM206_208 PTAC HEAT COIL | 1.6678 | 2.5514 | 1.9352 | 2.5033 | 1.7346 | 2.0081 | 1.9173 | 2.7843 | 2.2999 | 2.2864 | 3.6443 | 3.061 | 4.1169 | 3.9036 | 4.3354 | 5.3766
| GUESTROOM209_212 PTAC HEAT COIL | 2.2237 | 3.224 | 2.4768 | 3.2303 | 2.3128 | 2.6774 | 2.5564 | 3.583 | 2.9554 | 3.0486 | 4.6437 | 3.8974 | 5.2289 | 4.9486 | 5.494 | 6.8482
| GUESTROOM213 PTAC HEAT COIL | 0.58983 | 1.048 | 0.84381 | 1.0435 | 0.57819 | 0.857 | 0.76766 | 1.1258 | 0.96659 | 0.92531 | 1.4042 | 1.2155 | 1.5571 | 1.4888 | 1.6267 | 1.9712
| GUESTROOM214 PTAC HEAT COIL | 0.55593 | 1.0165 | 0.81661 | 1.014 | 0.57819 | 0.83028 | 0.73233 | 1.0977 | 0.9375 | 0.89859 | 1.3749 | 1.1876 | 1.5273 | 1.459 | 1.598 | 1.9448
| GUESTROOM215_218 PTAC HEAT COIL | 2.2237 | 2.9356 | 2.4768 | 3.1668 | 2.3128 | 2.6774 | 2.5564 | 3.5252 | 2.8009 | 3.0486 | 4.3567 | 3.612 | 4.949 | 4.6676 | 5.2207 | 6.5963
| GUESTROOM219 PTAC HEAT COIL | 0.69491 | 0.7339 | 0.61919 | 0.79169 | 0.69244 | 0.64207 | 0.69466 | 0.88129 | 0.57162 | 0.68508 | 1.0295 | 0.83588 | 1.1126 | 1.0139 | 1.1388 | 1.4497
| GUESTROOM220_223 PTAC HEAT COIL | 2.2237 | 3.0924 | 2.4768 | 3.1668 | 2.3128 | 2.6774 | 2.5564 | 3.5252 | 2.8336 | 3.0486 | 4.5304 | 3.7887 | 5.1157 | 4.8348 | 5.3857 | 6.7555
| GUESTROOM224 PTAC HEAT COIL | 0.55593 | 0.93911 | 0.73979 | 0.93741 | 0.57819 | 0.7524 | 0.67801 | 1.0215 | 0.86136 | 0.82026 | 1.3058 | 1.1157 | 1.4618 | 1.3928 | 1.5341 | 1.8895
| FRONTSTORAGEFLR2 UNIT HEATER COIL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FRONTSTAIRSFLR2 UNIT HEATER COIL | 0 | 0.33481 | 0.14864 | 0.3378 | 0 | 0.1717 | 0.0262 | 0.36945 | 0.257 | 0.18738 | 0.62986 | 0.49366 | 0.7844 | 0.7556 | 0.85917 | 1.2098
| REARSTAIRSFLR3 UNIT HEATER COIL | 0 | 0.25126 | 0.06528 | 0.25243 | 0 | 0.08397 | 0 | 0.2864 | 0.17312 | 0.10866 | 0.54016 | 0.40743 | 0.68613 | 0.65664 | 0.75751 | 1.0937
| REARSTORAGEFLR3 UNIT HEATER COIL | 0 | 0.23351 | 0.09119 | 0.20461 | 0 | 0.08631 | 0 | 0.206 | 0.14063 | 0.0847 | 0.38573 | 0.3096 | 0.49088 | 0.48482 | 0.5437 | 0.74038
| GUESTROOM301 PTAC HEAT COIL | 0.7617 | 1.3578 | 1.0395 | 1.3152 | 0.68559 | 1.034 | 0.90879 | 1.3957 | 1.1755 | 1.1048 | 1.8058 | 1.5506 | 2.0353 | 1.9565 | 2.1427 | 2.6267
| GUESTROOM302_305 PTAC HEAT COIL | 2.2237 | 3.4242 | 2.6114 | 3.4234 | 2.3128 | 2.6774 | 2.5564 | 3.7876 | 3.1384 | 3.0486 | 4.8802 | 4.1206 | 5.4793 | 5.2031 | 5.7516 | 7.0868
| GUESTROOM306_308 PTAC HEAT COIL | 1.6678 | 2.7633 | 2.1054 | 2.7141 | 1.7346 | 2.1202 | 1.9839 | 3.0052 | 2.5029 | 2.3844 | 3.8801 | 3.287 | 4.3563 | 4.1443 | 4.5771 | 5.5941
| GUESTROOM309_312 PTAC HEAT COIL | 2.2237 | 3.4066 | 2.5998 | 3.4114 | 2.3128 | 2.6774 | 2.5564 | 3.7776 | 3.13 | 3.0486 | 4.8646 | 4.1061 | 5.4607 | 5.1837 | 5.7312 | 7.0642
| GUESTROOM313 PTAC HEAT COIL | 0.66593 | 1.0907 | 0.87729 | 1.087 | 0.62153 | 0.89149 | 0.8187 | 1.173 | 1.0088 | 0.96956 | 1.4563 | 1.2648 | 1.6111 | 1.5435 | 1.6817 | 2.0207
| GUESTROOM314 PTAC HEAT COIL | 0.62655 | 1.0654 | 0.855 | 1.0633 | 0.58402 | 0.86901 | 0.78859 | 1.1499 | 0.98482 | 0.94689 | 1.4331 | 1.2428 | 1.5882 | 1.5199 | 1.6598 | 1.999
| GUESTROOM315_318 PTAC HEAT COIL | 2.2237 | 3.3527 | 2.5571 | 3.3644 | 2.3128 | 2.6774 | 2.5564 | 3.73 | 3.0779 | 3.0486 | 4.8213 | 4.067 | 5.4163 | 5.1354 | 5.6895 | 7.0244
| GUESTROOM319 PTAC HEAT COIL | 0.55593 | 0.82009 | 0.61919 | 0.81652 | 0.57819 | 0.66936 | 0.63909 | 0.90934 | 0.73598 | 0.76215 | 1.2008 | 1.0054 | 1.3606 | 1.2907 | 1.4343 | 1.7851
| GUESTROOM320_323 PTAC HEAT COIL | 2.2237 | 3.3453 | 2.555 | 3.3633 | 2.3128 | 2.6774 | 2.5564 | 3.7281 | 3.079 | 3.0486 | 4.8139 | 4.0608 | 5.4058 | 5.1246 | 5.6774 | 7.0102
| GUESTROOM324 PTAC HEAT COIL | 0.5835 | 1.001 | 0.78852 | 1.0018 | 0.57819 | 0.80402 | 0.73421 | 1.0876 | 0.92308 | 0.88403 | 1.3759 | 1.1826 | 1.5334 | 1.4642 | 1.6062 | 1.9522
| FRONTSTORAGEFLR3 UNIT HEATER COIL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FRONTSTAIRSFLR3 UNIT HEATER COIL | 0 | 0.37806 | 0.18346 | 0.38022 | 0 | 0.20962 | 0.08045 | 0.41462 | 0.30043 | 0.23424 | 0.67794 | 0.54104 | 0.83194 | 0.80402 | 0.90688 | 1.2552
| REARSTAIRSFLR4 UNIT HEATER COIL | 0 | 0.58111 | 0.30979 | 0.64766 | 0.02902 | 0.39225 | 0.20691 | 0.76051 | 0.57391 | 0.47088 | 1.1804 | 0.96467 | 1.4318 | 1.3964 | 1.5499 | 2.0974
| REARSTORAGEFLR4 UNIT HEATER COIL | 0.05347 | 0.48223 | 0.2784 | 0.49712 | 0.05012 | 0.315 | 0.17954 | 0.55288 | 0.44332 | 0.34583 | 0.84832 | 0.72881 | 1.0251 | 1.0281 | 1.1099 | 1.42
| GUESTROOM401 PTAC HEAT COIL | 1.0432 | 1.8529 | 1.4353 | 1.8836 | 1.014 | 1.5016 | 1.3012 | 2.0571 | 1.7598 | 1.6305 | 2.6543 | 2.3221 | 3.0011 | 2.9334 | 3.1614 | 3.818
| GUESTROOM402_405 PTAC HEAT COIL | 3.0347 | 5.3819 | 4.1703 | 5.6619 | 3.0694 | 4.512 | 3.9939 | 6.3928 | 5.4304 | 5.0719 | 8.2281 | 7.1532 | 9.2919 | 9.0507 | 9.7734 | 11.8062
| GUESTROOM406_408 PTAC HEAT COIL | 2.464 | 4.3619 | 3.3802 | 4.5405 | 2.4603 | 3.6196 | 3.2464 | 5.1293 | 4.3727 | 4.0715 | 6.6056 | 5.7569 | 7.4576 | 7.2738 | 7.8479 | 9.4286
| GUESTROOM409_412 PTAC HEAT COIL | 3.0335 | 5.3718 | 4.165 | 5.656 | 3.0721 | 4.5096 | 3.9944 | 6.3893 | 5.428 | 5.0719 | 8.22 | 7.1461 | 9.2814 | 9.0397 | 9.7617 | 11.7925
| GUESTROOM413 PTAC HEAT COIL | 0.97706 | 1.5966 | 1.2825 | 1.6662 | 0.98635 | 1.3695 | 1.2268 | 1.848 | 1.6047 | 1.5073 | 2.3201 | 2.0495 | 2.5939 | 2.5368 | 2.7181 | 3.2341
| GUESTROOM414 PTAC HEAT COIL | 0.95456 | 1.5758 | 1.2629 | 1.6474 | 0.96419 | 1.3492 | 1.2058 | 1.8289 | 1.5846 | 1.4866 | 2.3023 | 2.0327 | 2.5762 | 2.5178 | 2.701 | 3.216
| GUESTROOM415_418 PTAC HEAT COIL | 3.022 | 5.3576 | 4.162 | 5.6544 | 3.0628 | 4.5058 | 3.9904 | 6.3876 | 5.4228 | 5.0669 | 8.2212 | 7.1512 | 9.2824 | 9.0355 | 9.7652 | 11.7952
| GUESTROOM419 PTAC HEAT COIL | 0.79746 | 1.4399 | 1.1156 | 1.5192 | 0.80857 | 1.2074 | 1.0608 | 1.7148 | 1.459 | 1.3537 | 2.215 | 1.933 | 2.506 | 2.4479 | 2.6388 | 3.1838
| GUESTROOM420_423 PTAC HEAT COIL | 2.9988 | 5.3265 | 4.1349 | 5.6263 | 3.0429 | 4.4814 | 3.9656 | 6.3587 | 5.3958 | 5.0428 | 8.1866 | 7.118 | 9.2449 | 8.9975 | 9.726 | 11.7533
| GUESTROOM424 PTAC HEAT COIL | 0.90606 | 1.5474 | 1.2308 | 1.6236 | 0.92081 | 1.3259 | 1.1728 | 1.8073 | 1.565 | 1.4713 | 2.2737 | 2.0051 | 2.5438 | 2.4842 | 2.6666 | 3.1783
| FRONTSTORAGEFLR4 UNIT HEATER COIL | 0 | 0.03717 | 0 | 0.05085 | 0 | 0 | 0 | 0.08304 | 0.04348 | 0 | 0.19591 | 0.15455 | 0.26437 | 0.27101 | 0.29642 | 0.40123
| FRONTSTAIRSFLR4 UNIT HEATER COIL | 0.15651 | 0.74121 | 0.45238 | 0.81115 | 0.1732 | 0.54594 | 0.35121 | 0.92454 | 0.73576 | 0.62735 | 1.3511 | 1.1342 | 1.6064 | 1.5733 | 1.726 | 2.2795
| PSZ-HEATCOOL:1_HEATC | 6.1708 | 8.5072 | 7.3262 | 9.0444 | 5.9516 | 7.3123 | 5.7449 | 9.4745 | 8.4708 | 7.2304 | 11.1445 | 10.0988 | 12.2681 | 11.7439 | 11.479 | 12.4887
| PSZ-HEATCOOL:2_HEATC | 9.0503 | 13.0253 | 11.9972 | 14.0159 | 10.2163 | 12.3331 | 12.1149 | 15.2332 | 13.5775 | 13.2378 | 18.4858 | 16.7918 | 20.5267 | 20.2386 | 20.1167 | 24.7367
| PSZ-HEATCOOL:3_HEATC | 0.91582 | 1.245 | 1.0663 | 1.3154 | 0.95889 | 1.1016 | 1.0187 | 1.4045 | 1.1751 | 1.1561 | 1.6591 | 1.4018 | 1.8203 | 1.6838 | 1.6934 | 1.951
| PSZ-HEATCOOL:4_HEATC | 4.8397 | 6.7801 | 6.0409 | 7.3749 | 5.3349 | 6.352 | 6.063 | 7.962 | 7.2026 | 6.8719 | 9.5583 | 8.8029 | 10.553 | 10.4489 | 10.4413 | 12.5389
| PSZ-HEATCOOL:5_HEATC | 1.034 | 1.3651 | 1.1517 | 1.4726 | 1.0755 | 1.245 | 1.1887 | 1.6393 | 1.3025 | 1.4176 | 1.915 | 1.5548 | 2.0695 | 1.8858 | 2.1183 | 2.6232
| PSZ-HEATCOOL:6_HEATC | 4.0506 | 4.4843 | 3.9003 | 4.7857 | 3.4829 | 4.1482 | 3.6993 | 5.1879 | 4.4728 | 4.415 | 6.0048 | 5.1896 | 6.474 | 6.0768 | 6.5738 | 7.9376
| PSZ-HEATCOOL:7_HEATC | 20.874 | 22.4224 | 21.39 | 22.9158 | 20.6017 | 21.7222 | 20.2257 | 23.4283 | 22.5327 | 21.7035 | 24.7635 | 23.6203 | 17.4161 | 16.6303 | 17.4606 | 19.6261
| PSZ-HEATCOOL:8_HEATC | 1.5968 | 2.1569 | 1.879 | 2.3026 | 1.4717 | 1.8732 | 1.4468 | 2.3809 | 2.1639 | 1.7957 | 2.7722 | 2.5513 | 3.1047 | 3.021 | 2.9793 | 3.4015
| PSZ-HEATCOOL:9_HEATC | 4.2714 | 5.4799 | 4.7361 | 5.649 | 3.9091 | 4.7928 | 3.6403 | 6.0623 | 5.0895 | 4.5672 | 7.0032 | 5.8935 | 7.5694 | 6.9524 | 7.4826 | 8.0665
| PSZ-HEATCOOL:10_HEATC | 3.9769 | 5.25 | 4.4294 | 5.6634 | 4.1361 | 4.7883 | 4.5718 | 6.3044 | 5.0092 | 5.4521 | 7.3648 | 5.9795 | 7.9592 | 7.2528 | 8.1469 | 10.0886
| PSZ-HEATCOOL:11_HEATC | 3.9769 | 5.25 | 4.4294 | 5.6634 | 4.1361 | 4.7883 | 4.5718 | 6.3044 | 5.0092 | 5.4521 | 7.3648 | 5.9795 | 7.9592 | 7.2528 | 8.1469 | 10.0886
| PSZ-HEATCOOL:12_HEATC | 4.4767 | 6.5471 | 6.6008 | 6.7047 | 4.1361 | 6.6061 | 4.5718 | 6.91 | 6.5498 | 5.4521 | 7.993 | 7.2904 | 8.4547 | 8.3325 | 8.1469 | 10.0886
HVAC Efficiency
Air Conditioning (COP)
| GUESTROOM101 PTAC DXCOIL | 3.56 | 3.53 | 3.58 | 3.56 | 3.61 | 3.6 | 3.65 | 3.57 | 3.64 | 3.64 | 3.58 | 3.63 | 3.58 | 3.64 | 3.64 | 3.61
| GUESTROOM102 PTAC DXCOIL | 3.56 | 3.53 | 3.57 | 3.55 | 3.65 | 3.59 | 3.63 | 3.56 | 3.62 | 3.63 | 3.57 | 3.62 | 3.58 | 3.62 | 3.63 | 3.65
| GUESTROOM103 PTAC DXCOIL | 3.56 | 3.53 | 3.55 | 3.57 | 3.62 | 3.64 | 3.63 | 3.59 | 3.64 | 3.62 | 3.59 | 3.65 | 3.6 | 3.61 | 3.62 | 3.65
| GUESTROOM104 PTAC DXCOIL | 3.55 | 3.59 | 3.61 | 3.62 | 3.63 | 3.63 | 3.62 | 3.6 | 3.63 | 3.66 | 3.62 | 3.61 | 3.59 | 3.65 | 3.6 | 3.61
| GUESTROOM105 PTAC DXCOIL | 3.56 | 3.56 | 3.64 | 3.61 | 3.61 | 3.64 | 3.64 | 3.59 | 3.6 | 3.61 | 3.6 | 3.62 | 3.62 | 3.61 | 3.61 | 3.61
| GUESTROOM201 PTAC DXCOIL | 3.43 | 3.39 | 3.31 | 3.49 | 3.54 | 3.4 | 3.48 | 3.57 | 3.45 | 3.58 | 3.57 | 3.47 | 3.56 | 3.49 | 3.57 | 3.55
| GUESTROOM202_205 PTAC DXCOIL | 2.94 | 2.95 | 2.97 | 2.96 | 2.98 | 2.98 | 2.98 | 2.96 | 2.99 | 2.98 | 2.96 | 2.99 | 2.98 | 2.98 | 2.99 | 2.99
| GUESTROOM206_208 PTAC DXCOIL | 2.95 | 2.94 | 2.97 | 2.97 | 2.98 | 2.98 | 2.98 | 2.97 | 2.98 | 2.98 | 2.98 | 2.98 | 2.99 | 2.98 | 2.99 | 2.98
| GUESTROOM209_212 PTAC DXCOIL | 2.94 | 2.94 | 2.96 | 2.96 | 2.99 | 2.98 | 2.98 | 2.96 | 2.98 | 2.99 | 2.97 | 2.99 | 2.98 | 2.98 | 2.98 | 2.98
| GUESTROOM213 PTAC DXCOIL | 3.54 | 3.49 | 3.43 | 3.56 | 3.58 | 3.49 | 3.54 | 3.54 | 3.5 | 3.57 | 3.55 | 3.51 | 3.59 | 3.52 | 3.59 | 3.56
| GUESTROOM214 PTAC DXCOIL | 3.51 | 3.52 | 3.47 | 3.59 | 3.62 | 3.52 | 3.61 | 3.61 | 3.53 | 3.64 | 3.61 | 3.55 | 3.61 | 3.58 | 3.63 | 3.6
| GUESTROOM215_218 PTAC DXCOIL | 2.96 | 2.96 | 2.98 | 2.98 | 2.99 | 2.99 | 2.98 | 2.97 | 2.99 | 2.98 | 2.98 | 2.98 | 2.99 | 2.98 | 2.99 | 2.98
| GUESTROOM219 PTAC DXCOIL | 3.47 | 3.46 | 3.42 | 3.49 | 3.58 | 3.43 | 3.59 | 3.52 | 3.39 | 3.56 | 3.54 | 3.41 | 3.54 | 3.45 | 3.54 | 3.53
| GUESTROOM220_223 PTAC DXCOIL | 2.95 | 2.96 | 2.98 | 2.98 | 2.98 | 2.99 | 2.98 | 2.96 | 2.99 | 2.98 | 2.98 | 2.99 | 2.99 | 2.99 | 2.98 | 2.98
| GUESTROOM224 PTAC DXCOIL | 3.52 | 3.54 | 3.48 | 3.61 | 3.61 | 3.53 | 3.6 | 3.61 | 3.55 | 3.63 | 3.61 | 3.56 | 3.62 | 3.59 | 3.63 | 3.6
| GUESTROOM301 PTAC DXCOIL | 3.43 | 3.4 | 3.31 | 3.5 | 3.56 | 3.4 | 3.5 | 3.57 | 3.45 | 3.59 | 3.58 | 3.48 | 3.58 | 3.5 | 3.59 | 3.56
| GUESTROOM302_305 PTAC DXCOIL | 2.94 | 2.95 | 2.96 | 2.96 | 2.99 | 2.99 | 2.98 | 2.96 | 2.99 | 2.98 | 2.97 | 2.99 | 2.98 | 2.98 | 2.99 | 2.98
| GUESTROOM306_308 PTAC DXCOIL | 2.95 | 2.95 | 2.97 | 2.97 | 2.98 | 2.99 | 2.98 | 2.97 | 2.99 | 2.98 | 2.98 | 2.99 | 2.99 | 2.98 | 2.98 | 2.99
| GUESTROOM309_312 PTAC DXCOIL | 2.94 | 2.95 | 2.96 | 2.96 | 2.99 | 2.99 | 2.99 | 2.96 | 2.99 | 2.98 | 2.97 | 2.99 | 2.98 | 2.98 | 2.99 | 2.98
| GUESTROOM313 PTAC DXCOIL | 3.52 | 3.47 | 3.41 | 3.53 | 3.59 | 3.47 | 3.51 | 3.55 | 3.49 | 3.57 | 3.55 | 3.5 | 3.55 | 3.48 | 3.55 | 3.54
| GUESTROOM314 PTAC DXCOIL | 3.52 | 3.49 | 3.44 | 3.58 | 3.65 | 3.49 | 3.64 | 3.62 | 3.48 | 3.61 | 3.62 | 3.54 | 3.62 | 3.57 | 3.6 | 3.62
| GUESTROOM315_318 PTAC DXCOIL | 2.95 | 2.96 | 2.99 | 2.98 | 2.98 | 2.99 | 2.98 | 2.97 | 2.99 | 2.99 | 2.98 | 2.98 | 2.99 | 2.98 | 2.99 | 2.99
| GUESTROOM319 PTAC DXCOIL | 3.56 | 3.55 | 3.52 | 3.6 | 3.63 | 3.57 | 3.6 | 3.62 | 3.53 | 3.63 | 3.62 | 3.57 | 3.63 | 3.59 | 3.63 | 3.65
| GUESTROOM320_323 PTAC DXCOIL | 2.96 | 2.96 | 2.98 | 2.98 | 2.98 | 2.99 | 2.99 | 2.97 | 2.99 | 2.99 | 2.98 | 2.98 | 2.98 | 2.98 | 2.98 | 2.99
| GUESTROOM324 PTAC DXCOIL | 3.54 | 3.52 | 3.46 | 3.57 | 3.6 | 3.51 | 3.63 | 3.63 | 3.51 | 3.62 | 3.64 | 3.52 | 3.64 | 3.59 | 3.61 | 3.63
| GUESTROOM401 PTAC DXCOIL | 3.27 | 3.21 | 3.06 | 3.32 | 3.42 | 3.19 | 3.4 | 3.42 | 3.26 | 3.46 | 3.43 | 3.31 | 3.45 | 3.35 | 3.45 | 3.52
| GUESTROOM402_405 PTAC DXCOIL | 2.96 | 2.96 | 2.98 | 2.98 | 2.98 | 2.98 | 2.99 | 2.97 | 2.99 | 2.98 | 2.97 | 2.98 | 2.98 | 2.99 | 2.98 | 2.99
| GUESTROOM406_408 PTAC DXCOIL | 2.96 | 2.96 | 2.98 | 2.98 | 2.98 | 2.99 | 2.99 | 2.98 | 2.98 | 2.99 | 2.98 | 2.99 | 2.98 | 2.99 | 2.99 | 2.99
| GUESTROOM409_412 PTAC DXCOIL | 2.96 | 2.96 | 2.98 | 2.98 | 2.98 | 2.98 | 2.99 | 2.97 | 2.99 | 2.98 | 2.97 | 2.98 | 2.98 | 2.99 | 2.98 | 2.99
| GUESTROOM413 PTAC DXCOIL | 3.38 | 3.31 | 3.2 | 3.38 | 3.43 | 3.25 | 3.43 | 3.39 | 3.28 | 3.44 | 3.41 | 3.33 | 3.41 | 3.35 | 3.45 | 3.5
| GUESTROOM414 PTAC DXCOIL | 3.34 | 3.32 | 3.16 | 3.37 | 3.53 | 3.23 | 3.61 | 3.43 | 3.27 | 3.56 | 3.43 | 3.35 | 3.45 | 3.39 | 3.48 | 3.59
| GUESTROOM415_418 PTAC DXCOIL | 2.97 | 2.97 | 2.99 | 2.98 | 2.98 | 2.98 | 2.98 | 2.98 | 2.98 | 2.98 | 2.99 | 2.98 | 2.99 | 2.99 | 2.98 | 2.99
| GUESTROOM419 PTAC DXCOIL | 3.39 | 3.38 | 3.31 | 3.43 | 3.58 | 3.36 | 3.61 | 3.48 | 3.34 | 3.59 | 3.5 | 3.39 | 3.52 | 3.45 | 3.53 | 3.64
| GUESTROOM420_423 PTAC DXCOIL | 2.96 | 2.97 | 2.98 | 2.99 | 2.99 | 2.99 | 2.99 | 2.98 | 2.99 | 2.99 | 2.98 | 2.99 | 2.98 | 2.98 | 2.99 | 2.98
| GUESTROOM424 PTAC DXCOIL | 3.36 | 3.34 | 3.21 | 3.39 | 3.53 | 3.25 | 3.59 | 3.45 | 3.29 | 3.56 | 3.45 | 3.34 | 3.47 | 3.41 | 3.49 | 3.57
| PSZ-HEATCOOL:1_COOLC DXCOIL | 3.66 | 3.66 | 3.74 | 3.67 | 4.05 | 3.9 | 4.06 | 3.66 | 4.06 | 4.04 | 3.67 | 4.07 | 3.66 | 4.06 | 3.74 | 4.04
| PSZ-HEATCOOL:2_COOLC DXCOIL | 3.45 | 3.45 | 3.48 | 3.45 | 3.96 | 3.78 | 4.04 | 3.45 | 4.03 | 3.9 | 3.45 | 4.03 | 3.45 | 4.03 | 3.75 | 4.03
| PSZ-HEATCOOL:3_COOLC DXCOIL | 3.68 | 3.66 | 3.9 | 3.73 | 4.06 | 3.96 | 4.12 | 3.76 | 4.01 | 4.01 | 3.76 | 4.01 | 3.81 | 4.04 | 3.88 | 4.13
| PSZ-HEATCOOL:4_COOLC DXCOIL | 3.67 | 3.67 | 3.66 | 3.67 | 3.92 | 3.67 | 4.04 | 3.66 | 4.05 | 3.83 | 3.67 | 4.06 | 3.67 | 4.05 | 3.67 | 4.07
| PSZ-HEATCOOL:5_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.94 | 3.67 | 4.07 | 3.67 | 4.07 | 3.87 | 3.67 | 4.07 | 3.67 | 4.07 | 3.67 | 4.07
| PSZ-HEATCOOL:6_COOLC DXCOIL | 3.74 | 3.76 | 3.92 | 3.81 | 4.06 | 4.04 | 4.05 | 3.81 | 4.06 | 4.05 | 3.81 | 4.07 | 3.85 | 4.04 | 3.99 | 4.05
| PSZ-HEATCOOL:7_COOLC DXCOIL | 3.67 | 3.69 | 3.74 | 3.73 | 3.75 | 3.74 | 3.74 | 3.71 | 3.74 | 3.75 | 3.72 | 3.74 | 3.74 | 3.74 | 3.75 | 3.75
| PSZ-HEATCOOL:8_COOLC DXCOIL | 3.68 | 3.66 | 3.76 | 3.67 | 3.94 | 3.89 | 4.09 | 3.67 | 4.07 | 4.02 | 3.67 | 4.09 | 3.65 | 4.05 | 3.77 | 4.11
| PSZ-HEATCOOL:9_COOLC DXCOIL | 3.73 | 3.77 | 3.96 | 3.81 | 4.05 | 4.06 | 4.07 | 3.77 | 4.05 | 4.07 | 3.78 | 4.07 | 3.84 | 4.07 | 3.93 | 4.04
| PSZ-HEATCOOL:10_COOLC DXCOIL | 3.66 | 3.66 | 3.66 | 3.66 | 3.93 | 3.69 | 4.05 | 3.66 | 4.05 | 3.87 | 3.66 | 4.05 | 3.66 | 4.05 | 3.66 | 4.05
| PSZ-HEATCOOL:11_COOLC DXCOIL | 3.66 | 3.66 | 3.66 | 3.66 | 3.95 | 3.71 | 4.05 | 3.66 | 4.05 | 3.87 | 3.66 | 4.05 | 3.66 | 4.05 | 3.66 | 4.05
| PSZ-HEATCOOL:12_COOLC DXCOIL | 3.67 | 3.67 | 3.7 | 3.67 | 3.96 | 3.79 | 4.05 | 3.67 | 4.06 | 3.9 | 3.66 | 4.07 | 3.66 | 4.05 | 3.66 | 4.05
Heating Efficiency (%)
| REARSTAIRSFLR1 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTORAGEFLR1 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM101 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM102 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM103 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM104 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM105 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTAIRSFLR1 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTORAGEFLR1 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTAIRSFLR2 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTORAGEFLR2 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM201 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM202_205 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM206_208 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM209_212 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM213 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM214 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM215_218 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM219 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM220_223 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM224 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTORAGEFLR2 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTAIRSFLR2 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTAIRSFLR3 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTORAGEFLR3 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM301 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM302_305 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM306_308 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM309_312 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM313 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM314 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM315_318 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM319 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM320_323 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM324 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTORAGEFLR3 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTAIRSFLR3 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTAIRSFLR4 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTORAGEFLR4 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM401 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM402_405 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM406_408 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM409_412 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM413 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM414 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM415_418 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM419 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM420_423 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM424 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTORAGEFLR4 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTAIRSFLR4 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| PSZ-HEATCOOL:1_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:2_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:3_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:4_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:5_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:6_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:7_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:8_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:9_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-HEATCOOL:10_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:11_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:12_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
HVAC Control - Economizer
| All GuestRoom & UnitHeater systems | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
| PSZ-HEATCOOL:1_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:2_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:3_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:4_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:5_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:6_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:7_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:8_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:9_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:10_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:11_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:12_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
Fan Max Flow Rate (m3/s )
| REARSTAIRSFLR1 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0.02 | 0.01 | 0.02 | 0.03 | 0.03 | 0.04
| REARSTORAGEFLR1 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.02 | 0.02 | 0.03
| GUESTROOM101 PTACFAN | 0.1 | 0.1 | 0.11 | 0.1 | 0.1 | 0.1 | 0.11 | 0.1 | 0.11 | 0.1 | 0.1 | 0.11 | 0.1 | 0.11 | 0.1 | 0.09
| GUESTROOM102 PTACFAN | 0.1 | 0.11 | 0.11 | 0.1 | 0.11 | 0.1 | 0.11 | 0.1 | 0.11 | 0.1 | 0.1 | 0.11 | 0.11 | 0.11 | 0.1 | 0.1
| GUESTROOM103 PTACFAN | 0.11 | 0.12 | 0.13 | 0.11 | 0.11 | 0.12 | 0.11 | 0.11 | 0.12 | 0.1 | 0.11 | 0.12 | 0.11 | 0.12 | 0.1 | 0.1
| GUESTROOM104 PTACFAN | 0.11 | 0.12 | 0.12 | 0.11 | 0.09 | 0.11 | 0.07 | 0.1 | 0.11 | 0.08 | 0.1 | 0.1 | 0.1 | 0.1 | 0.08 | 0.07
| GUESTROOM105 PTACFAN | 0.11 | 0.11 | 0.12 | 0.11 | 0.09 | 0.11 | 0.08 | 0.1 | 0.11 | 0.08 | 0.1 | 0.11 | 0.1 | 0.11 | 0.09 | 0.08
| FRONTSTAIRSFLR1 UNIT HEATERFAN | 0 | 0.01 | 0 | 0.01 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0.02 | 0.02 | 0.03 | 0.03 | 0.03 | 0.05
| FRONTSTORAGEFLR1 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| REARSTAIRSFLR2 UNIT HEATERFAN | 0 | 0.01 | 0 | 0.01 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 0.04
| REARSTORAGEFLR2 UNIT HEATERFAN | 0 | 0.01 | 0 | 0.01 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0.01 | 0.01 | 0.02 | 0.02 | 0.02 | 0.02
| GUESTROOM201 PTACFAN | 0.16 | 0.17 | 0.2 | 0.15 | 0.14 | 0.17 | 0.15 | 0.14 | 0.16 | 0.14 | 0.14 | 0.16 | 0.14 | 0.16 | 0.14 | 0.14
| GUESTROOM202_205 PTACFAN | 0.43 | 0.47 | 0.55 | 0.48 | 0.48 | 0.53 | 0.55 | 0.47 | 0.55 | 0.5 | 0.5 | 0.57 | 0.51 | 0.57 | 0.51 | 0.53
| GUESTROOM206_208 PTACFAN | 0.35 | 0.38 | 0.44 | 0.39 | 0.39 | 0.43 | 0.46 | 0.39 | 0.44 | 0.41 | 0.41 | 0.46 | 0.42 | 0.47 | 0.42 | 0.44
| GUESTROOM209_212 PTACFAN | 0.42 | 0.46 | 0.53 | 0.47 | 0.47 | 0.51 | 0.53 | 0.46 | 0.53 | 0.49 | 0.48 | 0.55 | 0.49 | 0.55 | 0.49 | 0.51
| GUESTROOM213 PTACFAN | 0.13 | 0.14 | 0.16 | 0.14 | 0.13 | 0.15 | 0.15 | 0.13 | 0.15 | 0.13 | 0.14 | 0.15 | 0.14 | 0.15 | 0.14 | 0.14
| GUESTROOM214 PTACFAN | 0.13 | 0.14 | 0.16 | 0.13 | 0.11 | 0.15 | 0.1 | 0.12 | 0.15 | 0.11 | 0.12 | 0.14 | 0.13 | 0.13 | 0.12 | 0.11
| GUESTROOM215_218 PTACFAN | 0.49 | 0.5 | 0.55 | 0.49 | 0.43 | 0.53 | 0.42 | 0.46 | 0.56 | 0.42 | 0.47 | 0.54 | 0.47 | 0.52 | 0.47 | 0.45
| GUESTROOM219 PTACFAN | 0.15 | 0.15 | 0.17 | 0.15 | 0.14 | 0.16 | 0.13 | 0.14 | 0.17 | 0.13 | 0.15 | 0.17 | 0.15 | 0.16 | 0.15 | 0.14
| GUESTROOM220_223 PTACFAN | 0.45 | 0.46 | 0.51 | 0.45 | 0.39 | 0.49 | 0.38 | 0.42 | 0.51 | 0.38 | 0.43 | 0.5 | 0.43 | 0.47 | 0.42 | 0.41
| GUESTROOM224 PTACFAN | 0.13 | 0.14 | 0.15 | 0.13 | 0.11 | 0.14 | 0.11 | 0.12 | 0.15 | 0.11 | 0.12 | 0.14 | 0.12 | 0.13 | 0.12 | 0.11
| FRONTSTORAGEFLR2 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FRONTSTAIRSFLR2 UNIT HEATERFAN | 0 | 0.01 | 0.01 | 0.01 | 0 | 0.01 | 0 | 0.01 | 0.01 | 0.01 | 0.02 | 0.02 | 0.03 | 0.03 | 0.03 | 0.04
| REARSTAIRSFLR3 UNIT HEATERFAN | 0 | 0.01 | 0 | 0.01 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0.02 | 0.02 | 0.02 | 0.03 | 0.03 | 0.04
| REARSTORAGEFLR3 UNIT HEATERFAN | 0 | 0.01 | 0 | 0.01 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0.01 | 0.01 | 0.02 | 0.02 | 0.02 | 0.03
| GUESTROOM301 PTACFAN | 0.16 | 0.17 | 0.2 | 0.15 | 0.14 | 0.17 | 0.15 | 0.14 | 0.16 | 0.14 | 0.14 | 0.16 | 0.14 | 0.15 | 0.14 | 0.14
| GUESTROOM302_305 PTACFAN | 0.43 | 0.47 | 0.55 | 0.48 | 0.48 | 0.54 | 0.55 | 0.47 | 0.55 | 0.5 | 0.49 | 0.57 | 0.51 | 0.57 | 0.51 | 0.53
| GUESTROOM306_308 PTACFAN | 0.35 | 0.39 | 0.46 | 0.4 | 0.4 | 0.45 | 0.47 | 0.4 | 0.46 | 0.42 | 0.42 | 0.48 | 0.43 | 0.48 | 0.43 | 0.46
| GUESTROOM309_312 PTACFAN | 0.43 | 0.47 | 0.55 | 0.48 | 0.48 | 0.54 | 0.55 | 0.47 | 0.55 | 0.5 | 0.49 | 0.57 | 0.51 | 0.57 | 0.51 | 0.53
| GUESTROOM313 PTACFAN | 0.13 | 0.14 | 0.17 | 0.14 | 0.14 | 0.16 | 0.15 | 0.14 | 0.16 | 0.14 | 0.14 | 0.16 | 0.14 | 0.16 | 0.14 | 0.15
| GUESTROOM314 PTACFAN | 0.14 | 0.14 | 0.17 | 0.14 | 0.12 | 0.16 | 0.11 | 0.13 | 0.15 | 0.11 | 0.13 | 0.15 | 0.13 | 0.14 | 0.12 | 0.12
| GUESTROOM315_318 PTACFAN | 0.47 | 0.48 | 0.54 | 0.47 | 0.41 | 0.52 | 0.4 | 0.44 | 0.54 | 0.41 | 0.45 | 0.52 | 0.46 | 0.5 | 0.45 | 0.44
| GUESTROOM319 PTACFAN | 0.13 | 0.13 | 0.14 | 0.12 | 0.11 | 0.14 | 0.11 | 0.12 | 0.14 | 0.11 | 0.12 | 0.14 | 0.12 | 0.13 | 0.12 | 0.12
| GUESTROOM320_323 PTACFAN | 0.47 | 0.48 | 0.53 | 0.46 | 0.4 | 0.51 | 0.39 | 0.44 | 0.53 | 0.4 | 0.44 | 0.51 | 0.45 | 0.49 | 0.44 | 0.43
| GUESTROOM324 PTACFAN | 0.14 | 0.14 | 0.16 | 0.13 | 0.11 | 0.15 | 0.11 | 0.13 | 0.15 | 0.11 | 0.13 | 0.14 | 0.13 | 0.14 | 0.12 | 0.12
| FRONTSTORAGEFLR3 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FRONTSTAIRSFLR3 UNIT HEATERFAN | 0 | 0.01 | 0.01 | 0.01 | 0 | 0.01 | 0 | 0.01 | 0.01 | 0.01 | 0.02 | 0.02 | 0.03 | 0.03 | 0.03 | 0.04
| REARSTAIRSFLR4 UNIT HEATERFAN | 0 | 0.02 | 0.01 | 0.02 | 0 | 0.01 | 0.01 | 0.03 | 0.02 | 0.02 | 0.04 | 0.04 | 0.05 | 0.05 | 0.05 | 0.07
| REARSTORAGEFLR4 UNIT HEATERFAN | 0 | 0.02 | 0.01 | 0.02 | 0 | 0.01 | 0.01 | 0.02 | 0.02 | 0.01 | 0.03 | 0.03 | 0.04 | 0.04 | 0.04 | 0.05
| GUESTROOM401 PTACFAN | 0.2 | 0.21 | 0.25 | 0.19 | 0.17 | 0.22 | 0.17 | 0.17 | 0.2 | 0.16 | 0.17 | 0.19 | 0.17 | 0.19 | 0.16 | 0.15
| GUESTROOM402_405 PTACFAN | 0.57 | 0.62 | 0.73 | 0.62 | 0.58 | 0.7 | 0.62 | 0.6 | 0.7 | 0.59 | 0.61 | 0.69 | 0.61 | 0.68 | 0.6 | 0.57
| GUESTROOM406_408 PTACFAN | 0.46 | 0.51 | 0.6 | 0.51 | 0.48 | 0.58 | 0.53 | 0.5 | 0.57 | 0.5 | 0.51 | 0.57 | 0.52 | 0.57 | 0.51 | 0.49
| GUESTROOM409_412 PTACFAN | 0.57 | 0.62 | 0.73 | 0.62 | 0.58 | 0.7 | 0.62 | 0.6 | 0.7 | 0.59 | 0.61 | 0.69 | 0.62 | 0.68 | 0.6 | 0.57
| GUESTROOM413 PTACFAN | 0.17 | 0.18 | 0.22 | 0.18 | 0.16 | 0.21 | 0.17 | 0.17 | 0.2 | 0.16 | 0.17 | 0.19 | 0.17 | 0.19 | 0.17 | 0.16
| GUESTROOM414 PTACFAN | 0.18 | 0.19 | 0.22 | 0.18 | 0.15 | 0.21 | 0.13 | 0.17 | 0.2 | 0.14 | 0.16 | 0.19 | 0.16 | 0.18 | 0.15 | 0.14
| GUESTROOM415_418 PTACFAN | 0.62 | 0.65 | 0.74 | 0.62 | 0.52 | 0.7 | 0.48 | 0.58 | 0.7 | 0.5 | 0.58 | 0.66 | 0.57 | 0.63 | 0.55 | 0.49
| GUESTROOM419 PTACFAN | 0.16 | 0.17 | 0.2 | 0.16 | 0.14 | 0.19 | 0.12 | 0.15 | 0.18 | 0.13 | 0.15 | 0.17 | 0.15 | 0.16 | 0.14 | 0.13
| GUESTROOM420_423 PTACFAN | 0.61 | 0.64 | 0.73 | 0.62 | 0.52 | 0.7 | 0.47 | 0.58 | 0.7 | 0.5 | 0.57 | 0.66 | 0.57 | 0.62 | 0.55 | 0.48
| GUESTROOM424 PTACFAN | 0.18 | 0.19 | 0.22 | 0.18 | 0.15 | 0.2 | 0.13 | 0.17 | 0.2 | 0.14 | 0.16 | 0.18 | 0.16 | 0.17 | 0.15 | 0.13
| FRONTSTORAGEFLR4 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
| FRONTSTAIRSFLR4 UNIT HEATERFAN | 0.01 | 0.02 | 0.02 | 0.03 | 0.01 | 0.02 | 0.01 | 0.03 | 0.03 | 0.02 | 0.05 | 0.05 | 0.06 | 0.06 | 0.06 | 0.08
| PSZ-HEATCOOL:1_FAN | 0.53 | 0.55 | 0.57 | 0.55 | 0.49 | 0.52 | 0.43 | 0.51 | 0.58 | 0.45 | 0.52 | 0.58 | 0.53 | 0.55 | 0.48 | 0.42
| PSZ-HEATCOOL:2_FAN | 0.78 | 0.85 | 0.93 | 0.85 | 0.85 | 0.88 | 0.91 | 0.83 | 0.93 | 0.83 | 0.86 | 0.96 | 0.88 | 0.96 | 0.85 | 0.84
| PSZ-HEATCOOL:3_FAN | 0.08 | 0.08 | 0.09 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.07 | 0.08 | 0.08 | 0.08 | 0.08 | 0.07 | 0.07
| PSZ-HEATCOOL:4_FAN | 0.42 | 0.44 | 0.47 | 0.45 | 0.44 | 0.45 | 0.45 | 0.43 | 0.49 | 0.43 | 0.44 | 0.5 | 0.45 | 0.49 | 0.44 | 0.43
| PSZ-HEATCOOL:5_FAN | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09
| PSZ-HEATCOOL:6_FAN | 0.33 | 0.33 | 0.34 | 0.33 | 0.31 | 0.34 | 0.29 | 0.32 | 0.38 | 0.3 | 0.32 | 0.38 | 0.33 | 0.36 | 0.32 | 0.3
| PSZ-HEATCOOL:7_FAN | 1.52 | 1.52 | 1.56 | 1.56 | 1.5 | 1.6 | 1.43 | 1.5 | 1.79 | 1.47 | 1.52 | 1.78 | 1.53 | 1.68 | 1.53 | 1.45
| PSZ-HEATCOOL:8_FAN | 0.14 | 0.14 | 0.15 | 0.14 | 0.12 | 0.13 | 0.11 | 0.13 | 0.15 | 0.11 | 0.13 | 0.15 | 0.13 | 0.14 | 0.13 | 0.12
| PSZ-HEATCOOL:9_FAN | 0.4 | 0.41 | 0.42 | 0.38 | 0.33 | 0.38 | 0.27 | 0.35 | 0.4 | 0.29 | 0.35 | 0.39 | 0.35 | 0.36 | 0.31 | 0.27
| PSZ-HEATCOOL:10_FAN | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34
| PSZ-HEATCOOL:11_FAN | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34
| PSZ-HEATCOOL:12_FAN | 0.39 | 0.43 | 0.51 | 0.41 | 0.34 | 0.47 | 0.34 | 0.38 | 0.45 | 0.34 | 0.37 | 0.42 | 0.36 | 0.39 | 0.34 | 0.34
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.079025 | 0.10927 | 0.088683 | 0.10099 | 0.12374 | 0.094673 | 0.14555 | 0.069269 | 0.037255 | 0.071887 | 0.097744 | 0.037264 | 0.055654 | 0.071881 | 0.056165 | 0.093438
| Total Cost ($/m2) | 14.85 | 18.76 | 15.4 | 15.72 | 17.82 | 15.1 | 19.34 | 10.3 | 5.46 | 9.43 | 14.3 | 5.32 | 8.43 | 10.17 | 8.28 | 15.67
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011454 | 0.0081526 | 0.0084678 | 0.010344 | 0.0084456 | 0.0079732 | 0.0084565 | 0.0098959 | 0.0070791 | 0.0083395 | 0.0086458 | 0.0070842 | 0.0079034 | 0.0084728 | 0.007906 | 0.0041744
| Total Cost ($/m2) | 1.4 | 1.58 | 1.42 | 2.65 | 1.54 | 1.65 | 2.24 | 3.41 | 2.04 | 2.87 | 3.63 | 2.52 | 3.78 | 3.76 | 4.45 | 3.09
Total Utility Costs
| Cost Intensity ($/m2) | 16.26 | 20.34 | 16.82 | 18.37 | 19.37 | 16.75 | 21.58 | 13.71 | 7.5 | 12.31 | 17.93 | 7.83 | 12.22 | 13.93 | 12.74 | 18.75
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 2627.7778 | 347.2222 | 3458.3333 | 0 | 255.5556 | 205.5556 | 9311.1111 | 2086.1111 | 2463.8889 | 19883.3333 | 10447.2222 | 45566.6667 | 28072.2222 | 65391.6667 | 160605.5556
| Cooling | 270611.1111 | 204633.3333 | 210016.6667 | 142180.5556 | 102144.4444 | 157344.4444 | 62519.4444 | 112711.1111 | 102619.4444 | 54588.8889 | 92877.7778 | 80522.2222 | 86655.5556 | 61352.7778 | 54350 | 40955.5556
| Interior Lighting | 174625 | 174625 | 174625 | 174625 | 174625 | 174625 | 174625 | 174625 | 174625 | 174625 | 174625 | 174625 | 174625 | 174625 | 174625 | 174625
| Exterior Lighting | 10494.4444 | 10475 | 10472.2222 | 10488.8889 | 10488.8889 | 10477.7778 | 10466.6667 | 10477.7778 | 10475 | 10461.1111 | 10463.8889 | 10463.8889 | 10472.2222 | 10458.3333 | 10455.5556 | 10394.4444
| Interior Equipment | 226402.7778 | 226402.7778 | 226402.7778 | 226402.7778 | 226402.7778 | 226402.7778 | 226402.7778 | 226402.7778 | 226402.7778 | 226402.7778 | 226402.7778 | 226402.7778 | 226402.7778 | 226402.7778 | 226402.7778 | 226402.7778
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 71552.7778 | 69747.2222 | 74294.4444 | 66947.2222 | 63686.1111 | 70341.6667 | 58375 | 62600 | 71080.5556 | 57277.7778 | 62394.4444 | 69311.1111 | 63688.8889 | 66008.3333 | 59963.8889 | 59272.2222
| Pumps | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 754433.3333 | 689255.5556 | 696902.7778 | 624847.2222 | 578091.6667 | 640191.6667 | 533338.8889 | 596872.2222 | 588030.5556 | 526563.8889 | 587388.8889 | 572516.6667 | 608158.3333 | 567663.8889 | 591933.3333 | 673000
Gas (MJ)
| Heating | 12770 | 219270 | 159880 | 394240 | 115640 | 264910 | 378960 | 691800 | 475000 | 660720 | 939620 | 685770 | 1132350 | 983800 | 1397490 | 2014230
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 189470 | 189470 | 189470 | 189470 | 189470 | 189470 | 189470 | 189470 | 189470 | 189470 | 189470 | 189470 | 189470 | 189470 | 189470 | 189470
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 289590 | 367870 | 322880 | 443320 | 428650 | 377100 | 493210 | 502600 | 491360 | 533430 | 554630 | 551920 | 599600 | 607780 | 673780 | 763580
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 491840 | 776610 | 672230 | 1027030 | 733770 | 831490 | 1061640 | 1383870 | 1155830 | 1383630 | 1683720 | 1427160 | 1921430 | 1781060 | 2260740 | 2967280
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 3207790 | 3257930 | 3181080 | 3276490 | 2814900 | 3136180 | 2981650 | 3532610 | 3272740 | 3279250 | 3798330 | 3488220 | 4110790 | 3824650 | 4391710 | 5390070
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 2.357 | 0.31144 | 3.102 | 0 | 0.22922 | 0.18437 | 8.3516 | 1.8711 | 2.21 | 17.8344 | 9.3707 | 40.8711 | 25.1795 | 58.6532 | 144.0556
| Cooling (elec) | 242.7253 | 183.5464 | 188.375 | 127.5292 | 91.6187 | 141.1305 | 56.077 | 101.0965 | 92.0448 | 48.9636 | 83.307 | 72.2246 | 77.7259 | 55.0305 | 48.7494 | 36.7352
| Interior Lighting (elec) | 156.6303 | 156.6303 | 156.6303 | 156.6303 | 156.6303 | 156.6303 | 156.6303 | 156.6303 | 156.6303 | 156.6303 | 156.6303 | 156.6303 | 156.6303 | 156.6303 | 156.6303 | 156.6303
| Exterior Lighting (elec) | 9.413 | 9.3956 | 9.3931 | 9.408 | 9.408 | 9.3981 | 9.3881 | 9.3981 | 9.3956 | 9.3831 | 9.3856 | 9.3856 | 9.3931 | 9.3806 | 9.3781 | 9.3233
| Interior Equipment (elec) | 203.0726 | 203.0726 | 203.0726 | 203.0726 | 203.0726 | 203.0726 | 203.0726 | 203.0726 | 203.0726 | 203.0726 | 203.0726 | 203.0726 | 203.0726 | 203.0726 | 203.0726 | 203.0726
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 64.1795 | 62.56 | 66.6386 | 60.0485 | 57.1234 | 63.0931 | 52.3596 | 56.1492 | 63.7559 | 51.3755 | 55.9649 | 62.1688 | 57.1259 | 59.2063 | 53.7848 | 53.1644
| Pumps (elec) | 0.66524 | 0.66524 | 0.66524 | 0.66524 | 0.66524 | 0.66524 | 0.66524 | 0.66524 | 0.66524 | 0.66524 | 0.66524 | 0.66524 | 0.66524 | 0.66524 | 0.66524 | 0.66524
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 676.6909 | 618.2296 | 625.0888 | 560.4583 | 518.5208 | 574.2216 | 478.3797 | 535.3661 | 527.4355 | 472.3029 | 526.86 | 513.5203 | 545.4892 | 509.1676 | 530.9361 | 603.6491
Gas (MJ/m2)
| Heating (gas) | 3.1817 | 54.6319 | 39.8347 | 98.2263 | 28.8121 | 66.0033 | 94.4192 | 172.3644 | 118.3479 | 164.6207 | 234.1096 | 170.862 | 282.129 | 245.1172 | 348.1895 | 501.8525
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 47.2071 | 47.2071 | 47.2071 | 47.2071 | 47.2071 | 47.2071 | 47.2071 | 47.2071 | 47.2071 | 47.2071 | 47.2071 | 47.2071 | 47.2071 | 47.2071 | 47.2071 | 47.2071
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 72.1524 | 91.6561 | 80.4467 | 110.4547 | 106.7996 | 93.9558 | 122.885 | 125.2245 | 122.4241 | 132.906 | 138.188 | 137.5128 | 149.3924 | 151.4305 | 167.8746 | 190.2486
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 122.5437 | 193.4951 | 167.4885 | 255.8881 | 182.8214 | 207.1686 | 264.5113 | 344.7961 | 287.9791 | 344.7363 | 419.5047 | 355.5819 | 478.731 | 443.7573 | 563.2713 | 739.3082
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 799.2321 | 811.7247 | 792.5772 | 816.349 | 701.3422 | 781.3902 | 742.8885 | 880.1621 | 815.4146 | 817.0366 | 946.3672 | 869.1022 | 1024.2177 | 952.9249 | 1094.2099 | 1342.9548
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 131.4786 | 122.9835 | 107.2832 | 106.6157 | 105.0501 | 101.6146 | 100.643 | 109.697 | 100.2898 | 97.0089 | 129.4848 | 118.239 | 152.7904 | 149.2899 | 161.8117 | 236.2069
| Feb | 135.9 | 110.9284 | 104.3272 | 106.5263 | 110.1486 | 104.0535 | 103.0656 | 100.2331 | 101.1935 | 97.8207 | 109.7989 | 107.3897 | 141.3107 | 129.4981 | 164.3068 | 228.8928
| Mar | 135.1693 | 124.9424 | 124.5009 | 110.0244 | 106.557 | 103.7663 | 101.4932 | 109.1498 | 102.5201 | 100.1558 | 99.5999 | 102.1112 | 101.7182 | 111.8021 | 123.3875 | 149.6302
| Apr | 137.5034 | 135.5572 | 124.4134 | 120.4376 | 108.2736 | 122.041 | 104.9687 | 107.0947 | 110.6883 | 104.7872 | 107.5458 | 106.994 | 109.3178 | 101.755 | 100.3333 | 105.4114
| May | 147.0817 | 145.4636 | 147.0363 | 133.4434 | 115.7739 | 129.6124 | 104.7928 | 120.1326 | 117.5698 | 108.0627 | 118.2552 | 116.018 | 134.0313 | 106.3768 | 109.0608 | 104.5657
| Jun | 149.4385 | 143.2341 | 169.988 | 137.6908 | 110.9499 | 152.3622 | 109.2983 | 139.6929 | 124.5325 | 113.2702 | 128.4121 | 119.2304 | 136.225 | 127.2629 | 122.0913 | 112.5425
| Jul | 149.8586 | 152.2517 | 166.1119 | 147.0265 | 121.8676 | 151.2684 | 121.9231 | 146.0991 | 132.0193 | 117.4912 | 141.4318 | 126.7188 | 140.9279 | 124.9716 | 135.2942 | 116.6571
| Aug | 146.2585 | 153.7567 | 168.1119 | 138.1096 | 125.0709 | 147.5957 | 107.4033 | 146.4647 | 130.0262 | 116.1675 | 143.2764 | 122.962 | 140.3042 | 120.6674 | 129.7973 | 109.8653
| Sep | 147.4355 | 150.4453 | 152.1484 | 129.9908 | 122.5313 | 136.4348 | 115.8007 | 127.4607 | 121.1104 | 120.733 | 121.3262 | 121.0096 | 118.3079 | 117.0265 | 110.2841 | 102.3424
| Oct | 146.8061 | 134.628 | 128.8725 | 119.0876 | 114.0735 | 118.0012 | 106.6162 | 120.6373 | 110.1473 | 104.8589 | 108.5142 | 109.3057 | 112.1711 | 103.5527 | 105.2717 | 110.5798
| Nov | 135.2387 | 132.367 | 108.7703 | 111.3454 | 109.1791 | 107.8674 | 104.176 | 118.0196 | 102.6373 | 104.3062 | 104.8512 | 105.0241 | 101.3255 | 99.2045 | 125.0155 | 147.869
| Dec | 131.0216 | 132.1241 | 103.3678 | 108.86 | 105.65 | 103.2423 | 101.0279 | 101.9513 | 99.8656 | 96.9865 | 118.1262 | 113.4568 | 156.6266 | 142.5515 | 159.4405 | 200.0042
Time of Peak Electrical Demand
| Jan | 22-JAN-08:00 | 22-JAN-08:00 | 29-JAN-08:00 | 14-JAN-08:15 | 28-JAN-08:00 | 29-JAN-08:00 | 16-JAN-08:00 | 31-JAN-07:15 | 21-JAN-08:00 | 29-JAN-08:30 | 08-JAN-08:15 | 08-JAN-08:15 | 07-JAN-06:15 | 07-JAN-08:15 | 09-JAN-08:30 | 13-JAN-08:00
| Feb | 25-FEB-08:00 | 20-FEB-08:00 | 28-FEB-20:15 | 20-FEB-08:00 | 12-FEB-08:00 | 18-FEB-08:00 | 18-FEB-08:00 | 01-FEB-07:15 | 20-FEB-08:00 | 20-FEB-08:00 | 11-FEB-08:15 | 16-FEB-07:15 | 04-FEB-08:15 | 26-FEB-08:15 | 02-FEB-07:15 | 04-FEB-08:15
| Mar | 05-MAR-08:00 | 25-MAR-07:00 | 17-MAR-19:15 | 28-MAR-19:15 | 11-MAR-08:00 | 26-MAR-07:00 | 11-MAR-08:00 | 26-MAR-07:00 | 26-MAR-07:00 | 29-MAR-19:00 | 31-MAR-19:30 | 26-MAR-19:15 | 04-MAR-08:15 | 04-MAR-08:15 | 09-MAR-07:15 | 14-MAR-07:45
| Apr | 02-APR-07:00 | 30-APR-07:00 | 01-APR-17:15 | 16-APR-07:00 | 16-APR-07:00 | 21-APR-19:15 | 29-APR-07:00 | 05-APR-19:15 | 22-APR-19:15 | 30-APR-07:00 | 29-APR-07:00 | 25-APR-19:15 | 02-APR-07:00 | 30-APR-07:00 | 09-APR-07:00 | 02-APR-07:15
| May | 20-MAY-07:00 | 26-MAY-19:15 | 28-MAY-19:30 | 14-MAY-19:30 | 28-MAY-07:00 | 31-MAY-19:15 | 29-MAY-07:00 | 15-MAY-19:15 | 30-MAY-19:15 | 07-MAY-07:00 | 28-MAY-07:00 | 23-MAY-19:15 | 27-MAY-19:45 | 25-MAY-19:00 | 28-MAY-07:00 | 29-MAY-07:00
| Jun | 27-JUN-19:15 | 11-JUN-07:00 | 27-JUN-19:15 | 08-JUN-19:15 | 17-JUN-07:00 | 27-JUN-19:15 | 17-JUN-07:00 | 30-JUN-19:15 | 28-JUN-19:30 | 18-JUN-07:00 | 16-JUN-19:30 | 27-JUN-19:30 | 29-JUN-19:15 | 25-JUN-19:15 | 14-JUN-19:00 | 24-JUN-07:00
| Jul | 29-JUL-07:00 | 04-JUL-07:00 | 11-JUL-19:15 | 02-JUL-19:15 | 09-JUL-07:00 | 25-JUL-19:15 | 02-JUL-19:30 | 24-JUL-19:30 | 30-JUL-19:15 | 24-JUL-19:15 | 09-JUL-07:00 | 02-JUL-07:00 | 16-JUL-07:00 | 21-JUL-19:15 | 08-JUL-07:00 | 29-JUL-19:45
| Aug | 19-AUG-07:00 | 06-AUG-19:15 | 01-AUG-19:30 | 14-AUG-19:30 | 13-AUG-07:00 | 04-AUG-19:15 | 27-AUG-07:00 | 17-AUG-19:15 | 01-AUG-19:15 | 06-AUG-19:45 | 04-AUG-19:15 | 29-AUG-19:15 | 25-AUG-19:15 | 11-AUG-19:45 | 13-AUG-19:30 | 15-AUG-19:15
| Sep | 03-SEP-07:00 | 16-SEP-07:00 | 09-SEP-19:15 | 10-SEP-19:15 | 09-SEP-07:00 | 02-SEP-07:00 | 28-SEP-19:00 | 17-SEP-07:00 | 03-SEP-07:00 | 02-SEP-19:15 | 16-SEP-07:00 | 02-SEP-07:00 | 03-SEP-07:00 | 02-SEP-19:15 | 03-SEP-07:00 | 04-SEP-07:00
| Oct | 07-OCT-07:00 | 29-OCT-19:30 | 02-OCT-19:15 | 21-OCT-19:15 | 07-OCT-07:00 | 07-OCT-07:00 | 21-OCT-07:00 | 14-OCT-07:00 | 01-OCT-19:15 | 01-OCT-07:00 | 29-OCT-07:00 | 01-OCT-07:00 | 08-OCT-07:00 | 08-OCT-07:00 | 07-OCT-07:00 | 22-OCT-07:15
| Nov | 05-NOV-08:00 | 04-NOV-08:00 | 12-NOV-08:00 | 23-NOV-08:00 | 12-NOV-08:00 | 11-NOV-08:00 | 11-NOV-08:00 | 04-NOV-08:00 | 11-NOV-08:00 | 04-NOV-08:00 | 02-NOV-20:15 | 12-NOV-08:00 | 05-NOV-08:00 | 05-NOV-08:00 | 25-NOV-08:15 | 23-NOV-08:15
| Dec | 16-DEC-08:00 | 03-DEC-08:00 | 10-DEC-08:00 | 31-DEC-08:00 | 16-DEC-08:00 | 09-DEC-08:00 | 17-DEC-08:00 | 21-DEC-07:15 | 10-DEC-08:00 | 31-DEC-08:00 | 31-DEC-08:15 | 12-DEC-07:15 | 31-DEC-06:15 | 11-DEC-08:30 | 31-DEC-08:15 | 29-DEC-08:00
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09
| Total Building | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09
Emissions
| Carbon Equivalent (kg) | 215772.1178 | 243913.1919 | 222499.8103 | 210996.3825 | 80790.9811 | 230914.9351 | 81473.1409 | 186023.9933 | 261052.2455 | 63302.2899 | 343528.7216 | 259607.9024 | 242816.3904 | 239563.0505 | 243382.3463 | 242881.4463
| CO2 (kg) | 504719.6417 | 617368.4925 | 529768.0291 | 490352.3613 | 218600.8553 | 554731.941 | 221719.0621 | 433302.5114 | 619930.1435 | 163190.7749 | 810282.3302 | 619300.2891 | 580015.1425 | 575284.9273 | 584892.0504 | 628978.7017
| NOX (kg) | 868.1983 | 795.0252 | 867.9955 | 892.1239 | 189.0646 | 878.0072 | 192.623 | 787.6477 | 1036.7062 | 211.8259 | 1395.3471 | 1023.6321 | 966.6295 | 940.7129 | 959.3188 | 734.6642
| SO2 (kg) | 3229.4054 | 3287.9571 | 2802.5631 | 2193.4931 | 1682.3743 | 3521.7935 | 1552.2327 | 2179.19 | 2568.1244 | 407.362 | 3958.9913 | 2500.4526 | 1435.8627 | 1516.2085 | 1397.666 | 3426.6294
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0148 | 0.0093 | 0.0077 | 0.0081 | 0.0008 | 0.0067 | 0.0008 | 0.0089 | 0.0101 | 0.0017 | 0.0121 | 0.0099 | 0.0107 | 0.0107 | 0.0104 | 0.0119
| Water for Electricity (m3) | 399.6667 | 1121.5 | 20701.1 | 3901.3 | 10150 | 17563 | 9364.21 | 135.5122 | 2670.13 | 5379.79 | 911.3008 | 2599.69 | 943.5192 | 35958.2 | 918.3509 | 687.5896

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3207.79 | 799.23 | 811.4
Net Site Energy | 3207.79 | 799.23 | 811.4
Total Source Energy | 9545.92 | 2378.4 | 2414.62
Net Source Energy | 9545.92 | 2378.4 | 2414.62
Area [m2]
Total Building Area | 4013.59
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 60.2
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 12.77 | 0 | 0 | 0 | 0
Cooling | 974.2 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 628.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 37.78 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 815.05 | 189.47 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 257.59 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 289.59 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2715.96 | 491.84 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 6.46 |  | 0
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 5.38 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.6 |  | 0
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 11.84 | 3.08 | 15.43
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 9.7 | 32.61 | 10.7631
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 14 | 1.87 | 12.9
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 16.16 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 12.9 | 2.96 | 77.16
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 6.46 | 8.89 | 206.12
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2157.2117
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 9.7 | 2.96 | 11.4999
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 11.84 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 6.46 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 8.6 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 11.8 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
Total | 4013.59 |  | 11621.74 |  | 1694.58 | 184.21 | 10.425 | 15.71 | 24.2519
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 10.5838 | 15.47 | 16.4088
Unconditioned Total | 60.2 |  | 174.32 |  | 21.18 | 0 | 0 |  | 539.3029
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_REARSTAIRSFLR1_2_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_CORRIDORFLR1_2_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 6.13 | 90 | 90 | E
W_CORRIDORFLR1_10_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.22 | 180 | 90 | S
S_CORRIDORFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 150.51 | 270 | 180
W_REARSTORAGEFLR1_2_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 163.06 | 90 | 180
W_RESTROOMFLR1_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 80.27 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM101_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_EMPLOYEELOUNGEFLR1_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_LAUNDRYROOMFLR1_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 97.83 | 90 | 180
W_ELEVATORCOREFLR1_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 15.05 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_FRONTSTORAGEFLR1_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 12.54 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 6.69 | 0 | 90 | N
W_CORRIDORFLR2_2_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 8.36 | 0 | 90 | N
W_CORRIDORFLR2_15_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 5.02 | 270 | 90 | W
W_REARSTORAGEFLR2_2_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 6.69 | 180 | 90 | S
W_GUESTROOM201_4_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 43.48 | 0 | 90 | N
W_ELEVATORCOREFLR2_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 5.02 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 0 | 90 | N
W_FRONTSTORAGEFLR2_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 4.18 | 0 | 90 | N
W_FRONTSTAIRSFLR2_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 22.58 | 270 | 90 | W
W_REARSTAIRSFLR3_2_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 6.69 | 0 | 90 | N
W_CORRIDORFLR3_2_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 5.02 | 270 | 90 | W
W_REARSTORAGEFLR3_2_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 6.69 | 180 | 90 | S
W_GUESTROOM301_4_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 43.48 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 5.02 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 4.18 | 0 | 90 | N
W_FRONTSTAIRSFLR3_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 22.58 | 270 | 90 | W
W_REARSTAIRSFLR4_2_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 6.69 | 0 | 90 | N
R_REARSTAIRSFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
W_CORRIDORFLR4_2_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 5.02 | 270 | 90 | W
R_CORRIDORFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 125.42 | 90 | 0
W_REARSTORAGEFLR4_2_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 6.69 | 180 | 90 | S
R_REARSTORAGEFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
W_GUESTROOM401_4_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 180 | 90 | S
R_GUESTROOM401_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM402_405_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 43.48 | 180 | 90 | S
R_GUESTROOM402_405_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.45 | 90 | 0
W_GUESTROOM406_408_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 35.12 | 180 | 90 | S
R_GUESTROOM406_408_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 105.36 | 90 | 0
W_GUESTROOM409_412_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 43.48 | 180 | 90 | S
R_GUESTROOM409_412_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.45 | 90 | 0
W_GUESTROOM413_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 180 | 90 | S
R_GUESTROOM413_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM414_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 0 | 90 | N
R_GUESTROOM414_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM415_418_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 43.48 | 0 | 90 | N
R_GUESTROOM415_418_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.44 | 90 | 0
W_ELEVATORCOREFLR4_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 5.02 | 0 | 90 | N
R_ELEVATORCOREFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 15.05 | 90 | 0
W_GUESTROOM419_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 0 | 90 | N
R_GUESTROOM419_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM420_423_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 43.48 | 0 | 90 | N
R_GUESTROOM420_423_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.44 | 90 | 0
W_GUESTROOM424_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 0 | 90 | N
R_GUESTROOM424_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_FRONTSTORAGEFLR4_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 4.18 | 0 | 90 | N
R_FRONTSTORAGEFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12.54 | 90 | 0
W_FRONTSTAIRSFLR4_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 22.58 | 270 | 90 | W
R_FRONTSTAIRSFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
W_CORRIDORFLR1_2_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 2.69 | 2.69 | 6.49 | 0.25 | 0.25 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
D_CORRIDORFLR1_16_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 4.44 | 4.44 | 6.49 | 0.25 | 0.25 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 2.69 | 2.69 | 6.49 | 0.25 | 0.25 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 2.97 | 2.97 | 6.49 | 0.25 | 0.25 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 2.97 | 2.97 | 6.49 | 0.25 | 0.25 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 2.97 | 2.97 | 6.49 | 0.25 | 0.25 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 2.97 | 2.97 | 6.49 | 0.25 | 0.25 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 2.96 | 2.96 | 6.49 | 0.25 | 0.25 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.64 | 1.64 | 6.49 | 0.25 | 0.25 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.64 | 1.64 | 6.49 | 0.25 | 0.25 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.65 | 1.65 | 6.49 | 0.25 | 0.25 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_GUESTROOM101_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.64 | 1.64 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.64 | 1.64 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.65 | 1.65 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_CORRIDORFLR2_2_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 1.31 | 1.31 | 6.49 | 0.25 | 0.25 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 1.31 | 1.31 | 6.49 | 0.25 | 0.25 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_GUESTROOM201_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.64 | 1.64 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.64 | 1.64 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.64 | 1.64 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.64 | 1.64 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.64 | 1.64 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.65 | 1.65 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 3.41 | 3.41 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.65 | 1.65 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.64 | 1.64 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.64 | 1.64 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.64 | 1.64 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.64 | 1.64 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.65 | 1.65 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_CORRIDORFLR3_2_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 1.31 | 1.31 | 6.49 | 0.25 | 0.25 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 1.31 | 1.31 | 6.49 | 0.25 | 0.25 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_GUESTROOM301_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.64 | 1.64 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.64 | 1.64 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.64 | 1.64 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.64 | 1.64 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.64 | 1.64 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.65 | 1.65 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 3.41 | 3.41 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.65 | 1.65 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.64 | 1.64 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.64 | 1.64 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.64 | 1.64 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.64 | 1.64 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.65 | 1.65 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_CORRIDORFLR4_2_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 1.31 | 1.31 | 6.49 | 0.25 | 0.25 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 1.31 | 1.31 | 6.49 | 0.25 | 0.25 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_GUESTROOM401_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.64 | 1.64 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.64 | 1.64 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.64 | 1.64 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.64 | 1.64 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.64 | 1.64 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.65 | 1.65 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.65 | 1.65 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 3.41 | 3.41 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.64 | 1.64 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.64 | 1.64 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.64 | 1.64 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.64 | 1.64 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1.65 | 1.65 | 6.49 | 0.25 | 0.25 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM424_3_0_0 | 0 | N
Total or Average |  |  | 184.21 | 6.49 | 0.392 | 0.391
North Total or Average |  |  | 72.38 | 6.49 | 0.61 | 0.61
Non-North Total or Average |  |  | 111.83 | 6.49 | 0.25 | 0.25
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1859.62 | 1380.82 | 478.8 | 0.74 | 3.56
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1884.95 | 1403.5 | 481.45 | 0.74 | 3.56
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2045.8 | 1544.98 | 500.82 | 0.76 | 3.56
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2077.61 | 1592.71 | 484.9 | 0.77 | 3.55
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2063.8 | 1580.47 | 483.33 | 0.77 | 3.56
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2723.75 | 2135.57 | 588.18 | 0.78 | 3.43
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8133.34 | 6141.68 | 1991.66 | 0.76 | 2.94
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6376.79 | 4848.33 | 1528.46 | 0.76 | 2.95
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7954.66 | 5988.02 | 1966.64 | 0.75 | 2.94
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2263.01 | 1738.26 | 524.75 | 0.77 | 3.54
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2337.91 | 1829.02 | 508.89 | 0.78 | 3.51
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8744.24 | 6764.01 | 1980.23 | 0.77 | 2.96
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2565.18 | 2029.88 | 535.3 | 0.79 | 3.47
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8222.77 | 6301.14 | 1921.63 | 0.77 | 2.95
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2307.24 | 1799.46 | 507.78 | 0.78 | 3.52
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2712.34 | 2125.44 | 586.91 | 0.78 | 3.43
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8127.31 | 6136.37 | 1990.94 | 0.76 | 2.94
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6477.52 | 4936.85 | 1540.67 | 0.76 | 2.95
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8118.27 | 6128.47 | 1989.8 | 0.75 | 2.94
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2312.13 | 1781.59 | 530.54 | 0.77 | 3.52
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2391.69 | 1877.1 | 514.59 | 0.78 | 3.52
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8491.56 | 6541.29 | 1950.27 | 0.77 | 2.95
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2222.22 | 1723.73 | 498.49 | 0.78 | 3.56
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8391.17 | 6450.46 | 1940.71 | 0.77 | 2.96
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2350.17 | 1837.75 | 512.42 | 0.78 | 3.54
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3337.88 | 2633.8 | 704.09 | 0.79 | 3.27
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10246.86 | 7883.9 | 2362.96 | 0.77 | 2.96
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8215.31 | 6356.75 | 1858.56 | 0.77 | 2.96
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10269.07 | 7889.73 | 2379.34 | 0.77 | 2.96
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2902.77 | 2272.49 | 630.28 | 0.78 | 3.38
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3039.84 | 2407.33 | 632.51 | 0.79 | 3.34
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10797.05 | 8412.43 | 2384.62 | 0.78 | 2.97
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2808.13 | 2199.84 | 608.29 | 0.78 | 3.39
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10725.39 | 8348.77 | 2376.62 | 0.78 | 2.96
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2997.4 | 2368.56 | 628.85 | 0.79 | 3.36
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13193.18 | 8919.69 | 4273.49 | 0.68 | 3.66
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 19349.58 | 13081.93 | 6267.65 | 0.68 | 3.45
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1938.71 | 1315.16 | 623.55 | 0.68 | 3.68
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10347.24 | 6995.59 | 3351.64 | 0.68 | 3.67
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2210.8 | 1494.69 | 716.12 | 0.68 | 3.67
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7415.78 | 5210.15 | 2205.63 | 0.7 | 3.74
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 27074.35 | 20945.42 | 6128.93 | 0.77 | 3.67
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3414 | 2308.15 | 1105.85 | 0.68 | 3.68
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9065.48 | 6367.88 | 2697.6 | 0.7 | 3.73
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8502.54 | 5748.42 | 2754.11 | 0.68 | 3.66
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8502.54 | 5748.42 | 2754.11 | 0.68 | 3.66
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9571.12 | 6470.88 | 3100.25 | 0.68 | 3.67
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 555.93 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 555.93 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 555.93 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 555.93 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 555.93 | 1
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 706.84 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 2223.71 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 1667.78 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 2223.71 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 589.83 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 555.93 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 2223.71 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 694.91 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 2223.71 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 555.93 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 761.7 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 2223.71 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 1667.78 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 2223.71 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 665.93 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 626.55 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 2223.71 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 555.93 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 2223.71 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 583.5 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 53.47 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 1043.18 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 3034.69 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 2463.97 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 3033.53 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 977.06 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 954.56 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 3021.98 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 797.46 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 2998.79 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 906.06 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 156.51 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 6170.81 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 9050.33 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 915.82 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 4839.69 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1034.05 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 4050.58 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 20874.02 | 0.8
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 1596.82 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 4271.45 | 0.78
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 3976.87 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 3976.87 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 4476.67 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.1 | 60.57 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.1 | 61.8 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 69.35 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 72.91 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 72.25 | 1 | PTAC Fan
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.16 | 100.55 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.43 | 275.64 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.35 | 219.57 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.42 | 267.63 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.13 | 79.77 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.13 | 85.88 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.49 | 313.18 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.15 | 96.64 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.45 | 288.29 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.13 | 84.17 | 1 | PTAC Fan
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.16 | 100 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.43 | 275.36 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.35 | 224.29 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.43 | 274.94 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.13 | 82.09 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 88.49 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.47 | 301.28 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.13 | 80.09 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.47 | 296.31 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 86.24 | 1 | PTAC Fan
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0.36 | 1 | Unit Heater Fans
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.2 | 124.97 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.57 | 362.56 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.46 | 294.44 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.57 | 362.17 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.17 | 106.8 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.18 | 114.72 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.62 | 393.03 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.16 | 103.47 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.61 | 389.61 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.18 | 112.58 | 1 | PTAC Fan
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 1.04 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.53 | 616.25 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.78 | 887.67 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.08 | 91.4 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.42 | 483.31 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 103.27 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.33 | 383.83 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.52 | 1666.92 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.14 | 159.47 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.4 | 468.97 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.39 | 447.06 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 37672.1357 | 64.1558 | 235.9555 | 0 | 0.0011 | 29201.0235 | 16040.4177
February | 34535.3008 | 58.9906 | 217.6998 | 0 | 0.001 | 26941.8951 | 14722.4994
March | 38990.5765 | 66.7432 | 246.9056 | 0 | 0.0011 | 30556.4355 | 16636.0695
April | 40466.2055 | 69.5932 | 258.8006 | 0 | 0.0012 | 32028.7952 | 17298.1473
May | 44772.8003 | 77.2329 | 288.1792 | 0 | 0.0013 | 35664.827 | 19162.4653
June | 45261.7936 | 78.2247 | 292.494 | 0 | 0.0013 | 36198.9351 | 19386.6129
July | 48574.7745 | 84.0474 | 314.6662 | 0 | 0.0014 | 38943.0366 | 20815.3465
August | 48183.4216 | 83.3354 | 311.8569 | 0 | 0.0014 | 38595.3315 | 20644.1535
September | 45449.6917 | 78.5028 | 293.3412 | 0 | 0.0013 | 36303.7485 | 19462.4209
October | 44111.5538 | 75.9924 | 283.1373 | 0 | 0.0013 | 35040.769 | 18869.4524
November | 39265.3006 | 67.3986 | 250.1026 | 0 | 0.0011 | 30952.2383 | 16771.839
December | 37436.0873 | 63.9812 | 236.2667 | 0 | 0.0011 | 29239.71 | 15962.6936
Annual Sum or Average | 504719.6417 | 868.1983 | 3229.4054 | 0 | 0.0148 | 399666.7453 | 215772.1178
Minimum of Months | 34535.3008 | 58.9906 | 217.6998 | 0 | 0.001 | 26941.8951 | 14722.4994
Maximum of Months | 48574.7745 | 84.0474 | 314.6662 | 0 | 0.0014 | 38943.0366 | 20815.3465
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 198437000000 | 131478.551 | 22-JAN-08:00 | 26344.714 | 58181.634 | 8856.187 | 0 | 38011.237 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 183085000000 | 135899.99 | 25-FEB-08:00 | 26344.714 | 58181.634 | 9028.55 | 0 | 42260.314 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 207648000000 | 135169.27 | 05-MAR-08:00 | 26344.714 | 58181.634 | 8976.197 | 0 | 41581.946 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 217653000000 | 137503.438 | 02-APR-07:00 | 26344.714 | 58181.634 | 9082.518 | 0 | 43809.794 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 242362000000 | 147081.697 | 20-MAY-07:00 | 26344.714 | 58181.634 | 9499.08 | 0 | 52971.49 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 245992000000 | 149438.53 | 27-JUN-19:15 | 36525.994 | 38968.112 | 10337.597 | 0 | 61122.039 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 264640000000 | 149858.609 | 29-JUL-07:00 | 26344.714 | 58181.634 | 9631.117 | 0 | 55616.366 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 262277000000 | 146258.455 | 19-AUG-07:00 | 26344.714 | 58181.634 | 9457.276 | 0 | 52190.052 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 246704000000 | 147435.488 | 03-SEP-07:00 | 26344.714 | 58181.634 | 9455.903 | 0 | 53368.458 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 238121000000 | 146806.113 | 07-OCT-07:00 | 26344.714 | 58181.634 | 9490.931 | 0 | 52704.056 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 210338000000 | 135238.693 | 05-NOV-08:00 | 26344.714 | 58181.634 | 9004.548 | 0 | 41623.019 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 198700000000 | 131021.612 | 16-DEC-08:00 | 26344.714 | 58181.634 | 8781.993 | 0 | 37628.493 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2715960000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 183085000000 | 131021.612 |  | 26344.714 | 38968.112 | 8781.993 | 0 | 37628.493 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 264640000000 | 149858.609 |  | 36525.994 | 58181.634 | 10337.597 | 0 | 61122.039 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 59619.12 | 5633.32 | 0 | 65252.44
Cost per Total Building Area ($/m2) | 14.85 | 1.4 | 0 | 16.26
Cost per Net Conditioned Building Area ($/m2) | 15.08 | 1.42 | 0 | 16.51

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3257.93 | 811.73 | 824.09
Net Site Energy | 3257.93 | 811.73 | 824.09
Total Source Energy | 848.06 | 211.3 | 214.52
Net Source Energy | 848.06 | 211.3 | 214.52
Area [m2]
Total Building Area | 4013.59
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 60.2
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 9.46 | 219.27 | 0 | 0 | 0 | 0
Cooling | 736.68 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 628.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 37.71 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 815.05 | 189.47 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 251.09 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 367.87 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2481.32 | 776.61 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 6.46 |  | 0
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 5.38 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.6 |  | 0
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 11.84 | 3.08 | 15.43
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 9.7 | 32.61 | 10.7631
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 14 | 1.87 | 12.9
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 16.16 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 12.9 | 2.96 | 77.16
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 6.46 | 8.89 | 206.12
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2157.2117
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 9.7 | 2.96 | 11.4999
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 11.84 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 6.46 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 8.6 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 11.8 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
Total | 4013.59 |  | 11621.74 |  | 1694.58 | 184.21 | 10.425 | 15.71 | 24.2519
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 10.5838 | 15.47 | 16.4088
Unconditioned Total | 60.2 |  | 174.32 |  | 21.18 | 0 | 0 |  | 539.3029
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_REARSTAIRSFLR1_2_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_CORRIDORFLR1_2_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 6.13 | 90 | 90 | E
W_CORRIDORFLR1_10_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.22 | 180 | 90 | S
S_CORRIDORFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 150.51 | 270 | 180
W_REARSTORAGEFLR1_2_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 163.06 | 90 | 180
W_RESTROOMFLR1_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 80.27 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM101_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_EMPLOYEELOUNGEFLR1_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_LAUNDRYROOMFLR1_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 97.83 | 90 | 180
W_ELEVATORCOREFLR1_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 15.05 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_FRONTSTORAGEFLR1_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 12.54 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 6.69 | 0 | 90 | N
W_CORRIDORFLR2_2_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 8.36 | 0 | 90 | N
W_CORRIDORFLR2_15_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 5.02 | 270 | 90 | W
W_REARSTORAGEFLR2_2_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 6.69 | 180 | 90 | S
W_GUESTROOM201_4_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 43.48 | 0 | 90 | N
W_ELEVATORCOREFLR2_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 5.02 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 0 | 90 | N
W_FRONTSTORAGEFLR2_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 4.18 | 0 | 90 | N
W_FRONTSTAIRSFLR2_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 22.58 | 270 | 90 | W
W_REARSTAIRSFLR3_2_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 6.69 | 0 | 90 | N
W_CORRIDORFLR3_2_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 5.02 | 270 | 90 | W
W_REARSTORAGEFLR3_2_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 6.69 | 180 | 90 | S
W_GUESTROOM301_4_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 43.48 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 5.02 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 4.18 | 0 | 90 | N
W_FRONTSTAIRSFLR3_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 22.58 | 270 | 90 | W
W_REARSTAIRSFLR4_2_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 6.69 | 0 | 90 | N
R_REARSTAIRSFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
W_CORRIDORFLR4_2_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 5.02 | 270 | 90 | W
R_CORRIDORFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 125.42 | 90 | 0
W_REARSTORAGEFLR4_2_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 6.69 | 180 | 90 | S
R_REARSTORAGEFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
W_GUESTROOM401_4_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 180 | 90 | S
R_GUESTROOM401_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM402_405_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 43.48 | 180 | 90 | S
R_GUESTROOM402_405_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.45 | 90 | 0
W_GUESTROOM406_408_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 35.12 | 180 | 90 | S
R_GUESTROOM406_408_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 105.36 | 90 | 0
W_GUESTROOM409_412_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 43.48 | 180 | 90 | S
R_GUESTROOM409_412_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.45 | 90 | 0
W_GUESTROOM413_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 180 | 90 | S
R_GUESTROOM413_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM414_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 0 | 90 | N
R_GUESTROOM414_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM415_418_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 43.48 | 0 | 90 | N
R_GUESTROOM415_418_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.44 | 90 | 0
W_ELEVATORCOREFLR4_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 5.02 | 0 | 90 | N
R_ELEVATORCOREFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 15.05 | 90 | 0
W_GUESTROOM419_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 0 | 90 | N
R_GUESTROOM419_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM420_423_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 43.48 | 0 | 90 | N
R_GUESTROOM420_423_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.44 | 90 | 0
W_GUESTROOM424_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 0 | 90 | N
R_GUESTROOM424_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_FRONTSTORAGEFLR4_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 4.18 | 0 | 90 | N
R_FRONTSTORAGEFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12.54 | 90 | 0
W_FRONTSTAIRSFLR4_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 22.58 | 270 | 90 | W
R_FRONTSTAIRSFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
W_CORRIDORFLR1_2_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_EAST | 2.69 | 2.69 | 6.49 | 0.391 | 0.39 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
D_CORRIDORFLR1_16_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_WEST | 4.44 | 4.44 | 6.49 | 0.391 | 0.39 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 2.69 | 2.69 | 6.49 | 0.391 | 0.39 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 2.97 | 2.97 | 6.49 | 0.391 | 0.39 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 2.97 | 2.97 | 6.49 | 0.391 | 0.39 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 2.97 | 2.97 | 6.49 | 0.391 | 0.39 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 2.97 | 2.97 | 6.49 | 0.391 | 0.39 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 2.96 | 2.96 | 6.49 | 0.391 | 0.39 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.65 | 1.65 | 6.49 | 0.391 | 0.39 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_GUESTROOM101_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.65 | 1.65 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_CORRIDORFLR2_2_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_EAST | 1.31 | 1.31 | 6.49 | 0.391 | 0.39 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_WEST | 1.31 | 1.31 | 6.49 | 0.391 | 0.39 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_GUESTROOM201_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.65 | 1.65 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 3.41 | 3.41 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.65 | 1.65 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.65 | 1.65 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_CORRIDORFLR3_2_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_EAST | 1.31 | 1.31 | 6.49 | 0.391 | 0.39 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_WEST | 1.31 | 1.31 | 6.49 | 0.391 | 0.39 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_GUESTROOM301_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.65 | 1.65 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 3.41 | 3.41 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.65 | 1.65 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.65 | 1.65 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_CORRIDORFLR4_2_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_EAST | 1.31 | 1.31 | 6.49 | 0.391 | 0.39 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_WEST | 1.31 | 1.31 | 6.49 | 0.391 | 0.39 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_GUESTROOM401_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.65 | 1.65 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.65 | 1.65 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 3.41 | 3.41 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.65 | 1.65 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM424_3_0_0 | 0 | N
Total or Average |  |  | 184.21 | 6.49 | 0.477 | 0.476
North Total or Average |  |  | 72.38 | 6.49 | 0.61 | 0.61
Non-North Total or Average |  |  | 111.83 | 6.49 | 0.391 | 0.39
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2013.6 | 1502.84 | 510.76 | 0.75 | 3.53
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2046.86 | 1531.51 | 515.35 | 0.75 | 3.53
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2223.94 | 1685.83 | 538.11 | 0.76 | 3.53
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2094.41 | 1616.88 | 477.53 | 0.77 | 3.59
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2060.76 | 1587.2 | 473.55 | 0.77 | 3.56
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2910.01 | 2295.41 | 614.6 | 0.79 | 3.39
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8833.55 | 6693.62 | 2139.93 | 0.76 | 2.95
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6991.33 | 5335.26 | 1656.07 | 0.76 | 2.94
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8638.29 | 6524.63 | 2113.66 | 0.76 | 2.94
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2468.15 | 1899.03 | 569.13 | 0.77 | 3.49
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2381.72 | 1873.28 | 508.44 | 0.79 | 3.52
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8829.7 | 6857.85 | 1971.85 | 0.78 | 2.96
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2587.6 | 2056.24 | 531.36 | 0.79 | 3.46
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8301.54 | 6392.33 | 1909.21 | 0.77 | 2.96
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2334.57 | 1831.38 | 503.19 | 0.78 | 3.54
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2882.04 | 2277.65 | 604.38 | 0.79 | 3.4
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8824 | 6685.34 | 2138.66 | 0.76 | 2.95
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7109.33 | 5437.67 | 1671.65 | 0.76 | 2.95
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8813.45 | 6676.23 | 2137.23 | 0.76 | 2.95
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2524.48 | 1948.05 | 576.43 | 0.77 | 3.47
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2442.63 | 1927.39 | 515.24 | 0.79 | 3.49
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8590.73 | 6647.06 | 1943.66 | 0.77 | 2.96
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2252.04 | 1753.96 | 498.08 | 0.78 | 3.55
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8487.08 | 6555.72 | 1931.36 | 0.77 | 2.96
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2384.69 | 1875.86 | 508.83 | 0.79 | 3.52
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3573.93 | 2845.89 | 728.04 | 0.8 | 3.21
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11052.26 | 8539.7 | 2512.57 | 0.77 | 2.96
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8944.45 | 6942.15 | 2002.3 | 0.78 | 2.96
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11079.57 | 8548.58 | 2530.98 | 0.77 | 2.96
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3142.45 | 2470.44 | 672.01 | 0.79 | 3.31
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3157.88 | 2520.48 | 637.4 | 0.8 | 3.32
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11114.01 | 8724.01 | 2390 | 0.78 | 2.97
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2894.03 | 2286.41 | 607.61 | 0.79 | 3.38
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11043.29 | 8661.58 | 2381.71 | 0.78 | 2.97
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3100.86 | 2469.8 | 631.07 | 0.8 | 3.34
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13777.64 | 9314.83 | 4462.81 | 0.68 | 3.66
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 21094.85 | 14261.88 | 6832.98 | 0.68 | 3.45
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2007.66 | 1378.93 | 628.73 | 0.69 | 3.66
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10980.58 | 7423.79 | 3556.8 | 0.68 | 3.67
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2210.8 | 1494.69 | 716.12 | 0.68 | 3.67
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7250.71 | 5151.25 | 2099.46 | 0.71 | 3.76
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26644.82 | 20759.91 | 5884.91 | 0.78 | 3.69
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3493.16 | 2361.67 | 1131.49 | 0.68 | 3.66
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8885.81 | 6327.59 | 2558.22 | 0.71 | 3.77
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8502.54 | 5748.42 | 2754.11 | 0.68 | 3.66
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8502.54 | 5748.42 | 2754.11 | 0.68 | 3.66
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10603.16 | 7168.62 | 3434.54 | 0.68 | 3.67
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 112.64 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 63.44 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 811.48 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 834.54 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1047.72 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 1037.7 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 826.47 | 1
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 200.24 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 223.84 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 204.29 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 1312.43 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 3303.33 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 2551.45 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 3224.01 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1048 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1016.49 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 2935.61 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 733.9 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 3092.42 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 939.11 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 334.81 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 251.26 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 233.51 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 1357.79 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 3424.18 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 2763.31 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 3406.59 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1090.69 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1065.43 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 3352.73 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 820.09 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 3345.35 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1001.01 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 378.06 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 581.11 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 482.23 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 1852.94 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 5381.91 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 4361.9 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 5371.81 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 1596.61 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 1575.81 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 5357.57 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 1439.86 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 5326.46 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 1547.35 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 37.17 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 741.21 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 8507.2 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 13025.32 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1245 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 6780.12 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1365.09 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 4484.31 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 22422.36 | 0.8
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 2156.9 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 5479.92 | 0.78
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 5250.01 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 5250.01 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 6547.07 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0.75 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0.43 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.1 | 66.39 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 67.89 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.12 | 76.05 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.12 | 74.68 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 73.09 | 1 | PTAC Fan
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 1.34 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 1.5 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 1.37 | 1 | Unit Heater Fans
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.17 | 108.87 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.47 | 301.8 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.38 | 242.79 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.46 | 292.93 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 87.33 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 88.54 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.5 | 319.14 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.15 | 98.39 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.46 | 294.27 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 86.28 | 1 | PTAC Fan
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 2.24 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 1.68 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 1.56 | 1 | Unit Heater Fans
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.17 | 108.27 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.47 | 301.36 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.39 | 248.18 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.47 | 300.89 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 89.92 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 91.45 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.48 | 307.87 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.13 | 81.9 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.48 | 302.99 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 88.67 | 1 | PTAC Fan
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 2.53 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.02 | 3.89 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.02 | 3.23 | 1 | Unit Heater Fans
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.21 | 136.51 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.62 | 394.84 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.51 | 322.79 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.62 | 394.54 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.18 | 116.69 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.19 | 121.23 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.65 | 411.33 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.17 | 108.65 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.64 | 407.99 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.19 | 118.5 | 1 | PTAC Fan
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0.25 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.02 | 4.97 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.55 | 643.55 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.85 | 967.73 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.08 | 97.89 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.44 | 512.9 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 103.27 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.33 | 386.16 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.52 | 1666.85 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.14 | 163.16 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.41 | 476.05 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.43 | 495.27 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 46303.3297 | 58.4774 | 230.4892 | 0 | 0.0007 | 78612.9805 | 18145.4846
February | 40314.2906 | 50.7168 | 197.9182 | 0 | 0.0006 | 67503.0174 | 15773.0931
March | 45371.5374 | 58.0443 | 236.2654 | 0 | 0.0007 | 80586.7388 | 17876.1799
April | 48083.4004 | 62.1174 | 258.8441 | 0 | 0.0007 | 88290.8684 | 19022.4759
May | 55218.2312 | 71.6187 | 301.2309 | 0 | 0.0009 | 102750.162 | 21881.7306
June | 58246.4882 | 75.7167 | 320.1365 | 0 | 0.0009 | 109199.6373 | 23103.7156
July | 64009.4165 | 83.3051 | 353.1687 | 0 | 0.001 | 120467.4632 | 25402.1016
August | 62405.5592 | 81.1897 | 343.9265 | 0 | 0.001 | 117314.7715 | 24761.9945
September | 56213.8886 | 73.0293 | 308.3324 | 0 | 0.0009 | 105173.0059 | 22291.6553
October | 51239.5473 | 66.3163 | 277.5367 | 0 | 0.0008 | 94667.392 | 20286.7592
November | 45378.3525 | 58.2464 | 239.0101 | 0 | 0.0007 | 81523.8222 | 17903.7988
December | 44584.4508 | 56.247 | 221.0983 | 0 | 0.0006 | 75409.7029 | 17464.2029
Annual Sum or Average | 617368.4925 | 795.0252 | 3287.9571 | 0 | 0.0093 | 1121500 | 243913.1919
Minimum of Months | 40314.2906 | 50.7168 | 197.9182 | 0 | 0.0006 | 67503.0174 | 15773.0931
Maximum of Months | 64009.4165 | 83.3051 | 353.1687 | 0 | 0.001 | 120467.4632 | 25402.1016
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 173931000000 | 122983.522 | 22-JAN-08:00 | 26344.714 | 58181.634 | 8783.607 | 0 | 29588.789 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 149351000000 | 110928.374 | 20-FEB-08:00 | 26344.714 | 58181.634 | 8086.103 | 0 | 18231.145 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 178298000000 | 124942.393 | 25-MAR-07:00 | 26344.714 | 58181.634 | 8831.039 | 0 | 31500.227 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 195344000000 | 135557.237 | 30-APR-07:00 | 26344.714 | 58181.634 | 9262.857 | 0 | 41683.254 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 227335000000 | 145463.568 | 26-MAY-19:15 | 36525.994 | 38968.112 | 10331.67 | 0 | 57153.004 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 241604000000 | 143234.055 | 11-JUN-07:00 | 26344.714 | 58181.634 | 9557.32 | 0 | 49065.609 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 266534000000 | 152251.74 | 04-JUL-07:00 | 26344.714 | 58181.634 | 10003.226 | 0 | 57637.388 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 259559000000 | 153756.661 | 06-AUG-19:15 | 36441.661 | 38950.562 | 10848.251 | 0 | 65031.398 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 232695000000 | 150445.307 | 16-SEP-07:00 | 26344.714 | 58181.634 | 9838.885 | 0 | 55995.296 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 209452000000 | 134628.006 | 29-OCT-19:30 | 36441.661 | 38950.562 | 9650.609 | 0 | 47100.386 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 180372000000 | 132366.999 | 04-NOV-08:00 | 26344.714 | 58181.634 | 9072.073 | 0 | 38683.8 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 166844000000 | 132124.057 | 03-DEC-08:00 | 26344.714 | 58181.634 | 9096.104 | 0 | 38416.827 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2481320000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 149351000000 | 110928.374 |  | 26344.714 | 38950.562 | 8086.103 | 0 | 18231.145 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 266534000000 | 153756.661 |  | 36525.994 | 58181.634 | 10848.251 | 0 | 65031.398 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 75312.29 | 6331.36 | 0 | 81643.65
Cost per Total Building Area ($/m2) | 18.76 | 1.58 | 0 | 20.34
Cost per Net Conditioned Building Area ($/m2) | 19.05 | 1.6 | 0 | 20.65

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3181.08 | 792.58 | 804.65
Net Site Energy | 3181.08 | 792.58 | 804.65
Total Source Energy | 8669.56 | 2160.05 | 2192.95
Net Source Energy | 8669.56 | 2160.05 | 2192.95
Area [m2]
Total Building Area | 4013.59
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 60.2
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 1.25 | 159.88 | 0 | 0 | 0 | 0
Cooling | 756.06 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 628.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 37.7 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 815.05 | 189.47 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 267.46 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 322.88 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2508.85 | 672.23 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 6.46 |  | 0
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 5.38 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.6 |  | 0
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 11.84 | 3.08 | 15.43
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 9.7 | 32.61 | 10.7631
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 14 | 1.87 | 12.9
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 16.16 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 12.9 | 2.96 | 77.16
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 6.46 | 8.89 | 206.12
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2157.2117
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 9.7 | 2.96 | 11.4999
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 11.84 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 6.46 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 8.6 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 11.8 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
Total | 4013.59 |  | 11621.74 |  | 1694.58 | 184.21 | 10.425 | 15.71 | 24.2519
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 10.5838 | 15.47 | 16.4088
Unconditioned Total | 60.2 |  | 174.32 |  | 21.18 | 0 | 0 |  | 539.3029
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_REARSTAIRSFLR1_2_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_CORRIDORFLR1_2_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 6.13 | 90 | 90 | E
W_CORRIDORFLR1_10_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.22 | 180 | 90 | S
S_CORRIDORFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 150.51 | 270 | 180
W_REARSTORAGEFLR1_2_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 163.06 | 90 | 180
W_RESTROOMFLR1_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 80.27 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM101_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_EMPLOYEELOUNGEFLR1_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_LAUNDRYROOMFLR1_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 97.83 | 90 | 180
W_ELEVATORCOREFLR1_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 15.05 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_FRONTSTORAGEFLR1_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 12.54 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 6.69 | 0 | 90 | N
W_CORRIDORFLR2_2_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 8.36 | 0 | 90 | N
W_CORRIDORFLR2_15_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 5.02 | 270 | 90 | W
W_REARSTORAGEFLR2_2_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 6.69 | 180 | 90 | S
W_GUESTROOM201_4_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 43.48 | 0 | 90 | N
W_ELEVATORCOREFLR2_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 5.02 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 0 | 90 | N
W_FRONTSTORAGEFLR2_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 4.18 | 0 | 90 | N
W_FRONTSTAIRSFLR2_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 22.58 | 270 | 90 | W
W_REARSTAIRSFLR3_2_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 6.69 | 0 | 90 | N
W_CORRIDORFLR3_2_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 5.02 | 270 | 90 | W
W_REARSTORAGEFLR3_2_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 6.69 | 180 | 90 | S
W_GUESTROOM301_4_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 43.48 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 5.02 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 4.18 | 0 | 90 | N
W_FRONTSTAIRSFLR3_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 22.58 | 270 | 90 | W
W_REARSTAIRSFLR4_2_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 6.69 | 0 | 90 | N
R_REARSTAIRSFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
W_CORRIDORFLR4_2_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 5.02 | 270 | 90 | W
R_CORRIDORFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 125.42 | 90 | 0
W_REARSTORAGEFLR4_2_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 6.69 | 180 | 90 | S
R_REARSTORAGEFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
W_GUESTROOM401_4_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 180 | 90 | S
R_GUESTROOM401_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM402_405_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 43.48 | 180 | 90 | S
R_GUESTROOM402_405_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.45 | 90 | 0
W_GUESTROOM406_408_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 35.12 | 180 | 90 | S
R_GUESTROOM406_408_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 105.36 | 90 | 0
W_GUESTROOM409_412_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 43.48 | 180 | 90 | S
R_GUESTROOM409_412_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.45 | 90 | 0
W_GUESTROOM413_5_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 180 | 90 | S
R_GUESTROOM413_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM414_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 0 | 90 | N
R_GUESTROOM414_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM415_418_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 43.48 | 0 | 90 | N
R_GUESTROOM415_418_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.44 | 90 | 0
W_ELEVATORCOREFLR4_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 5.02 | 0 | 90 | N
R_ELEVATORCOREFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 15.05 | 90 | 0
W_GUESTROOM419_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 0 | 90 | N
R_GUESTROOM419_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM420_423_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 43.48 | 0 | 90 | N
R_GUESTROOM420_423_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.44 | 90 | 0
W_GUESTROOM424_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 10.87 | 0 | 90 | N
R_GUESTROOM424_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_FRONTSTORAGEFLR4_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 4.18 | 0 | 90 | N
R_FRONTSTORAGEFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12.54 | 90 | 0
W_FRONTSTAIRSFLR4_3_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 22.58 | 270 | 90 | W
R_FRONTSTAIRSFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
W_CORRIDORFLR1_2_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_EAST | 2.69 | 2.69 | 6.49 | 0.391 | 0.39 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
D_CORRIDORFLR1_16_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_WEST | 4.44 | 4.44 | 6.49 | 0.391 | 0.39 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 2.69 | 2.69 | 6.49 | 0.391 | 0.39 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 2.97 | 2.97 | 6.49 | 0.391 | 0.39 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 2.97 | 2.97 | 6.49 | 0.391 | 0.39 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 2.97 | 2.97 | 6.49 | 0.391 | 0.39 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 2.97 | 2.97 | 6.49 | 0.391 | 0.39 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 2.96 | 2.96 | 6.49 | 0.391 | 0.39 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.65 | 1.65 | 6.49 | 0.391 | 0.39 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_GUESTROOM101_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.65 | 1.65 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_CORRIDORFLR2_2_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_EAST | 1.31 | 1.31 | 6.49 | 0.391 | 0.39 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_WEST | 1.31 | 1.31 | 6.49 | 0.391 | 0.39 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_GUESTROOM201_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.65 | 1.65 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 3.41 | 3.41 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.65 | 1.65 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.65 | 1.65 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_CORRIDORFLR3_2_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_EAST | 1.31 | 1.31 | 6.49 | 0.391 | 0.39 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_WEST | 1.31 | 1.31 | 6.49 | 0.391 | 0.39 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_GUESTROOM301_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.65 | 1.65 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 3.41 | 3.41 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.65 | 1.65 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.65 | 1.65 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_CORRIDORFLR4_2_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_EAST | 1.31 | 1.31 | 6.49 | 0.391 | 0.39 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_WEST | 1.31 | 1.31 | 6.49 | 0.391 | 0.39 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_GUESTROOM401_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.65 | 1.65 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.65 | 1.65 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 3.41 | 3.41 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.64 | 1.64 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 1.65 | 1.65 | 6.49 | 0.391 | 0.39 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM424_3_0_0 | 0 | N
Total or Average |  |  | 184.21 | 6.49 | 0.477 | 0.476
North Total or Average |  |  | 72.38 | 6.49 | 0.61 | 0.61
Non-North Total or Average |  |  | 111.83 | 6.49 | 0.391 | 0.39
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2000.73 | 1534.12 | 466.61 | 0.77 | 3.58
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2045.98 | 1572.17 | 473.82 | 0.77 | 3.57
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2286.21 | 1776.14 | 510.07 | 0.78 | 3.55
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2035.6 | 1625.74 | 409.86 | 0.8 | 3.61
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1938.8 | 1542.66 | 396.15 | 0.8 | 3.64
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3275.54 | 2616.03 | 659.51 | 0.8 | 3.31
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9573.65 | 7457.29 | 2116.36 | 0.78 | 2.97
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7657.8 | 6002.42 | 1655.38 | 0.78 | 2.97
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9325.46 | 7247.89 | 2077.57 | 0.78 | 2.96
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2764.87 | 2178.22 | 586.65 | 0.79 | 3.43
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2640.55 | 2108.89 | 531.66 | 0.8 | 3.47
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9137.11 | 7297.4 | 1839.71 | 0.8 | 2.98
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2801.16 | 2237.16 | 564 | 0.8 | 3.42
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8470.33 | 6760.06 | 1710.27 | 0.8 | 2.98
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2533.34 | 2023.26 | 510.07 | 0.8 | 3.48
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3279.83 | 2619.45 | 660.38 | 0.8 | 3.31
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9627.07 | 7502.39 | 2124.69 | 0.78 | 2.96
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7865.86 | 6178.39 | 1687.47 | 0.79 | 2.97
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9612.31 | 7489.94 | 2122.38 | 0.78 | 2.96
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2865.15 | 2263.09 | 602.06 | 0.79 | 3.41
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2764.29 | 2207.71 | 556.57 | 0.8 | 3.44
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8930.92 | 7132.73 | 1798.19 | 0.8 | 2.99
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2383.5 | 1903.59 | 479.91 | 0.8 | 3.52
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8793.96 | 7023.34 | 1770.62 | 0.8 | 2.98
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2645.19 | 2112.6 | 532.6 | 0.8 | 3.46
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4161.62 | 3323.7 | 837.92 | 0.8 | 3.06
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12135.95 | 9679.66 | 2456.29 | 0.8 | 2.98
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9997.65 | 7984.68 | 2012.97 | 0.8 | 2.98
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12135 | 9678.86 | 2456.14 | 0.8 | 2.98
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3649.53 | 2914.71 | 734.81 | 0.8 | 3.2
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3717.6 | 2969.08 | 748.52 | 0.8 | 3.16
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12206.31 | 9748.63 | 2457.68 | 0.8 | 2.99
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3242.76 | 2589.84 | 652.91 | 0.8 | 3.31
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12110.41 | 9672.04 | 2438.37 | 0.8 | 2.98
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3598.99 | 2874.35 | 724.64 | 0.8 | 3.21
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12603.04 | 8878.54 | 3724.5 | 0.7 | 3.74
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 21666.29 | 14982.29 | 6684.01 | 0.69 | 3.48
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1711.3 | 1261.38 | 449.92 | 0.74 | 3.9
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11595.96 | 7839.84 | 3756.13 | 0.68 | 3.66
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2210.8 | 1494.69 | 716.12 | 0.68 | 3.67
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6281.41 | 4785.09 | 1496.32 | 0.76 | 3.92
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 25905.18 | 20689.31 | 5215.87 | 0.8 | 3.74
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3279.4 | 2297.4 | 982 | 0.7 | 3.76
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7534.72 | 5775.75 | 1758.97 | 0.77 | 3.96
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8502.54 | 5748.42 | 2754.11 | 0.68 | 3.66
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8502.54 | 5748.42 | 2754.11 | 0.68 | 3.66
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12020.84 | 8286.34 | 3734.51 | 0.69 | 3.7
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 686.86 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 707 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 901.37 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 896.26 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 702.49 | 1
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 40.07 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 38.01 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 65.53 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 1006.55 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 2527.08 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 1935.15 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 2476.76 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 843.81 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 816.61 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 2476.76 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 619.19 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 2476.76 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 739.79 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 148.64 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 65.28 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 91.19 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 1039.5 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 2611.39 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 2105.44 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 2599.85 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 877.29 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 855 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 2557.12 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 619.19 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 2554.96 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 788.52 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 183.46 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 309.79 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 278.4 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 1435.25 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 4170.3 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 3380.17 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 4164.96 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 1282.47 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 1262.85 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 4162 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 1115.55 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 4134.87 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 1230.82 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 452.38 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 7326.19 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 11997.19 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1066.28 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 6040.93 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1151.72 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 3900.29 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 21390.01 | 0.8
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 1878.99 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 4736.13 | 0.78
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 4429.41 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 4429.41 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 6600.77 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 70.24 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 72.18 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.13 | 82.68 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.12 | 78.25 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.12 | 73.93 | 1 | PTAC Fan
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0.28 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0.26 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0.46 | 1 | Unit Heater Fans
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.2 | 125.92 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.55 | 348.3 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.44 | 282.51 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.53 | 337.59 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.16 | 103.16 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.16 | 101.51 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.55 | 351.25 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.17 | 107.68 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.51 | 325.11 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.15 | 97.39 | 1 | PTAC Fan
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 1.03 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0.45 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0.63 | 1 | Unit Heater Fans
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.2 | 126.08 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.55 | 350.6 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.46 | 291.54 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.55 | 349.97 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.17 | 107.51 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.17 | 106.27 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.54 | 343.32 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 91.63 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.53 | 338.06 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.16 | 101.69 | 1 | PTAC Fan
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 1.27 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 2.15 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 1.93 | 1 | Unit Heater Fans
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.25 | 159.98 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.73 | 465.2 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.6 | 384.33 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.73 | 465.15 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.22 | 140.3 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.22 | 142.91 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.74 | 469.24 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.2 | 124.66 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.73 | 465.55 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.22 | 138.35 | 1 | PTAC Fan
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.02 | 3.14 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.57 | 656.88 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.93 | 1056.48 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 99.83 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.47 | 541.64 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 103.27 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 396 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.56 | 1711.45 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.15 | 168.47 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.42 | 481.86 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.51 | 591.84 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 37433.2614 | 59.2511 | 182.9725 | 0 | 0.0005 | 1351410 | 15511.3144
February | 34057.2518 | 54.0199 | 167.2845 | 0 | 0.0005 | 1235550 | 14123.7651
March | 39692.8524 | 64.6083 | 206.8982 | 0 | 0.0006 | 1528230 | 16627.6852
April | 40703.3543 | 66.9009 | 216.8522 | 0 | 0.0006 | 1601780 | 17116.5069
May | 45501.3882 | 75.296 | 246.0957 | 0 | 0.0007 | 1817820 | 19185.6285
June | 51484.1852 | 85.6586 | 281.7975 | 0 | 0.0008 | 2081560 | 21755.0107
July | 56915.8864 | 94.8856 | 312.9015 | 0 | 0.0009 | 2311320 | 24069.4173
August | 55324.634 | 92.159 | 303.6192 | 0 | 0.0008 | 2242750 | 23389.0186
September | 49966.2822 | 83.0021 | 272.5414 | 0 | 0.0007 | 2013180 | 21100.3608
October | 43289.0059 | 71.3912 | 232.3673 | 0 | 0.0006 | 1716400 | 18228.1395
November | 37729.2567 | 61.3899 | 196.5022 | 0 | 0.0005 | 1451440 | 15802.8697
December | 37670.6705 | 59.4331 | 182.731 | 0 | 0.0005 | 1349620 | 15590.0935
Annual Sum or Average | 529768.0291 | 867.9955 | 2802.5631 | 0 | 0.0077 | 20701100 | 222499.8103
Minimum of Months | 34057.2518 | 54.0199 | 167.2845 | 0 | 0.0005 | 1235550 | 14123.7651
Maximum of Months | 56915.8864 | 94.8856 | 312.9015 | 0 | 0.0009 | 2311320 | 24069.4173
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 163783000000 | 107283.156 | 29-JAN-08:00 | 26344.714 | 58181.634 | 8235.749 | 0 | 14436.28 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 149741000000 | 104327.199 | 28-FEB-20:15 | 36525.994 | 38968.112 | 8763.644 | 0 | 17584.66 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 185212000000 | 124500.869 | 17-MAR-19:15 | 36525.994 | 38968.112 | 9806.327 | 0 | 36715.647 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 194127000000 | 124413.402 | 01-APR-17:15 | 32698.342 | 37261.294 | 9954.233 | 0 | 44414.754 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 220309000000 | 147036.329 | 28-MAY-19:30 | 36441.661 | 38950.562 | 11045.829 | 0 | 58113.488 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 252273000000 | 169987.984 | 27-JUN-19:15 | 36525.994 | 38968.112 | 12253.267 | 0 | 82155.832 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 280119000000 | 166111.908 | 11-JUL-19:15 | 36525.994 | 38968.112 | 12144.014 | 0 | 78389.009 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 271809000000 | 168111.942 | 01-AUG-19:30 | 36525.994 | 38968.112 | 12083.293 | 0 | 78049.754 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 243986000000 | 152148.367 | 09-SEP-19:15 | 36357.328 | 38915.462 | 11367.397 | 0 | 63023.392 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 208018000000 | 128872.456 | 02-OCT-19:15 | 36525.994 | 38968.112 | 10066.243 | 0 | 40827.318 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 175906000000 | 108770.251 | 12-NOV-08:00 | 26344.714 | 58181.634 | 8351.38 | 0 | 15807.744 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 163566000000 | 103367.823 | 10-DEC-08:00 | 26344.714 | 58181.634 | 7816.526 | 0 | 10940.17 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2508850000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 149741000000 | 103367.823 |  | 26344.714 | 37261.294 | 7816.526 | 0 | 10940.17 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 280119000000 | 169987.984 |  | 36525.994 | 58181.634 | 12253.267 | 0 | 82155.832 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 61803.42 | 5692.29 | 0 | 67495.71
Cost per Total Building Area ($/m2) | 15.4 | 1.42 | 0 | 16.82
Cost per Net Conditioned Building Area ($/m2) | 15.63 | 1.44 | 0 | 17.07

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3276.49 | 816.35 | 828.78
Net Site Energy | 3276.49 | 816.35 | 828.78
Total Source Energy | 8688.68 | 2164.82 | 2197.78
Net Source Energy | 8688.68 | 2164.82 | 2197.78
Area [m2]
Total Building Area | 4013.59
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 60.2
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 12.45 | 394.24 | 0 | 0 | 0 | 0
Cooling | 511.85 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 628.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 37.76 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 815.05 | 189.47 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 241.01 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 443.32 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2249.45 | 1027.03 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 6.46 |  | 0
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 5.38 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.6 |  | 0
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 11.84 | 3.08 | 15.43
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 9.7 | 32.61 | 10.7631
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 14 | 1.87 | 12.9
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 16.16 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 12.9 | 2.96 | 77.16
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 6.46 | 8.89 | 206.12
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2157.2117
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 9.7 | 2.96 | 11.4999
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 11.84 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 6.46 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 8.6 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 11.8 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
Total | 4013.59 |  | 11621.74 |  | 1694.58 | 184.21 | 10.425 | 15.71 | 24.2519
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 10.5838 | 15.47 | 16.4088
Unconditioned Total | 60.2 |  | 174.32 |  | 21.18 | 0 | 0 |  | 539.3029
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_REARSTAIRSFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_CORRIDORFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.13 | 90 | 90 | E
W_CORRIDORFLR1_10_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.22 | 180 | 90 | S
S_CORRIDORFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 150.51 | 270 | 180
W_REARSTORAGEFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 163.06 | 90 | 180
W_RESTROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 80.27 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM101_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_EMPLOYEELOUNGEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_LAUNDRYROOMFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 97.83 | 90 | 180
W_ELEVATORCOREFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 15.05 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_FRONTSTORAGEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 12.54 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.69 | 0 | 90 | N
W_CORRIDORFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 8.36 | 0 | 90 | N
W_CORRIDORFLR2_15_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.02 | 270 | 90 | W
W_REARSTORAGEFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.69 | 180 | 90 | S
W_GUESTROOM201_4_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 0 | 90 | N
W_ELEVATORCOREFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.02 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 0 | 90 | N
W_FRONTSTORAGEFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 4.18 | 0 | 90 | N
W_FRONTSTAIRSFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 270 | 90 | W
W_REARSTAIRSFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.69 | 0 | 90 | N
W_CORRIDORFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.02 | 270 | 90 | W
W_REARSTORAGEFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.69 | 180 | 90 | S
W_GUESTROOM301_4_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.02 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 4.18 | 0 | 90 | N
W_FRONTSTAIRSFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 270 | 90 | W
W_REARSTAIRSFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.69 | 0 | 90 | N
R_REARSTAIRSFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
W_CORRIDORFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.02 | 270 | 90 | W
R_CORRIDORFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 125.42 | 90 | 0
W_REARSTORAGEFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.69 | 180 | 90 | S
R_REARSTORAGEFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
W_GUESTROOM401_4_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 180 | 90 | S
R_GUESTROOM401_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM402_405_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 180 | 90 | S
R_GUESTROOM402_405_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.45 | 90 | 0
W_GUESTROOM406_408_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 35.12 | 180 | 90 | S
R_GUESTROOM406_408_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 105.36 | 90 | 0
W_GUESTROOM409_412_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 180 | 90 | S
R_GUESTROOM409_412_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.45 | 90 | 0
W_GUESTROOM413_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 180 | 90 | S
R_GUESTROOM413_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM414_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 0 | 90 | N
R_GUESTROOM414_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM415_418_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 0 | 90 | N
R_GUESTROOM415_418_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.44 | 90 | 0
W_ELEVATORCOREFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.02 | 0 | 90 | N
R_ELEVATORCOREFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 15.05 | 90 | 0
W_GUESTROOM419_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 0 | 90 | N
R_GUESTROOM419_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM420_423_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 0 | 90 | N
R_GUESTROOM420_423_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.44 | 90 | 0
W_GUESTROOM424_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 0 | 90 | N
R_GUESTROOM424_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_FRONTSTORAGEFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 4.18 | 0 | 90 | N
R_FRONTSTORAGEFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12.54 | 90 | 0
W_FRONTSTAIRSFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 270 | 90 | W
R_FRONTSTAIRSFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
W_CORRIDORFLR1_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 2.69 | 2.69 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
D_CORRIDORFLR1_16_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.44 | 4.44 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 2.69 | 2.69 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 2.97 | 2.97 | 3.18 | 0.402 | 0.495 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 2.97 | 2.97 | 3.18 | 0.402 | 0.495 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 2.97 | 2.97 | 3.18 | 0.402 | 0.495 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 2.97 | 2.97 | 3.18 | 0.402 | 0.495 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 2.96 | 2.96 | 3.18 | 0.402 | 0.495 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_GUESTROOM101_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_CORRIDORFLR2_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 1.31 | 1.31 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 1.31 | 1.31 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_GUESTROOM201_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 3.41 | 3.41 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_CORRIDORFLR3_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 1.31 | 1.31 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 1.31 | 1.31 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_GUESTROOM301_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 3.41 | 3.41 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_CORRIDORFLR4_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 1.31 | 1.31 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 1.31 | 1.31 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_GUESTROOM401_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 3.41 | 3.41 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM424_3_0_0 | 0 | N
Total or Average |  |  | 184.21 | 3.18 | 0.441 | 0.545
North Total or Average |  |  | 72.38 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 111.83 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1875.7 | 1430.93 | 444.77 | 0.76 | 3.56
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1906.99 | 1458.5 | 448.5 | 0.76 | 3.55
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2029.79 | 1566.88 | 462.91 | 0.77 | 3.57
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1834.3 | 1438.39 | 395.9 | 0.78 | 3.62
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1851.83 | 1454.17 | 397.66 | 0.79 | 3.61
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2512.08 | 2006.29 | 505.79 | 0.8 | 3.49
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8446.71 | 6566.4 | 1880.31 | 0.78 | 2.96
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6717.07 | 5261.31 | 1455.76 | 0.78 | 2.97
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8251.27 | 6393.36 | 1857.91 | 0.77 | 2.96
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2312.74 | 1820.15 | 492.59 | 0.79 | 3.56
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2174.53 | 1736.7 | 437.83 | 0.8 | 3.59
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8130.22 | 6466.53 | 1663.69 | 0.8 | 2.98
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2512.46 | 2006.59 | 505.87 | 0.8 | 3.49
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7604.56 | 5991.72 | 1612.85 | 0.79 | 2.98
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2138.57 | 1707.98 | 430.59 | 0.8 | 3.61
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2496 | 1993.44 | 502.56 | 0.8 | 3.5
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8441.76 | 6562.01 | 1879.75 | 0.78 | 2.96
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6842.54 | 5372.72 | 1469.83 | 0.79 | 2.97
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8434.23 | 6555.34 | 1878.88 | 0.78 | 2.96
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2372.71 | 1873.49 | 499.22 | 0.79 | 3.53
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2256.23 | 1801.95 | 454.28 | 0.8 | 3.58
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7893.36 | 6252.4 | 1640.96 | 0.79 | 2.98
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2068.13 | 1648.95 | 419.19 | 0.8 | 3.6
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7794.37 | 6162.98 | 1631.38 | 0.79 | 2.98
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2202.97 | 1759.41 | 443.56 | 0.8 | 3.57
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3156.44 | 2520.9 | 635.53 | 0.8 | 3.32
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10518.49 | 8291.66 | 2226.83 | 0.79 | 2.98
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8524.54 | 6769.09 | 1755.44 | 0.79 | 2.98
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10524.68 | 8297.16 | 2227.52 | 0.79 | 2.98
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2963.23 | 2366.6 | 596.63 | 0.8 | 3.38
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2985.99 | 2384.78 | 601.21 | 0.8 | 3.37
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10285.34 | 8214.44 | 2070.9 | 0.8 | 2.98
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2708.52 | 2163.17 | 545.35 | 0.8 | 3.43
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10202.58 | 8148.34 | 2054.24 | 0.8 | 2.99
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2933.1 | 2342.54 | 590.56 | 0.8 | 3.39
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13578.43 | 9180.15 | 4398.28 | 0.68 | 3.67
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 21042.26 | 14226.32 | 6815.94 | 0.68 | 3.45
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1814.42 | 1274.44 | 539.98 | 0.7 | 3.73
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11071.95 | 7485.56 | 3586.39 | 0.68 | 3.67
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2210.8 | 1494.69 | 716.12 | 0.68 | 3.67
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6789.33 | 4956.62 | 1832.71 | 0.73 | 3.81
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26138.3 | 20756.03 | 5382.26 | 0.79 | 3.73
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3456.95 | 2337.19 | 1119.76 | 0.68 | 3.67
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7889.54 | 5725.39 | 2164.16 | 0.73 | 3.81
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8502.54 | 5748.42 | 2754.11 | 0.68 | 3.66
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8502.54 | 5748.42 | 2754.11 | 0.68 | 3.66
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10065.82 | 6805.33 | 3260.49 | 0.68 | 3.67
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 140.41 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 54.11 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 847.42 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 868.42 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1079.03 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 1078.33 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 867.99 | 1
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 238.17 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 222.48 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 175.18 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 1269.31 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 3291.97 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 2503.28 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 3230.3 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1043.53 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1013.98 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 3166.76 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 791.69 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 3166.76 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 937.41 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 337.8 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 252.43 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 204.61 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 1315.23 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 3423.45 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 2714.09 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 3411.44 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1087 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1063.34 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 3364.41 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 816.52 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 3363.26 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1001.76 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 380.22 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 647.66 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 497.12 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 1883.6 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 5661.89 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 4540.54 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 5656.03 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 1666.18 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 1647.38 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 5654.35 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 1519.19 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 5626.34 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 1623.61 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 50.85 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 811.15 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 9044.39 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 14015.93 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1315.44 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 7374.85 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1472.58 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 4785.72 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 22915.8 | 0.8
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 2302.62 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 5648.97 | 0.78
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 5663.41 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 5663.41 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 6704.69 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0.97 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0.37 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.1 | 65.09 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.1 | 66.56 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 72.36 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 67.74 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 68.59 | 1 | PTAC Fan
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 1.65 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 1.54 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 1.21 | 1 | Unit Heater Fans
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.15 | 96.57 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.48 | 305.93 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.39 | 247.42 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.47 | 296.64 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 86.09 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.13 | 83.59 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.49 | 309.75 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.15 | 96.58 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.45 | 283.79 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.13 | 82.21 | 1 | PTAC Fan
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 2.34 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 1.75 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 1.42 | 1 | Unit Heater Fans
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.15 | 95.95 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.48 | 305.69 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.4 | 253.41 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.48 | 305.34 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 88.97 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 86.73 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.47 | 298.03 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.12 | 79.21 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.46 | 293.15 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.13 | 84.69 | 1 | PTAC Fan
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 2.63 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.02 | 4.49 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.02 | 3.44 | 1 | Unit Heater Fans
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.19 | 121.34 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.62 | 392.96 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.51 | 323.62 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.62 | 393.25 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.18 | 113.91 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.18 | 114.79 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.62 | 395.39 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.16 | 104.12 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.62 | 392.21 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.18 | 112.75 | 1 | PTAC Fan
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0.35 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.03 | 5.62 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.55 | 634.24 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.85 | 965.32 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.08 | 93.85 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.45 | 517.16 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 103.27 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.33 | 386.97 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.56 | 1705.39 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.14 | 161.47 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.38 | 443.11 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.41 | 470.17 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 39685.1816 | 67.7305 | 155.6074 | 0 | 0.0006 | 276715.3946 | 16663.4599
February | 35483.4787 | 61.3956 | 143.2308 | 0 | 0.0005 | 254715.6876 | 14976.4142
March | 37631.3094 | 67.1677 | 161.9785 | 0 | 0.0006 | 288078.7107 | 16072.8061
April | 37824.2759 | 69.1288 | 170.734 | 0 | 0.0006 | 303667.163 | 16304.5255
May | 42080.0995 | 78.4248 | 197.3854 | 0 | 0.0007 | 351084.4474 | 18279.2286
June | 44295.3669 | 83.0599 | 210.2597 | 0 | 0.0008 | 373988.4846 | 19288.3025
July | 48416.084 | 91.0707 | 231.2111 | 0 | 0.0008 | 411257.3221 | 21108.8693
August | 47469.8042 | 89.2582 | 226.5325 | 0 | 0.0008 | 402935.1694 | 20693.2947
September | 43456.5237 | 81.4764 | 206.2262 | 0 | 0.0008 | 366813.9291 | 18922.0554
October | 39002.093 | 71.9337 | 179.2481 | 0 | 0.0007 | 318816.8368 | 16872.4764
November | 36319.8016 | 64.6602 | 155.5167 | 0 | 0.0006 | 276584.6252 | 15497.2598
December | 38688.3428 | 66.8174 | 155.5627 | 0 | 0.0006 | 276644.8509 | 16317.6902
Annual Sum or Average | 490352.3613 | 892.1239 | 2193.4931 | 0 | 0.0081 | 3901300 | 210996.3825
Minimum of Months | 35483.4787 | 61.3956 | 143.2308 | 0 | 0.0005 | 254715.6876 | 14976.4142
Maximum of Months | 48416.084 | 91.0707 | 231.2111 | 0 | 0.0008 | 411257.3221 | 21108.8693
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 159551000000 | 106615.661 | 14-JAN-08:15 | 26344.714 | 58181.634 | 7104.892 | 14845.231 | 54.412 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 146867000000 | 106526.259 | 20-FEB-08:00 | 26344.714 | 58181.634 | 7801.945 | 0 | 14113.187 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 166103000000 | 110024.441 | 28-MAR-19:15 | 36525.994 | 38968.112 | 8814.616 | 0 | 23230.93 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 175092000000 | 120437.631 | 16-APR-07:00 | 26344.714 | 58181.634 | 8812.491 | 0 | 27014.014 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 202432000000 | 133443.44 | 14-MAY-19:30 | 36441.661 | 38950.562 | 10005.844 | 0 | 45560.584 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 215638000000 | 137690.812 | 08-JUN-19:15 | 36525.994 | 38968.112 | 10178.709 | 0 | 51933.218 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 237127000000 | 147026.482 | 02-JUL-19:15 | 36441.661 | 38950.562 | 10815.641 | 0 | 60733.839 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 232329000000 | 138109.571 | 14-AUG-19:30 | 36525.994 | 38968.112 | 10134.607 | 0 | 49996.069 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 211501000000 | 129990.755 | 10-SEP-19:15 | 36441.661 | 38950.562 | 9781.42 | 0 | 42332.324 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 183827000000 | 119087.634 | 21-OCT-19:15 | 36357.328 | 38915.462 | 9182.981 | 0 | 32147.074 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 159476000000 | 111345.35 | 23-NOV-08:00 | 26344.714 | 58181.634 | 8216.442 | 0 | 18517.782 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 159511000000 | 108860.011 | 31-DEC-08:00 | 26344.714 | 58181.634 | 7940.101 | 0 | 16308.784 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2249450000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 146867000000 | 106526.259 |  | 26344.714 | 38915.462 | 7104.892 | 0 | 54.412 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 237127000000 | 147026.482 |  | 36525.994 | 58181.634 | 10815.641 | 14845.231 | 60733.839 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 63103.27 | 10623.35 | 0 | 73726.62
Cost per Total Building Area ($/m2) | 15.72 | 2.65 | 0 | 18.37
Cost per Net Conditioned Building Area ($/m2) | 15.96 | 2.69 | 0 | 18.65

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2814.9 | 701.34 | 712.02
Net Site Energy | 2814.9 | 701.34 | 712.02
Total Source Energy | 7242.37 | 1804.46 | 1831.94
Net Source Energy | 7242.37 | 1804.46 | 1831.94
Area [m2]
Total Building Area | 4013.59
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 60.2
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 115.64 | 0 | 0 | 0 | 0
Cooling | 367.72 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 628.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 37.76 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 815.05 | 189.47 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 229.27 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 428.65 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2081.13 | 733.77 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 6.46 |  | 0
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 5.38 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.6 |  | 0
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 11.84 | 3.08 | 15.43
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 9.7 | 32.61 | 10.7631
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 14 | 1.87 | 12.9
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 16.16 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 12.9 | 2.96 | 77.16
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 6.46 | 8.89 | 206.12
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2157.2117
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 9.7 | 2.96 | 11.4999
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 11.84 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 6.46 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 8.6 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 11.8 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
Total | 4013.59 |  | 11621.74 |  | 1694.58 | 184.21 | 10.425 | 15.71 | 24.2519
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 10.5838 | 15.47 | 16.4088
Unconditioned Total | 60.2 |  | 174.32 |  | 21.18 | 0 | 0 |  | 539.3029
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_REARSTAIRSFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_CORRIDORFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.13 | 90 | 90 | E
W_CORRIDORFLR1_10_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.22 | 180 | 90 | S
S_CORRIDORFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 150.51 | 270 | 180
W_REARSTORAGEFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 163.06 | 90 | 180
W_RESTROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 80.27 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM101_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_EMPLOYEELOUNGEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_LAUNDRYROOMFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 97.83 | 90 | 180
W_ELEVATORCOREFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 15.05 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_FRONTSTORAGEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 12.54 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.69 | 0 | 90 | N
W_CORRIDORFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 8.36 | 0 | 90 | N
W_CORRIDORFLR2_15_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.02 | 270 | 90 | W
W_REARSTORAGEFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.69 | 180 | 90 | S
W_GUESTROOM201_4_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 0 | 90 | N
W_ELEVATORCOREFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.02 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 0 | 90 | N
W_FRONTSTORAGEFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 4.18 | 0 | 90 | N
W_FRONTSTAIRSFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 270 | 90 | W
W_REARSTAIRSFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.69 | 0 | 90 | N
W_CORRIDORFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.02 | 270 | 90 | W
W_REARSTORAGEFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.69 | 180 | 90 | S
W_GUESTROOM301_4_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.02 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 4.18 | 0 | 90 | N
W_FRONTSTAIRSFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 270 | 90 | W
W_REARSTAIRSFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.69 | 0 | 90 | N
R_REARSTAIRSFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
W_CORRIDORFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.02 | 270 | 90 | W
R_CORRIDORFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 125.42 | 90 | 0
W_REARSTORAGEFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.69 | 180 | 90 | S
R_REARSTORAGEFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
W_GUESTROOM401_4_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 180 | 90 | S
R_GUESTROOM401_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM402_405_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 180 | 90 | S
R_GUESTROOM402_405_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.45 | 90 | 0
W_GUESTROOM406_408_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 35.12 | 180 | 90 | S
R_GUESTROOM406_408_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 105.36 | 90 | 0
W_GUESTROOM409_412_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 180 | 90 | S
R_GUESTROOM409_412_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.45 | 90 | 0
W_GUESTROOM413_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 180 | 90 | S
R_GUESTROOM413_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM414_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 0 | 90 | N
R_GUESTROOM414_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM415_418_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 0 | 90 | N
R_GUESTROOM415_418_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.44 | 90 | 0
W_ELEVATORCOREFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.02 | 0 | 90 | N
R_ELEVATORCOREFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 15.05 | 90 | 0
W_GUESTROOM419_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 0 | 90 | N
R_GUESTROOM419_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM420_423_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 0 | 90 | N
R_GUESTROOM420_423_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.44 | 90 | 0
W_GUESTROOM424_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 0 | 90 | N
R_GUESTROOM424_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_FRONTSTORAGEFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 4.18 | 0 | 90 | N
R_FRONTSTORAGEFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12.54 | 90 | 0
W_FRONTSTAIRSFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 270 | 90 | W
R_FRONTSTAIRSFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
W_CORRIDORFLR1_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 2.69 | 2.69 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
D_CORRIDORFLR1_16_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.44 | 4.44 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 2.69 | 2.69 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 2.97 | 2.97 | 3.18 | 0.402 | 0.495 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 2.97 | 2.97 | 3.18 | 0.402 | 0.495 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 2.97 | 2.97 | 3.18 | 0.402 | 0.495 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 2.97 | 2.97 | 3.18 | 0.402 | 0.495 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 2.96 | 2.96 | 3.18 | 0.402 | 0.495 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_GUESTROOM101_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_CORRIDORFLR2_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 1.31 | 1.31 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 1.31 | 1.31 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_GUESTROOM201_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 3.41 | 3.41 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_CORRIDORFLR3_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 1.31 | 1.31 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 1.31 | 1.31 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_GUESTROOM301_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 3.41 | 3.41 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_CORRIDORFLR4_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 1.31 | 1.31 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 1.31 | 1.31 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_GUESTROOM401_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 3.41 | 3.41 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM424_3_0_0 | 0 | N
Total or Average |  |  | 184.21 | 3.18 | 0.441 | 0.545
North Total or Average |  |  | 72.38 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 111.83 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1703.78 | 1360.73 | 343.05 | 0.8 | 3.61
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1741.53 | 1390.88 | 350.65 | 0.8 | 3.65
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1844.15 | 1472.84 | 371.31 | 0.8 | 3.62
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1470.13 | 1174.13 | 296 | 0.8 | 3.63
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1542.13 | 1231.63 | 310.5 | 0.8 | 3.61
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2337.25 | 1866.66 | 470.59 | 0.8 | 3.54
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7976.07 | 6370.13 | 1605.94 | 0.8 | 2.98
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6499.01 | 5190.47 | 1308.54 | 0.8 | 2.98
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7729.9 | 6173.53 | 1556.38 | 0.8 | 2.99
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2183.7 | 1744.02 | 439.68 | 0.8 | 3.58
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1843.83 | 1472.58 | 371.24 | 0.8 | 3.62
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7121.3 | 5687.46 | 1433.84 | 0.8 | 2.99
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2265.34 | 1809.23 | 456.11 | 0.8 | 3.58
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6477.48 | 5173.27 | 1304.21 | 0.8 | 2.98
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1854.95 | 1481.47 | 373.48 | 0.8 | 3.61
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2302.78 | 1839.13 | 463.65 | 0.8 | 3.56
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7932.2 | 6335.09 | 1597.11 | 0.8 | 2.99
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6635.31 | 5299.33 | 1335.98 | 0.8 | 2.98
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7922.07 | 6327.01 | 1595.07 | 0.8 | 2.99
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2241.15 | 1789.9 | 451.24 | 0.8 | 3.59
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1905.61 | 1521.93 | 383.69 | 0.8 | 3.65
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6796.89 | 5428.37 | 1368.52 | 0.8 | 2.98
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1809.62 | 1445.27 | 364.36 | 0.8 | 3.63
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6684.02 | 5338.23 | 1345.79 | 0.8 | 2.98
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1899.48 | 1517.03 | 382.45 | 0.8 | 3.6
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2796.42 | 2233.38 | 563.04 | 0.8 | 3.42
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9615.14 | 7679.18 | 1935.96 | 0.8 | 2.98
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7994.7 | 6385.01 | 1609.69 | 0.8 | 2.98
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9621.76 | 7684.47 | 1937.29 | 0.8 | 2.98
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2711.49 | 2165.55 | 545.94 | 0.8 | 3.43
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2436.75 | 1946.12 | 490.63 | 0.8 | 3.53
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8653.89 | 6911.47 | 1742.41 | 0.8 | 2.98
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2270.48 | 1813.33 | 457.15 | 0.8 | 3.58
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8585 | 6856.45 | 1728.54 | 0.8 | 2.99
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2431.39 | 1941.84 | 489.55 | 0.8 | 3.53
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8155.75 | 6513.63 | 1642.12 | 0.8 | 4.05
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14916.57 | 11576.13 | 3340.45 | 0.78 | 3.96
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1323.79 | 1057.25 | 266.54 | 0.8 | 4.06
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8117.91 | 6186.63 | 1931.29 | 0.76 | 3.92
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1632.43 | 1245.41 | 387.02 | 0.76 | 3.94
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5133.19 | 4099.65 | 1033.54 | 0.8 | 4.06
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 24753.89 | 19769.82 | 4984.07 | 0.8 | 3.75
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2186.19 | 1683.71 | 502.48 | 0.77 | 3.94
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5473.15 | 4371.16 | 1101.99 | 0.8 | 4.05
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6213.41 | 4761.81 | 1451.6 | 0.77 | 3.93
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6108.24 | 4716.48 | 1391.76 | 0.77 | 3.95
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6052.89 | 4692.63 | 1360.27 | 0.78 | 3.96
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 578.19 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 578.19 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 578.19 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 578.19 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 578.19 | 1
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 643.6 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 2312.76 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 1734.57 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 2312.76 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 578.19 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 578.19 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 2312.76 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 692.44 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 2312.76 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 578.19 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 685.59 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 2312.76 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 1734.57 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 2312.76 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 621.53 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 584.02 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 2312.76 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 578.19 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 2312.76 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 578.19 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 29.02 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 50.12 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 1013.99 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 3069.42 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 2460.34 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 3072.11 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 986.35 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 964.19 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 3062.79 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 808.57 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 3042.94 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 920.81 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 173.2 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 5951.61 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 10216.25 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 958.89 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 5334.92 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1075.46 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 3482.93 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 20601.65 | 0.8
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 1471.71 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 3909.11 | 0.78
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 4136.11 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 4136.11 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 4136.11 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.1 | 65.5 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 66.95 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 70.89 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.09 | 56.51 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.09 | 59.28 | 1 | PTAC Fan
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 89.85 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.48 | 306.62 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.39 | 249.84 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.47 | 297.15 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.13 | 83.95 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 70.88 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.43 | 273.76 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 87.08 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.39 | 249.01 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 71.31 | 1 | PTAC Fan
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 88.52 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.48 | 304.93 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.4 | 255.08 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.48 | 304.54 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 86.15 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.12 | 73.26 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.41 | 261.29 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 69.57 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.4 | 256.95 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 73.02 | 1 | PTAC Fan
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0.34 | 1 | Unit Heater Fans
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.17 | 107.5 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.58 | 369.63 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.48 | 307.33 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.58 | 369.88 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.16 | 104.24 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.15 | 93.67 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.52 | 332.67 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 87.28 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.52 | 330.03 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.15 | 93.47 | 1 | PTAC Fan
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 1.16 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.49 | 571.47 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.85 | 963.45 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.08 | 92.76 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.44 | 512.26 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 103.27 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.31 | 359.68 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.5 | 1635.39 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.12 | 141.31 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.33 | 383.5 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 18430.1693 | 15.9962 | 131.7731 | 0 | 0.0001 | 794964.7497 | 6780.7472
February | 16691.1319 | 14.4833 | 119.9848 | 0 | 0.0001 | 723850.6079 | 6142.8977
March | 18112.8649 | 15.6936 | 134.3844 | 0 | 0.0001 | 810739.3289 | 6678.8945
April | 17491.8961 | 15.137 | 133.1027 | 0 | 0.0001 | 803020.6821 | 6460.0657
May | 18206.6556 | 15.734 | 142.3817 | 0 | 0.0001 | 859017.3101 | 6735.755
June | 17719.6859 | 15.3027 | 140.4435 | 0 | 0.0001 | 847331.3655 | 6561.3007
July | 19195.7049 | 16.5625 | 154.8196 | 0 | 0.0001 | 934076.5348 | 7116.0142
August | 19551.1948 | 16.8667 | 158.1264 | 0 | 0.0001 | 954028.9104 | 7249.1386
September | 18694.7184 | 16.1311 | 150.6143 | 0 | 0.0001 | 908703.8215 | 6929.7917
October | 18612.4831 | 16.0728 | 147.6939 | 0 | 0.0001 | 891075.4621 | 6892.4199
November | 17557.5622 | 15.1883 | 134.5897 | 0 | 0.0001 | 811996.2654 | 6487.3298
December | 18336.7883 | 15.8964 | 134.4602 | 0 | 0.0001 | 811190.1811 | 6756.6261
Annual Sum or Average | 218600.8553 | 189.0646 | 1682.3743 | 0 | 0.0008 | 10150000 | 80790.9811
Minimum of Months | 16691.1319 | 14.4833 | 119.9848 | 0 | 0.0001 | 723850.6079 | 6142.8977
Maximum of Months | 19551.1948 | 16.8667 | 158.1264 | 0 | 0.0001 | 954028.9104 | 7249.1386
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 162998000000 | 105050.141 | 28-JAN-08:00 | 26344.714 | 58181.634 | 7649.621 | 0 | 12789.393 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 148417000000 | 110148.583 | 12-FEB-08:00 | 26344.714 | 58181.634 | 7922.293 | 0 | 17615.163 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 166232000000 | 106557.025 | 11-MAR-08:00 | 26344.714 | 58181.634 | 7782.589 | 0 | 14163.31 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 164649000000 | 108273.63 | 16-APR-07:00 | 26344.714 | 58181.634 | 7943.226 | 0 | 15719.278 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 176131000000 | 115773.923 | 28-MAY-07:00 | 26344.714 | 58181.634 | 8295.474 | 0 | 22867.322 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 173735000000 | 110949.924 | 17-JUN-07:00 | 26344.714 | 58181.634 | 8225.085 | 0 | 18113.713 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 191521000000 | 121867.644 | 09-JUL-07:00 | 26344.714 | 58181.634 | 8523.926 | 0 | 28732.591 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 195612000000 | 125070.906 | 13-AUG-07:00 | 26344.714 | 58181.634 | 8689.519 | 0 | 31770.26 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 186318000000 | 122531.339 | 09-SEP-07:00 | 26344.714 | 58181.634 | 8590.985 | 0 | 29329.228 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 182704000000 | 114073.544 | 07-OCT-07:00 | 26344.714 | 58181.634 | 8373.962 | 0 | 21088.456 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 166490000000 | 109179.1 | 12-NOV-08:00 | 26344.714 | 58181.634 | 8043.602 | 0 | 16524.371 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 166324000000 | 105649.993 | 16-DEC-08:00 | 26344.714 | 58181.634 | 7694.782 | 0 | 13344.085 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2081130000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 148417000000 | 105050.141 |  | 26344.714 | 58181.634 | 7649.621 | 0 | 12789.393 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 195612000000 | 125070.906 |  | 26344.714 | 58181.634 | 8689.519 | 0 | 31770.26 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 71533.88 | 6197.12 | 0 | 77731
Cost per Total Building Area ($/m2) | 17.82 | 1.54 | 0 | 19.37
Cost per Net Conditioned Building Area ($/m2) | 18.09 | 1.57 | 0 | 19.66

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3136.18 | 781.39 | 793.29
Net Site Energy | 3136.18 | 781.39 | 793.29
Total Source Energy | 9151.87 | 2280.22 | 2314.95
Net Source Energy | 9151.87 | 2280.22 | 2314.95
Area [m2]
Total Building Area | 4013.59
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 60.2
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0.92 | 264.91 | 0 | 0 | 0 | 0
Cooling | 566.44 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 628.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 37.72 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 815.05 | 189.47 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 253.23 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 377.1 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2304.69 | 831.49 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 6.46 |  | 0
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 5.38 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.6 |  | 0
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 11.84 | 3.08 | 15.43
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 9.7 | 32.61 | 10.7631
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 14 | 1.87 | 12.9
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 16.16 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 12.9 | 2.96 | 77.16
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 6.46 | 8.89 | 206.12
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2157.2117
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 9.7 | 2.96 | 11.4999
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 11.84 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 6.46 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 8.6 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 11.8 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
Total | 4013.59 |  | 11621.74 |  | 1694.58 | 184.21 | 10.425 | 15.71 | 24.2519
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 10.5838 | 15.47 | 16.4088
Unconditioned Total | 60.2 |  | 174.32 |  | 21.18 | 0 | 0 |  | 539.3029
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_REARSTAIRSFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_CORRIDORFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.13 | 90 | 90 | E
W_CORRIDORFLR1_10_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.22 | 180 | 90 | S
S_CORRIDORFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 150.51 | 270 | 180
W_REARSTORAGEFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 163.06 | 90 | 180
W_RESTROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 80.27 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM101_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_EMPLOYEELOUNGEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_LAUNDRYROOMFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 97.83 | 90 | 180
W_ELEVATORCOREFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 15.05 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_FRONTSTORAGEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 12.54 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.69 | 0 | 90 | N
W_CORRIDORFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 8.36 | 0 | 90 | N
W_CORRIDORFLR2_15_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.02 | 270 | 90 | W
W_REARSTORAGEFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.69 | 180 | 90 | S
W_GUESTROOM201_4_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 0 | 90 | N
W_ELEVATORCOREFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.02 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 0 | 90 | N
W_FRONTSTORAGEFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 4.18 | 0 | 90 | N
W_FRONTSTAIRSFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 270 | 90 | W
W_REARSTAIRSFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.69 | 0 | 90 | N
W_CORRIDORFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.02 | 270 | 90 | W
W_REARSTORAGEFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.69 | 180 | 90 | S
W_GUESTROOM301_4_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.02 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 4.18 | 0 | 90 | N
W_FRONTSTAIRSFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 270 | 90 | W
W_REARSTAIRSFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.69 | 0 | 90 | N
R_REARSTAIRSFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
W_CORRIDORFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.02 | 270 | 90 | W
R_CORRIDORFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 125.42 | 90 | 0
W_REARSTORAGEFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.69 | 180 | 90 | S
R_REARSTORAGEFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
W_GUESTROOM401_4_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 180 | 90 | S
R_GUESTROOM401_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM402_405_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 180 | 90 | S
R_GUESTROOM402_405_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.45 | 90 | 0
W_GUESTROOM406_408_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 35.12 | 180 | 90 | S
R_GUESTROOM406_408_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 105.36 | 90 | 0
W_GUESTROOM409_412_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 180 | 90 | S
R_GUESTROOM409_412_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.45 | 90 | 0
W_GUESTROOM413_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 180 | 90 | S
R_GUESTROOM413_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM414_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 0 | 90 | N
R_GUESTROOM414_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM415_418_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 0 | 90 | N
R_GUESTROOM415_418_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.44 | 90 | 0
W_ELEVATORCOREFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.02 | 0 | 90 | N
R_ELEVATORCOREFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 15.05 | 90 | 0
W_GUESTROOM419_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 0 | 90 | N
R_GUESTROOM419_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM420_423_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 0 | 90 | N
R_GUESTROOM420_423_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.44 | 90 | 0
W_GUESTROOM424_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 0 | 90 | N
R_GUESTROOM424_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_FRONTSTORAGEFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 4.18 | 0 | 90 | N
R_FRONTSTORAGEFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12.54 | 90 | 0
W_FRONTSTAIRSFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 270 | 90 | W
R_FRONTSTAIRSFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
W_CORRIDORFLR1_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 2.69 | 2.69 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
D_CORRIDORFLR1_16_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.44 | 4.44 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 2.69 | 2.69 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 2.97 | 2.97 | 3.18 | 0.402 | 0.495 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 2.97 | 2.97 | 3.18 | 0.402 | 0.495 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 2.97 | 2.97 | 3.18 | 0.402 | 0.495 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 2.97 | 2.97 | 3.18 | 0.402 | 0.495 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 2.96 | 2.96 | 3.18 | 0.402 | 0.495 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_GUESTROOM101_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_CORRIDORFLR2_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 1.31 | 1.31 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 1.31 | 1.31 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_GUESTROOM201_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 3.41 | 3.41 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_CORRIDORFLR3_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 1.31 | 1.31 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 1.31 | 1.31 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_GUESTROOM301_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 3.41 | 3.41 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_CORRIDORFLR4_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 1.31 | 1.31 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 1.31 | 1.31 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_GUESTROOM401_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 3.41 | 3.41 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM424_3_0_0 | 0 | N
Total or Average |  |  | 184.21 | 3.18 | 0.441 | 0.545
North Total or Average |  |  | 72.38 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 111.83 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1736.9 | 1370.4 | 366.5 | 0.79 | 3.6
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1776.26 | 1404.18 | 372.09 | 0.79 | 3.59
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1929.12 | 1535.46 | 393.66 | 0.8 | 3.64
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1787.41 | 1427.53 | 359.89 | 0.8 | 3.63
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1762.98 | 1408.01 | 354.97 | 0.8 | 3.64
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2859.23 | 2283.54 | 575.69 | 0.8 | 3.4
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8796.81 | 7025.62 | 1771.19 | 0.8 | 2.98
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7144.59 | 5706.06 | 1438.53 | 0.8 | 2.98
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8521.29 | 6805.58 | 1715.72 | 0.8 | 2.98
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2520.99 | 2013.4 | 507.59 | 0.8 | 3.49
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2453.94 | 1959.85 | 494.09 | 0.8 | 3.52
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8775.04 | 7008.23 | 1766.81 | 0.8 | 2.99
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2715.47 | 2168.72 | 546.75 | 0.8 | 3.43
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8053.85 | 6432.25 | 1621.6 | 0.8 | 2.99
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2372.53 | 1894.84 | 477.7 | 0.8 | 3.53
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2860.59 | 2284.63 | 575.97 | 0.8 | 3.4
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8868.7 | 7083.04 | 1785.67 | 0.8 | 2.99
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7391.36 | 5903.15 | 1488.21 | 0.8 | 2.99
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8857.94 | 7074.44 | 1783.5 | 0.8 | 2.99
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2640.01 | 2108.46 | 531.55 | 0.8 | 3.47
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2582.91 | 2062.86 | 520.06 | 0.8 | 3.49
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8546.98 | 6826.09 | 1720.89 | 0.8 | 2.99
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2277.78 | 1819.16 | 458.62 | 0.8 | 3.57
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8409.79 | 6716.53 | 1693.27 | 0.8 | 2.99
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2486.12 | 1985.55 | 500.57 | 0.8 | 3.51
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3646.67 | 2912.43 | 734.24 | 0.8 | 3.19
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11615.23 | 9276.57 | 2338.67 | 0.8 | 2.98
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9605.01 | 7671.09 | 1933.92 | 0.8 | 2.99
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11624.21 | 9283.74 | 2340.47 | 0.8 | 2.98
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3427.82 | 2737.65 | 690.17 | 0.8 | 3.25
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3476.38 | 2776.43 | 699.95 | 0.8 | 3.23
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11611.16 | 9273.31 | 2337.85 | 0.8 | 2.98
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3069.67 | 2451.61 | 618.06 | 0.8 | 3.36
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11519.94 | 9200.46 | 2319.48 | 0.8 | 2.99
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3375.65 | 2695.98 | 679.67 | 0.8 | 3.25
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9786.57 | 7400.25 | 2386.32 | 0.76 | 3.9
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 18395.66 | 13295.79 | 5099.87 | 0.72 | 3.78
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1430.75 | 1097.35 | 333.4 | 0.77 | 3.96
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11096.29 | 7546.84 | 3549.45 | 0.68 | 3.67
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2210.8 | 1494.69 | 716.12 | 0.68 | 3.67
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5709.17 | 4535.1 | 1174.06 | 0.79 | 4.04
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26501.11 | 21165.25 | 5335.86 | 0.8 | 3.74
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2477.32 | 1882.91 | 594.4 | 0.76 | 3.89
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6284.71 | 5000.86 | 1283.85 | 0.8 | 4.06
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8161.43 | 5601.41 | 2560.03 | 0.69 | 3.69
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7892.28 | 5485.4 | 2406.88 | 0.7 | 3.71
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9916.88 | 7149.1 | 2767.78 | 0.72 | 3.79
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 734.16 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 753.03 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 949.35 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 958.88 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 754.68 | 1
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 96.65 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 59.33 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 58.75 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 999.68 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 2677.44 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 2008.08 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 2677.44 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 857 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 830.28 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 2677.44 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 642.07 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 2677.44 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 752.4 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 171.7 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 83.97 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 86.31 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 1034.05 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 2677.44 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 2120.25 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 2677.44 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 891.49 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 869.01 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 2677.44 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 669.36 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 2677.44 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 804.02 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 209.62 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 392.25 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 315 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 1501.59 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 4512.03 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 3619.57 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 4509.65 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 1369.47 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 1349.2 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 4505.82 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 1207.41 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 4481.4 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 1325.93 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 545.94 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 7312.27 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 12333.11 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1101.64 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 6352.01 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1245.04 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 4148.19 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 21722.23 | 0.8
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 1873.17 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 4792.78 | 0.78
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 4788.31 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 4788.31 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 6606.11 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.1 | 65.02 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.1 | 66.77 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.12 | 73.61 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 68.71 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 67.77 | 1 | PTAC Fan
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0.7 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0.43 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0.42 | 1 | Unit Heater Fans
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.17 | 109.91 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.53 | 338.17 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.43 | 274.65 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.51 | 327.58 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.15 | 96.91 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.15 | 94.33 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.53 | 337.33 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.16 | 104.39 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.49 | 309.61 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 91.21 | 1 | PTAC Fan
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 1.24 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0.61 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0.62 | 1 | Unit Heater Fans
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.17 | 109.97 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.54 | 340.93 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.45 | 284.14 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.54 | 340.52 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.16 | 101.49 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.16 | 99.29 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.52 | 328.56 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 87.56 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.51 | 323.29 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.15 | 95.57 | 1 | PTAC Fan
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 1.51 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 2.83 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 2.28 | 1 | Unit Heater Fans
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.22 | 140.19 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.7 | 446.51 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.58 | 369.24 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.7 | 446.86 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.21 | 131.77 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.21 | 133.64 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.7 | 446.36 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.19 | 118 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.7 | 442.85 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.2 | 129.77 | 1 | PTAC Fan
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.02 | 3.94 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.52 | 606.49 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.88 | 1004.66 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.08 | 91.61 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.45 | 526.84 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 103.27 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 395.36 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.6 | 1750.82 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.13 | 155.36 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.38 | 436.85 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.47 | 547.92 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 41961.1658 | 63.4809 | 238.8237 | 0 | 0.0005 | 1190890 | 17162.0229
February | 37354.9617 | 57.7971 | 224.6824 | 0 | 0.0004 | 1120430 | 15411.6234
March | 41362.5915 | 64.2188 | 250.864 | 0 | 0.0005 | 1251000 | 17088.0229
April | 42780.1236 | 68.1015 | 275.2696 | 0 | 0.0005 | 1372770 | 17848.4523
May | 46795.9847 | 74.9497 | 305.3901 | 0 | 0.0006 | 1523000 | 19571.257
June | 52736.9985 | 85.0423 | 349.5866 | 0 | 0.0007 | 1743430 | 22115.934
July | 58237.2397 | 94.1269 | 388.0691 | 0 | 0.0007 | 1935360 | 24444.8911
August | 57266.7063 | 92.5222 | 381.2628 | 0 | 0.0007 | 1901410 | 24033.7633
September | 50428.5254 | 81.2251 | 333.3946 | 0 | 0.0006 | 1662680 | 21138.0103
October | 44508.3992 | 71.101 | 288.7232 | 0 | 0.0005 | 1439880 | 18595.3101
November | 39777.5896 | 62.1443 | 244.882 | 0 | 0.0005 | 1221190 | 16473.367
December | 41521.655 | 63.2973 | 240.8453 | 0 | 0.0005 | 1200990 | 17032.2808
Annual Sum or Average | 554731.941 | 878.0072 | 3521.7935 | 0 | 0.0067 | 17563000 | 230914.9351
Minimum of Months | 37354.9617 | 57.7971 | 224.6824 | 0 | 0.0004 | 1120430 | 15411.6234
Maximum of Months | 58237.2397 | 94.1269 | 388.0691 | 0 | 0.0007 | 1935360 | 24444.8911
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 156274000000 | 101614.647 | 29-JAN-08:00 | 26344.714 | 58181.634 | 7661.577 | 0 | 9341.944 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 147028000000 | 104053.498 | 18-FEB-08:00 | 26344.714 | 58181.634 | 7981.796 | 0 | 11460.576 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 164161000000 | 103766.258 | 26-MAR-07:00 | 26344.714 | 58181.634 | 7916.194 | 0 | 11238.938 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 180141000000 | 122040.998 | 21-APR-19:15 | 36525.994 | 38968.112 | 9626.641 | 0 | 34435.462 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 199854000000 | 129612.417 | 31-MAY-19:15 | 36525.994 | 38968.112 | 9997.644 | 0 | 41635.878 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 228780000000 | 152362.199 | 27-JUN-19:15 | 36525.994 | 38968.112 | 11167.641 | 0 | 63215.663 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 253966000000 | 151268.439 | 25-JUL-19:15 | 36525.994 | 38968.112 | 11068.06 | 0 | 62221.484 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 249511000000 | 147595.702 | 04-AUG-19:15 | 36525.994 | 38968.112 | 10950.967 | 0 | 58665.84 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 218183000000 | 136434.806 | 02-SEP-07:00 | 26344.714 | 58181.634 | 9790.602 | 0 | 42033.078 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 188946000000 | 118001.244 | 07-OCT-07:00 | 26344.714 | 58181.634 | 9030.49 | 0 | 24359.628 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 160249000000 | 107867.397 | 11-NOV-08:00 | 26344.714 | 58181.634 | 8424.982 | 0 | 14831.288 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 157599000000 | 103242.318 | 09-DEC-08:00 | 26344.714 | 58181.634 | 7840.138 | 0 | 10791.054 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2304690000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 147028000000 | 101614.647 |  | 26344.714 | 38968.112 | 7661.577 | 0 | 9341.944 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 253966000000 | 152362.199 |  | 36525.994 | 58181.634 | 11167.641 | 0 | 63215.663 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 60608.92 | 6629.63 | 0 | 67238.55
Cost per Total Building Area ($/m2) | 15.1 | 1.65 | 0 | 16.75
Cost per Net Conditioned Building Area ($/m2) | 15.33 | 1.68 | 0 | 17.01

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2981.65 | 742.89 | 754.2
Net Site Energy | 2981.65 | 742.89 | 754.2
Total Source Energy | 7101.76 | 1769.43 | 1796.37
Net Source Energy | 7101.76 | 1769.43 | 1796.37
Area [m2]
Total Building Area | 4013.59
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 60.2
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0.74 | 378.96 | 0 | 0 | 0 | 0
Cooling | 225.07 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 628.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 37.68 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 815.05 | 189.47 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 210.15 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 493.21 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1920.02 | 1061.64 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 6.46 |  | 0
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 5.38 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.6 |  | 0
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 11.84 | 3.08 | 15.43
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 9.7 | 32.61 | 10.7631
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 14 | 1.87 | 12.9
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 16.16 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 12.9 | 2.96 | 77.16
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 6.46 | 8.89 | 206.12
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2157.2117
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 9.7 | 2.96 | 11.4999
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 11.84 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 6.46 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 8.6 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 11.8 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
Total | 4013.59 |  | 11621.74 |  | 1694.58 | 184.21 | 10.425 | 15.71 | 24.2519
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 10.5838 | 15.47 | 16.4088
Unconditioned Total | 60.2 |  | 174.32 |  | 21.18 | 0 | 0 |  | 539.3029
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_REARSTAIRSFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_CORRIDORFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.13 | 90 | 90 | E
W_CORRIDORFLR1_10_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.22 | 180 | 90 | S
S_CORRIDORFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 150.51 | 270 | 180
W_REARSTORAGEFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 163.06 | 90 | 180
W_RESTROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 80.27 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM101_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_EMPLOYEELOUNGEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_LAUNDRYROOMFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 97.83 | 90 | 180
W_ELEVATORCOREFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 15.05 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_FRONTSTORAGEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 12.54 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.69 | 0 | 90 | N
W_CORRIDORFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 8.36 | 0 | 90 | N
W_CORRIDORFLR2_15_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.02 | 270 | 90 | W
W_REARSTORAGEFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.69 | 180 | 90 | S
W_GUESTROOM201_4_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 0 | 90 | N
W_ELEVATORCOREFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.02 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 0 | 90 | N
W_FRONTSTORAGEFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 4.18 | 0 | 90 | N
W_FRONTSTAIRSFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 270 | 90 | W
W_REARSTAIRSFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.69 | 0 | 90 | N
W_CORRIDORFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.02 | 270 | 90 | W
W_REARSTORAGEFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.69 | 180 | 90 | S
W_GUESTROOM301_4_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.02 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 4.18 | 0 | 90 | N
W_FRONTSTAIRSFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 270 | 90 | W
W_REARSTAIRSFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.69 | 0 | 90 | N
R_REARSTAIRSFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
W_CORRIDORFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.02 | 270 | 90 | W
R_CORRIDORFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 125.42 | 90 | 0
W_REARSTORAGEFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.69 | 180 | 90 | S
R_REARSTORAGEFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
W_GUESTROOM401_4_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 180 | 90 | S
R_GUESTROOM401_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM402_405_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 180 | 90 | S
R_GUESTROOM402_405_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.45 | 90 | 0
W_GUESTROOM406_408_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 35.12 | 180 | 90 | S
R_GUESTROOM406_408_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 105.36 | 90 | 0
W_GUESTROOM409_412_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 180 | 90 | S
R_GUESTROOM409_412_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.45 | 90 | 0
W_GUESTROOM413_5_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 180 | 90 | S
R_GUESTROOM413_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM414_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 0 | 90 | N
R_GUESTROOM414_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM415_418_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 0 | 90 | N
R_GUESTROOM415_418_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.44 | 90 | 0
W_ELEVATORCOREFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 5.02 | 0 | 90 | N
R_ELEVATORCOREFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 15.05 | 90 | 0
W_GUESTROOM419_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 0 | 90 | N
R_GUESTROOM419_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM420_423_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 43.48 | 0 | 90 | N
R_GUESTROOM420_423_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.44 | 90 | 0
W_GUESTROOM424_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 10.87 | 0 | 90 | N
R_GUESTROOM424_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_FRONTSTORAGEFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 4.18 | 0 | 90 | N
R_FRONTSTORAGEFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12.54 | 90 | 0
W_FRONTSTAIRSFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 22.58 | 270 | 90 | W
R_FRONTSTAIRSFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
W_CORRIDORFLR1_2_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61_EAST | 2.69 | 2.69 | 6.49 | 0.61 | 0.61 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
D_CORRIDORFLR1_16_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61_WEST | 4.44 | 4.44 | 6.49 | 0.61 | 0.61 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 2.69 | 2.69 | 6.49 | 0.61 | 0.61 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 2.97 | 2.97 | 6.49 | 0.61 | 0.61 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 2.97 | 2.97 | 6.49 | 0.61 | 0.61 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 2.97 | 2.97 | 6.49 | 0.61 | 0.61 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 2.97 | 2.97 | 6.49 | 0.61 | 0.61 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 2.96 | 2.96 | 6.49 | 0.61 | 0.61 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_GUESTROOM101_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.65 | 1.65 | 6.49 | 0.82 | 0.82 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.64 | 1.64 | 6.49 | 0.82 | 0.82 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.64 | 1.64 | 6.49 | 0.82 | 0.82 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.64 | 1.64 | 6.49 | 0.82 | 0.82 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.64 | 1.64 | 6.49 | 0.82 | 0.82 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.65 | 1.65 | 6.49 | 0.82 | 0.82 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.65 | 1.65 | 6.49 | 0.82 | 0.82 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.64 | 1.64 | 6.49 | 0.82 | 0.82 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.64 | 1.64 | 6.49 | 0.82 | 0.82 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.64 | 1.64 | 6.49 | 0.82 | 0.82 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.64 | 1.64 | 6.49 | 0.82 | 0.82 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_CORRIDORFLR2_2_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61_EAST | 1.31 | 1.31 | 6.49 | 0.61 | 0.61 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61_WEST | 1.31 | 1.31 | 6.49 | 0.61 | 0.61 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_GUESTROOM201_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 3.41 | 3.41 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.65 | 1.65 | 6.49 | 0.82 | 0.82 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.64 | 1.64 | 6.49 | 0.82 | 0.82 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.64 | 1.64 | 6.49 | 0.82 | 0.82 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.64 | 1.64 | 6.49 | 0.82 | 0.82 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.64 | 1.64 | 6.49 | 0.82 | 0.82 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.65 | 1.65 | 6.49 | 0.82 | 0.82 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.65 | 1.65 | 6.49 | 0.82 | 0.82 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.64 | 1.64 | 6.49 | 0.82 | 0.82 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.64 | 1.64 | 6.49 | 0.82 | 0.82 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.64 | 1.64 | 6.49 | 0.82 | 0.82 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.64 | 1.64 | 6.49 | 0.82 | 0.82 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_CORRIDORFLR3_2_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61_EAST | 1.31 | 1.31 | 6.49 | 0.61 | 0.61 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61_WEST | 1.31 | 1.31 | 6.49 | 0.61 | 0.61 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_GUESTROOM301_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 3.41 | 3.41 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.65 | 1.65 | 6.49 | 0.82 | 0.82 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.64 | 1.64 | 6.49 | 0.82 | 0.82 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.64 | 1.64 | 6.49 | 0.82 | 0.82 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.64 | 1.64 | 6.49 | 0.82 | 0.82 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.64 | 1.64 | 6.49 | 0.82 | 0.82 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.65 | 1.65 | 6.49 | 0.82 | 0.82 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.65 | 1.65 | 6.49 | 0.82 | 0.82 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.64 | 1.64 | 6.49 | 0.82 | 0.82 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.64 | 1.64 | 6.49 | 0.82 | 0.82 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.64 | 1.64 | 6.49 | 0.82 | 0.82 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.64 | 1.64 | 6.49 | 0.82 | 0.82 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_CORRIDORFLR4_2_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61_EAST | 1.31 | 1.31 | 6.49 | 0.61 | 0.61 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61_WEST | 1.31 | 1.31 | 6.49 | 0.61 | 0.61 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_GUESTROOM401_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 3.41 | 3.41 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.64 | 1.64 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 1.65 | 1.65 | 6.49 | 0.61 | 0.61 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.65 | 1.65 | 6.49 | 0.82 | 0.82 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.64 | 1.64 | 6.49 | 0.82 | 0.82 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.64 | 1.64 | 6.49 | 0.82 | 0.82 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.64 | 1.64 | 6.49 | 0.82 | 0.82 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.64 | 1.64 | 6.49 | 0.82 | 0.82 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.65 | 1.65 | 6.49 | 0.82 | 0.82 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.65 | 1.65 | 6.49 | 0.82 | 0.82 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.64 | 1.64 | 6.49 | 0.82 | 0.82 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.64 | 1.64 | 6.49 | 0.82 | 0.82 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.64 | 1.64 | 6.49 | 0.82 | 0.82 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | STD_WINDOW_UVALUE_6.878_SHGC_0.82_VT_0.82 | 1.64 | 1.64 | 6.49 | 0.82 | 0.82 | No | W_GUESTROOM424_3_0_0 | 0 | N
Total or Average |  |  | 184.21 | 6.49 | 0.692 | 0.692
North Total or Average |  |  | 72.38 | 6.49 | 0.82 | 0.82
Non-North Total or Average |  |  | 111.83 | 6.49 | 0.61 | 0.61
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1745.97 | 1394.43 | 351.54 | 0.8 | 3.65
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1792.74 | 1431.78 | 360.96 | 0.8 | 3.63
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1812.82 | 1447.82 | 365 | 0.8 | 3.63
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1182.66 | 944.54 | 238.12 | 0.8 | 3.62
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1311.03 | 1047.06 | 263.97 | 0.8 | 3.64
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2545.95 | 2033.33 | 512.61 | 0.8 | 3.48
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9139.02 | 7298.92 | 1840.09 | 0.8 | 2.98
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7627.89 | 6092.05 | 1535.83 | 0.8 | 2.98
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8848.09 | 7066.57 | 1781.52 | 0.8 | 2.98
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2412.63 | 1926.86 | 485.77 | 0.8 | 3.54
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1724.67 | 1377.42 | 347.25 | 0.8 | 3.61
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6921.65 | 5528.01 | 1393.64 | 0.8 | 2.98
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2209.06 | 1764.28 | 444.78 | 0.8 | 3.59
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6251.95 | 4993.15 | 1258.8 | 0.8 | 2.98
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1757.21 | 1403.41 | 353.81 | 0.8 | 3.6
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2502.25 | 1998.44 | 503.81 | 0.8 | 3.5
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9118.02 | 7282.16 | 1835.87 | 0.8 | 2.98
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7829.07 | 6252.73 | 1576.34 | 0.8 | 2.98
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9105.64 | 7272.27 | 1833.37 | 0.8 | 2.99
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2487.1 | 1986.33 | 500.76 | 0.8 | 3.51
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1791.05 | 1430.43 | 360.62 | 0.8 | 3.64
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6607.48 | 5277.1 | 1330.38 | 0.8 | 2.98
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1756.76 | 1403.04 | 353.71 | 0.8 | 3.6
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6496.44 | 5188.42 | 1308.02 | 0.8 | 2.99
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1813.52 | 1448.38 | 365.14 | 0.8 | 3.63
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2841.02 | 2269 | 572.02 | 0.8 | 3.4
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10253.37 | 8188.91 | 2064.46 | 0.8 | 2.99
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8756.22 | 6993.2 | 1763.02 | 0.8 | 2.99
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10259.51 | 8193.81 | 2065.7 | 0.8 | 2.99
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2793.48 | 2231.02 | 562.45 | 0.8 | 3.43
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2165.96 | 1729.86 | 436.11 | 0.8 | 3.61
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7923.81 | 6328.39 | 1595.42 | 0.8 | 2.98
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2056.84 | 1642.7 | 414.13 | 0.8 | 3.61
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7860.26 | 6277.64 | 1582.62 | 0.8 | 2.99
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2187.72 | 1747.24 | 440.49 | 0.8 | 3.59
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7122.29 | 5688.26 | 1434.04 | 0.8 | 4.06
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 15019.49 | 11995.39 | 3024.1 | 0.8 | 4.04
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1262.89 | 1008.61 | 254.28 | 0.8 | 4.12
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7516.65 | 6003.21 | 1513.44 | 0.8 | 4.04
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1473.75 | 1177.01 | 296.73 | 0.8 | 4.07
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4857.04 | 3879.1 | 977.94 | 0.8 | 4.05
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 23641.5 | 18881.41 | 4760.09 | 0.8 | 3.74
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1793.68 | 1432.53 | 361.15 | 0.8 | 4.09
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4513.12 | 3604.43 | 908.69 | 0.8 | 4.07
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5667.89 | 4526.69 | 1141.2 | 0.8 | 4.05
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5667.89 | 4526.69 | 1141.2 | 0.8 | 4.05
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5667.89 | 4526.69 | 1141.2 | 0.8 | 4.05
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 639.09 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 639.09 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 767.15 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 762.65 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 639.09 | 1
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 873.67 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 2556.36 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 1917.27 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 2556.36 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 767.66 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 732.33 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 2556.36 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 694.66 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 2556.36 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 678.01 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 26.2 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 908.79 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 2556.36 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 1983.87 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 2556.36 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 818.7 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 788.59 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 2556.36 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 639.09 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 2556.36 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 734.21 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 80.45 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 206.91 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 179.54 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 1301.16 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 3993.95 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 3246.42 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 3994.36 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 1226.76 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 1205.77 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 3990.39 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 1060.76 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 3965.59 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 1172.79 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 351.21 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 5744.91 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 12114.86 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1018.66 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 6063 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1188.74 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 3699.35 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 20225.74 | 0.8
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 1446.8 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 3640.33 | 0.78
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 4571.77 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 4571.77 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 4571.77 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 67.12 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 68.92 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 69.69 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.07 | 45.46 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.08 | 50.4 | 1 | PTAC Fan
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.15 | 97.87 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.55 | 351.32 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.46 | 293.23 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.53 | 340.14 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.15 | 92.75 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.1 | 66.3 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.42 | 266.08 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.13 | 84.92 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.38 | 240.34 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 67.55 | 1 | PTAC Fan
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.15 | 96.19 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.55 | 350.52 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.47 | 300.97 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.55 | 350.04 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.15 | 95.61 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 68.85 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.4 | 254.01 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 67.53 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.39 | 249.74 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 69.72 | 1 | PTAC Fan
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0.54 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 1.38 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 1.2 | 1 | Unit Heater Fans
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.17 | 109.21 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.62 | 394.16 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.53 | 336.61 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.62 | 394.4 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.17 | 107.39 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.13 | 83.26 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.48 | 304.61 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.12 | 79.07 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.47 | 302.17 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.13 | 84.1 | 1 | PTAC Fan
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 2.35 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.43 | 499.06 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.91 | 1033.62 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.08 | 88.49 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.45 | 526.69 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 103.27 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.29 | 340.33 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.43 | 1561.9 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.11 | 125.68 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.27 | 316.23 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 20109.125 | 17.5692 | 123.0801 | 0 | 0.0001 | 742431.28 | 7335.3145
February | 17350.5039 | 15.1071 | 115.4814 | 0 | 0.0001 | 696642.1525 | 6357.3677
March | 19188.7229 | 16.7176 | 125.925 | 0 | 0.0001 | 759634.8943 | 7025.4414
April | 18222.3005 | 15.8449 | 125.0937 | 0 | 0.0001 | 754646.5906 | 6688.4249
May | 18426.1367 | 15.9907 | 132.1042 | 0 | 0.0001 | 796963.7492 | 6780.3617
June | 17643.8242 | 15.2912 | 130.1921 | 0 | 0.0001 | 785444.2553 | 6503.7682
July | 18320.7291 | 15.8561 | 139.0759 | 0 | 0.0001 | 839056.4757 | 6765.1503
August | 18262.6139 | 15.8045 | 138.8681 | 0 | 0.0001 | 837803.5512 | 6744.4025
September | 17985.3162 | 15.5586 | 137.8233 | 0 | 0.0001 | 831504.7254 | 6645.2417
October | 18383.6798 | 15.926 | 136.7937 | 0 | 0.0001 | 825276.1485 | 6779.9746
November | 17982.486 | 15.6306 | 124.4799 | 0 | 0.0001 | 750948.1869 | 6603.5519
December | 19843.6239 | 17.3268 | 123.3152 | 0 | 0.0001 | 743858.8966 | 7244.1414
Annual Sum or Average | 221719.0621 | 192.623 | 1552.2327 | 0 | 0.0008 | 9364210 | 81473.1409
Minimum of Months | 17350.5039 | 15.1071 | 115.4814 | 0 | 0.0001 | 696642.1525 | 6357.3677
Maximum of Months | 20109.125 | 17.5692 | 139.0759 | 0 | 0.0001 | 839056.4757 | 7335.3145
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 152226000000 | 100642.984 | 16-JAN-08:00 | 26344.714 | 58181.634 | 6976.309 | 0 | 9055.549 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 142838000000 | 103065.552 | 18-FEB-08:00 | 26344.714 | 58181.634 | 7240.837 | 0 | 11213.589 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 155754000000 | 101493.154 | 11-MAR-08:00 | 26344.714 | 58181.634 | 7055.539 | 0 | 9826.489 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 154731000000 | 104968.691 | 29-APR-07:00 | 26344.714 | 58181.634 | 7431.519 | 0 | 12926.045 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 163408000000 | 104792.757 | 29-MAY-07:00 | 26344.714 | 58181.634 | 7419.536 | 0 | 12762.094 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 161046000000 | 109298.348 | 17-JUN-07:00 | 26344.714 | 58181.634 | 7851.559 | 0 | 16835.662 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 172038000000 | 121923.062 | 02-JUL-19:30 | 36441.661 | 38950.562 | 9184.786 | 0 | 34861.264 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 171781000000 | 107403.305 | 27-AUG-07:00 | 26344.714 | 58181.634 | 7707.41 | 0 | 15084.768 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 170490000000 | 115800.7 | 28-SEP-19:00 | 36525.994 | 38968.112 | 8717.271 | 0 | 29104.534 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 169213000000 | 106616.234 | 21-OCT-07:00 | 26344.714 | 58181.634 | 7622.298 | 0 | 14382.809 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 153973000000 | 104176.017 | 11-NOV-08:00 | 26344.714 | 58181.634 | 7360.068 | 0 | 12204.822 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 152519000000 | 101027.935 | 17-DEC-08:00 | 26344.714 | 58181.634 | 7002.08 | 0 | 9414.729 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1920020000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 142838000000 | 100642.984 |  | 26344.714 | 38950.562 | 6976.309 | 0 | 9055.549 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 172038000000 | 121923.062 |  | 36525.994 | 58181.634 | 9184.786 | 0 | 34861.264 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 77627.27 | 8977.75 | 0 | 86605.03
Cost per Total Building Area ($/m2) | 19.34 | 2.24 | 0 | 21.58
Cost per Net Conditioned Building Area ($/m2) | 19.64 | 2.27 | 0 | 21.91

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3532.61 | 880.16 | 893.57
Net Site Energy | 3532.61 | 880.16 | 893.57
Total Source Energy | 9195.07 | 2290.99 | 2325.87
Net Source Energy | 9195.07 | 2290.99 | 2325.87
Area [m2]
Total Building Area | 4013.59
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 60.2
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 33.52 | 691.8 | 0 | 0 | 0 | 0
Cooling | 405.76 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 628.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 37.72 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 815.05 | 189.47 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 225.36 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 502.6 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2148.74 | 1383.87 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 6.46 |  | 0
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 5.38 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.6 |  | 0
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 11.84 | 3.08 | 15.43
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 9.7 | 32.61 | 10.7631
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 14 | 1.87 | 12.9
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 16.16 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 12.9 | 2.96 | 77.16
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 6.46 | 8.89 | 206.12
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2157.2117
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 9.7 | 2.96 | 11.4999
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 11.84 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 6.46 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 8.6 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 11.8 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
Total | 4013.59 |  | 11621.74 |  | 1694.58 | 184.21 | 10.425 | 15.71 | 24.2519
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 10.5838 | 15.47 | 16.4088
Unconditioned Total | 60.2 |  | 174.32 |  | 21.18 | 0 | 0 |  | 539.3029
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_REARSTAIRSFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_CORRIDORFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.13 | 90 | 90 | E
W_CORRIDORFLR1_10_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.22 | 180 | 90 | S
S_CORRIDORFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 150.51 | 270 | 180
W_REARSTORAGEFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 163.06 | 90 | 180
W_RESTROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 80.27 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM101_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_EMPLOYEELOUNGEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_LAUNDRYROOMFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 97.83 | 90 | 180
W_ELEVATORCOREFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 15.05 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_FRONTSTORAGEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 12.54 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_CORRIDORFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.36 | 0 | 90 | N
W_CORRIDORFLR2_15_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 270 | 90 | W
W_REARSTORAGEFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 180 | 90 | S
W_GUESTROOM201_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
W_ELEVATORCOREFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_FRONTSTORAGEFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 4.18 | 0 | 90 | N
W_FRONTSTAIRSFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_REARSTAIRSFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_CORRIDORFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 270 | 90 | W
W_REARSTORAGEFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 180 | 90 | S
W_GUESTROOM301_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 4.18 | 0 | 90 | N
W_FRONTSTAIRSFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_REARSTAIRSFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
R_REARSTAIRSFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
W_CORRIDORFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 270 | 90 | W
R_CORRIDORFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 125.42 | 90 | 0
W_REARSTORAGEFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 180 | 90 | S
R_REARSTORAGEFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
W_GUESTROOM401_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
R_GUESTROOM401_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM402_405_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
R_GUESTROOM402_405_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.45 | 90 | 0
W_GUESTROOM406_408_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 35.12 | 180 | 90 | S
R_GUESTROOM406_408_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 105.36 | 90 | 0
W_GUESTROOM409_412_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
R_GUESTROOM409_412_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.45 | 90 | 0
W_GUESTROOM413_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
R_GUESTROOM413_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM414_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
R_GUESTROOM414_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM415_418_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
R_GUESTROOM415_418_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.44 | 90 | 0
W_ELEVATORCOREFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 0 | 90 | N
R_ELEVATORCOREFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 15.05 | 90 | 0
W_GUESTROOM419_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
R_GUESTROOM419_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM420_423_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
R_GUESTROOM420_423_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.44 | 90 | 0
W_GUESTROOM424_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
R_GUESTROOM424_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_FRONTSTORAGEFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 4.18 | 0 | 90 | N
R_FRONTSTORAGEFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12.54 | 90 | 0
W_FRONTSTAIRSFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
R_FRONTSTAIRSFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
W_CORRIDORFLR1_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 2.69 | 2.69 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
D_CORRIDORFLR1_16_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.44 | 4.44 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 2.69 | 2.69 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 2.97 | 2.97 | 3.18 | 0.402 | 0.495 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 2.97 | 2.97 | 3.18 | 0.402 | 0.495 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 2.97 | 2.97 | 3.18 | 0.402 | 0.495 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 2.97 | 2.97 | 3.18 | 0.402 | 0.495 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 2.96 | 2.96 | 3.18 | 0.402 | 0.495 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_GUESTROOM101_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_CORRIDORFLR2_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 1.31 | 1.31 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 1.31 | 1.31 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_GUESTROOM201_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 3.41 | 3.41 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_CORRIDORFLR3_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 1.31 | 1.31 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 1.31 | 1.31 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_GUESTROOM301_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 3.41 | 3.41 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_CORRIDORFLR4_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 1.31 | 1.31 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 1.31 | 1.31 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_GUESTROOM401_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 3.41 | 3.41 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM424_3_0_0 | 0 | N
Total or Average |  |  | 184.21 | 3.18 | 0.441 | 0.545
North Total or Average |  |  | 72.38 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 111.83 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1834.32 | 1391.06 | 443.25 | 0.76 | 3.57
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1866.1 | 1418.82 | 447.29 | 0.76 | 3.56
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1957.17 | 1497.32 | 459.85 | 0.77 | 3.59
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1730.72 | 1338.43 | 392.29 | 0.77 | 3.6
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1770 | 1373.3 | 396.69 | 0.78 | 3.59
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2292.42 | 1820.73 | 471.69 | 0.79 | 3.57
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8398.19 | 6501.81 | 1896.37 | 0.77 | 2.96
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6717.88 | 5242.99 | 1474.89 | 0.78 | 2.97
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8196.23 | 6324.46 | 1871.77 | 0.77 | 2.96
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2267.32 | 1773.17 | 494.15 | 0.78 | 3.54
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2054.88 | 1634.38 | 420.5 | 0.8 | 3.61
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7910.09 | 6225.16 | 1684.93 | 0.79 | 2.97
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2390.09 | 1908.86 | 481.23 | 0.8 | 3.52
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7384.87 | 5757.21 | 1627.66 | 0.78 | 2.96
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2045.36 | 1620.76 | 424.6 | 0.79 | 3.61
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2276.99 | 1806.93 | 470.06 | 0.79 | 3.57
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8391.6 | 6496.03 | 1895.58 | 0.77 | 2.96
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6851.21 | 5360.42 | 1490.79 | 0.78 | 2.97
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8384.69 | 6489.95 | 1894.74 | 0.77 | 2.96
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2331.62 | 1828.5 | 503.11 | 0.78 | 3.55
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2118.17 | 1691.31 | 426.87 | 0.8 | 3.62
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7674.93 | 6015.45 | 1659.48 | 0.78 | 2.97
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2001.66 | 1581.63 | 420.03 | 0.79 | 3.62
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7577.87 | 5928.99 | 1648.89 | 0.78 | 2.97
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2094.92 | 1665.19 | 429.73 | 0.79 | 3.63
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2814.88 | 2248.12 | 566.76 | 0.8 | 3.42
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10355.88 | 8102.44 | 2253.44 | 0.78 | 2.97
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8450.4 | 6664.01 | 1786.39 | 0.79 | 2.98
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10364.91 | 8110.38 | 2254.53 | 0.78 | 2.97
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2872.33 | 2276.7 | 595.64 | 0.79 | 3.39
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2777.25 | 2218.06 | 559.18 | 0.8 | 3.43
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9780.05 | 7763.62 | 2016.43 | 0.79 | 2.98
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2535.23 | 2024.23 | 511.01 | 0.8 | 3.48
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9717.82 | 7708.1 | 2009.72 | 0.79 | 2.98
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2731.42 | 2181.46 | 549.96 | 0.8 | 3.45
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12777.99 | 8638.98 | 4139 | 0.68 | 3.66
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 20544.62 | 13889.87 | 6654.75 | 0.68 | 3.45
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1757.1 | 1221.54 | 535.56 | 0.7 | 3.76
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10738.13 | 7259.87 | 3478.26 | 0.68 | 3.66
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2210.8 | 1494.69 | 716.12 | 0.68 | 3.67
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6636.19 | 4802.09 | 1834.1 | 0.72 | 3.81
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 25658.22 | 20208.63 | 5449.59 | 0.79 | 3.71
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3211.03 | 2170.92 | 1040.11 | 0.68 | 3.67
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7594.44 | 5429.91 | 2164.53 | 0.71 | 3.77
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8502.54 | 5748.42 | 2754.11 | 0.68 | 3.66
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8502.54 | 5748.42 | 2754.11 | 0.68 | 3.66
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9319.28 | 6300.61 | 3018.67 | 0.68 | 3.67
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 194.43 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 66.38 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 950.72 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 972.13 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1178.85 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 1179.25 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 972.84 | 1
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 291.79 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 254.25 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 175.8 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 1348.78 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 3643.84 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 2784.31 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 3583 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1125.82 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1097.69 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 3525.17 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 881.29 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 3525.17 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 1021.55 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 369.45 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 286.4 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 206 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 1395.65 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 3787.56 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 3005.21 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 3777.62 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1172.95 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1149.85 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 3730 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 909.34 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 3728.11 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1087.59 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 414.62 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 760.51 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 552.88 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 2057.14 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 6392.84 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 5129.32 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 6389.34 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 1847.99 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 1828.93 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 6387.58 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 1714.81 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 6358.68 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 1807.25 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 83.04 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 924.54 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 9474.51 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 15233.25 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1404.48 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 7962.02 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1639.25 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 5187.87 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 23428.26 | 0.8
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 2380.88 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 6062.32 | 0.78
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 6304.39 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 6304.39 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 6909.98 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 1.3 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0.45 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.1 | 62.79 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.1 | 64.26 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 68.36 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.1 | 61.95 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.1 | 63.83 | 1 | PTAC Fan
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 1.96 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 1.71 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 1.18 | 1 | Unit Heater Fans
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 87.07 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.47 | 301.36 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.39 | 245.46 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.46 | 291.92 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.13 | 83.23 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.12 | 78.29 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.46 | 294.43 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 91.88 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.42 | 269.17 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.12 | 77.29 | 1 | PTAC Fan
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 2.48 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 1.92 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 1.38 | 1 | Unit Heater Fans
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 86.32 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.47 | 301.05 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.4 | 251.73 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.47 | 300.73 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 86.11 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.13 | 81.39 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.44 | 283.1 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.12 | 75.17 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.44 | 278.44 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.13 | 79.7 | 1 | PTAC Fan
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 2.78 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.03 | 5.1 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.02 | 3.71 | 1 | Unit Heater Fans
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.17 | 108.21 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.6 | 380.5 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.5 | 315.97 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.6 | 380.92 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.17 | 108.61 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.17 | 106.76 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.58 | 371.02 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.15 | 97.4 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.58 | 368.02 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.17 | 105 | 1 | PTAC Fan
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0.56 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.03 | 6.2 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.51 | 596.85 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.83 | 942.49 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.08 | 88.48 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.43 | 501.57 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 103.27 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.32 | 370.1 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.5 | 1644.2 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.13 | 149.99 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.35 | 411.04 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.38 | 435.3 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 39398.5507 | 66.1654 | 168.0397 | 0 | 0.0007 | 10447.5783 | 16415.9034
February | 34136.3814 | 57.2159 | 144.9758 | 0 | 0.0006 | 9013.5715 | 14213.0848
March | 34778.7091 | 60.4264 | 159.4861 | 0 | 0.0007 | 9916.6076 | 14675.6413
April | 32090.2835 | 58.0547 | 159.8537 | 0 | 0.0007 | 9940.3553 | 13751.448
May | 34207.3823 | 64.3623 | 184.0795 | 0 | 0.0007 | 11447.6917 | 14885.211
June | 37409.9526 | 71.8257 | 209.2515 | 0 | 0.0008 | 13013.5821 | 16410.2517
July | 41218.0535 | 79.5649 | 232.914 | 0 | 0.0009 | 14485.3139 | 18119.828
August | 41132.4527 | 79.4303 | 232.5996 | 0 | 0.0009 | 14465.7716 | 18085.0012
September | 34597.8568 | 66.21 | 192.3262 | 0 | 0.0008 | 11960.9071 | 15156.8923
October | 33919.0493 | 62.8446 | 177.1436 | 0 | 0.0007 | 11016.0346 | 14670.5798
November | 33099.1004 | 58.7015 | 158.373 | 0 | 0.0007 | 9847.8597 | 14076.0104
December | 37314.7392 | 62.8462 | 160.1474 | 0 | 0.0007 | 9956.9635 | 15564.1413
Annual Sum or Average | 433302.5114 | 787.6477 | 2179.19 | 0 | 0.0089 | 135512.2369 | 186023.9933
Minimum of Months | 32090.2835 | 57.2159 | 144.9758 | 0 | 0.0006 | 9013.5715 | 13751.448
Maximum of Months | 41218.0535 | 79.5649 | 232.914 | 0 | 0.0009 | 14485.3139 | 18119.828
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 165661000000 | 109696.956 | 31-JAN-07:15 | 24319.757 | 51459.268 | 7234.686 | 24198.457 | 0 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 142923000000 | 100233.141 | 01-FEB-07:15 | 24319.757 | 51459.268 | 6783.75 | 15185.578 | 0 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 157242000000 | 109149.752 | 26-MAR-07:00 | 26344.714 | 58181.634 | 7810.632 | 0 | 16727.994 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 157618000000 | 107094.742 | 05-APR-19:15 | 36525.994 | 38968.112 | 8411.228 | 0 | 20704.619 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 181519000000 | 120132.587 | 15-MAY-19:15 | 36525.994 | 38968.112 | 8985.912 | 0 | 33167.78 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 206349000000 | 139692.937 | 30-JUN-19:15 | 36525.994 | 38968.112 | 10052.239 | 0 | 54061.813 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 229685000000 | 146099.143 | 24-JUL-19:30 | 36525.994 | 38968.112 | 10239.251 | 0 | 57880.997 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 229375000000 | 146464.663 | 17-AUG-19:15 | 36525.994 | 38968.112 | 10278.564 | 0 | 58207.205 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 189657000000 | 127460.73 | 17-SEP-07:00 | 26344.714 | 58181.634 | 8763.172 | 0 | 34086.432 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 174675000000 | 120637.276 | 14-OCT-07:00 | 26344.714 | 58181.634 | 8516.228 | 0 | 27509.922 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 156152000000 | 118019.568 | 04-NOV-08:00 | 26344.714 | 58181.634 | 8350.766 | 0 | 25057.676 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 157882000000 | 101951.346 | 21-DEC-07:15 | 24319.757 | 51459.268 | 6858.351 | 16829.182 | 0 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2148740000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 142923000000 | 100233.141 |  | 24319.757 | 38968.112 | 6783.75 | 0 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 229685000000 | 146464.663 |  | 36525.994 | 58181.634 | 10278.564 | 24198.457 | 58207.205 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 41344.57 | 13694.62 | 0 | 55039.19
Cost per Total Building Area ($/m2) | 10.3 | 3.41 | 0 | 13.71
Cost per Net Conditioned Building Area ($/m2) | 10.46 | 3.46 | 0 | 13.92

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3272.74 | 815.41 | 827.83
Net Site Energy | 3272.74 | 815.41 | 827.83
Total Source Energy | 8286.08 | 2064.51 | 2095.94
Net Source Energy | 8286.08 | 2064.51 | 2095.94
Area [m2]
Total Building Area | 4013.59
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 60.2
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 7.51 | 475 | 0 | 0 | 0 | 0
Cooling | 369.43 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 628.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 37.71 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 815.05 | 189.47 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 255.89 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 491.36 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2116.91 | 1155.83 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 6.46 |  | 0
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 5.38 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.6 |  | 0
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 11.84 | 3.08 | 15.43
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 9.7 | 32.61 | 10.7631
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 14 | 1.87 | 12.9
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 16.16 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 12.9 | 2.96 | 77.16
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 6.46 | 8.89 | 206.12
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2157.2117
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 9.7 | 2.96 | 11.4999
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 11.84 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 6.46 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 8.6 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 11.8 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
Total | 4013.59 |  | 11621.74 |  | 1694.58 | 184.21 | 10.425 | 15.71 | 24.2519
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 10.5838 | 15.47 | 16.4088
Unconditioned Total | 60.2 |  | 174.32 |  | 21.18 | 0 | 0 |  | 539.3029
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_REARSTAIRSFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_CORRIDORFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.13 | 90 | 90 | E
W_CORRIDORFLR1_10_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.22 | 180 | 90 | S
S_CORRIDORFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 150.51 | 270 | 180
W_REARSTORAGEFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 163.06 | 90 | 180
W_RESTROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 80.27 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM101_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_EMPLOYEELOUNGEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_LAUNDRYROOMFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 97.83 | 90 | 180
W_ELEVATORCOREFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 15.05 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_FRONTSTORAGEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 12.54 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_CORRIDORFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.36 | 0 | 90 | N
W_CORRIDORFLR2_15_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 270 | 90 | W
W_REARSTORAGEFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 180 | 90 | S
W_GUESTROOM201_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
W_ELEVATORCOREFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_FRONTSTORAGEFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 4.18 | 0 | 90 | N
W_FRONTSTAIRSFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_REARSTAIRSFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_CORRIDORFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 270 | 90 | W
W_REARSTORAGEFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 180 | 90 | S
W_GUESTROOM301_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 4.18 | 0 | 90 | N
W_FRONTSTAIRSFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_REARSTAIRSFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
R_REARSTAIRSFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
W_CORRIDORFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 270 | 90 | W
R_CORRIDORFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 125.42 | 90 | 0
W_REARSTORAGEFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 180 | 90 | S
R_REARSTORAGEFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
W_GUESTROOM401_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
R_GUESTROOM401_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM402_405_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
R_GUESTROOM402_405_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.45 | 90 | 0
W_GUESTROOM406_408_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 35.12 | 180 | 90 | S
R_GUESTROOM406_408_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 105.36 | 90 | 0
W_GUESTROOM409_412_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
R_GUESTROOM409_412_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.45 | 90 | 0
W_GUESTROOM413_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
R_GUESTROOM413_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM414_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
R_GUESTROOM414_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM415_418_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
R_GUESTROOM415_418_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.44 | 90 | 0
W_ELEVATORCOREFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 0 | 90 | N
R_ELEVATORCOREFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 15.05 | 90 | 0
W_GUESTROOM419_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
R_GUESTROOM419_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM420_423_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
R_GUESTROOM420_423_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.44 | 90 | 0
W_GUESTROOM424_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
R_GUESTROOM424_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_FRONTSTORAGEFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 4.18 | 0 | 90 | N
R_FRONTSTORAGEFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12.54 | 90 | 0
W_FRONTSTAIRSFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
R_FRONTSTAIRSFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
W_CORRIDORFLR1_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 2.69 | 2.69 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
D_CORRIDORFLR1_16_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.44 | 4.44 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 2.69 | 2.69 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 2.97 | 2.97 | 3.18 | 0.402 | 0.495 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 2.97 | 2.97 | 3.18 | 0.402 | 0.495 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 2.97 | 2.97 | 3.18 | 0.402 | 0.495 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 2.97 | 2.97 | 3.18 | 0.402 | 0.495 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 2.96 | 2.96 | 3.18 | 0.402 | 0.495 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_GUESTROOM101_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_CORRIDORFLR2_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 1.31 | 1.31 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 1.31 | 1.31 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_GUESTROOM201_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 3.41 | 3.41 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_CORRIDORFLR3_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 1.31 | 1.31 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 1.31 | 1.31 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_GUESTROOM301_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 3.41 | 3.41 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_CORRIDORFLR4_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 1.31 | 1.31 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 1.31 | 1.31 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_GUESTROOM401_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 3.41 | 3.41 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM424_3_0_0 | 0 | N
Total or Average |  |  | 184.21 | 3.18 | 0.441 | 0.545
North Total or Average |  |  | 72.38 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 111.83 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1778.96 | 1420.77 | 358.18 | 0.8 | 3.64
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1820.07 | 1453.61 | 366.46 | 0.8 | 3.62
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1917.83 | 1531.69 | 386.15 | 0.8 | 3.64
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1810.34 | 1445.84 | 364.5 | 0.8 | 3.63
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1898.19 | 1516 | 382.19 | 0.8 | 3.6
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2678.36 | 2139.08 | 539.27 | 0.8 | 3.45
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9067.01 | 7241.42 | 1825.59 | 0.8 | 2.99
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7355.4 | 5874.43 | 1480.97 | 0.8 | 2.98
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8786.29 | 7017.22 | 1769.07 | 0.8 | 2.98
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2490.85 | 1989.33 | 501.52 | 0.8 | 3.5
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2428.5 | 1939.54 | 488.97 | 0.8 | 3.53
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9221.49 | 7364.79 | 1856.7 | 0.8 | 2.99
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2875.61 | 2296.62 | 578.99 | 0.8 | 3.39
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8414.15 | 6720.01 | 1694.15 | 0.8 | 2.99
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2400.47 | 1917.15 | 483.32 | 0.8 | 3.55
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2666.11 | 2129.3 | 536.81 | 0.8 | 3.45
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9094.93 | 7263.71 | 1831.22 | 0.8 | 2.99
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7564.6 | 6041.51 | 1523.09 | 0.8 | 2.99
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9085.65 | 7256.31 | 1829.35 | 0.8 | 2.99
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2590.29 | 2068.75 | 521.54 | 0.8 | 3.49
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2535.72 | 2025.17 | 510.55 | 0.8 | 3.48
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8889.95 | 7100.01 | 1789.95 | 0.8 | 2.99
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2356.73 | 1882.22 | 474.52 | 0.8 | 3.53
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8740.36 | 6980.53 | 1759.83 | 0.8 | 2.99
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2485.24 | 1984.85 | 500.39 | 0.8 | 3.51
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3361.77 | 2684.89 | 676.87 | 0.8 | 3.26
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11536.87 | 9213.98 | 2322.89 | 0.8 | 2.99
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9514.75 | 7599 | 1915.74 | 0.8 | 2.98
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11546.54 | 9221.7 | 2324.83 | 0.8 | 2.99
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3304.99 | 2639.55 | 665.44 | 0.8 | 3.28
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3339.23 | 2666.89 | 672.34 | 0.8 | 3.27
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11662.17 | 9314.06 | 2348.12 | 0.8 | 2.98
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3058.96 | 2443.05 | 615.9 | 0.8 | 3.34
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11565.64 | 9236.96 | 2328.68 | 0.8 | 2.99
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3281.76 | 2621 | 660.77 | 0.8 | 3.29
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9584.7 | 7654.87 | 1929.83 | 0.8 | 4.06
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 15362.91 | 12269.67 | 3093.24 | 0.8 | 4.03
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1374.55 | 1097.8 | 276.76 | 0.8 | 4.01
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8149.79 | 6508.87 | 1640.92 | 0.8 | 4.05
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1473.75 | 1177.01 | 296.73 | 0.8 | 4.07
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6266.79 | 5005.01 | 1261.79 | 0.8 | 4.06
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 29622.2 | 23657.92 | 5964.27 | 0.8 | 3.74
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2448.51 | 1955.51 | 492.99 | 0.8 | 4.07
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6635.86 | 5299.76 | 1336.1 | 0.8 | 4.05
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5667.89 | 4526.69 | 1141.2 | 0.8 | 4.05
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5667.89 | 4526.69 | 1141.2 | 0.8 | 4.05
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7411.05 | 5918.88 | 1492.18 | 0.8 | 4.06
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 86.68 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 819.84 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 840.86 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1046.62 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 1046.09 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 840.46 | 1
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 182.99 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 143.97 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 112.83 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 1134.2 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 3013.16 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 2299.91 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 2955.43 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 966.59 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 937.5 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 2800.94 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 571.62 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 2833.62 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 861.36 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 257 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 173.12 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 140.63 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 1175.53 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 3138.44 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 2502.87 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 3129.99 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1008.8 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 984.82 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 3077.94 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 735.98 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 3078.98 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 923.08 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 300.43 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 573.91 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 443.32 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 1759.84 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 5430.41 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 4372.7 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 5428.01 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 1604.68 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 1584.58 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 5422.81 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 1458.98 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 5395.78 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 1564.95 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 43.48 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 735.76 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 8470.8 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 13577.48 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1175.07 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 7202.64 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1302.47 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 4472.83 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 22532.73 | 0.8
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 2163.95 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 5089.54 | 0.78
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 5009.18 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 5009.18 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 6549.76 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0.7 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 68.39 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 69.97 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.12 | 73.73 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 69.59 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 72.97 | 1 | PTAC Fan
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 1.49 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 1.17 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0.92 | 1 | Unit Heater Fans
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.16 | 102.96 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.55 | 348.56 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.44 | 282.76 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.53 | 337.76 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.15 | 95.75 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.15 | 93.36 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.56 | 354.49 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.17 | 110.54 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.51 | 323.46 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.15 | 92.28 | 1 | PTAC Fan
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 2.09 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 1.4 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 1.14 | 1 | Unit Heater Fans
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.16 | 102.49 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.55 | 349.63 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.46 | 290.8 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.55 | 349.27 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.16 | 99.58 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.15 | 97.48 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.54 | 341.75 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 90.6 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.53 | 336 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.15 | 95.54 | 1 | PTAC Fan
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 2.44 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.02 | 4.66 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.02 | 3.6 | 1 | Unit Heater Fans
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.2 | 129.23 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.7 | 443.5 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.57 | 365.77 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.7 | 443.87 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.2 | 127.05 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.2 | 128.37 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.7 | 448.32 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.18 | 117.59 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.7 | 444.61 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.2 | 126.16 | 1 | PTAC Fan
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0.35 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.03 | 5.97 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.58 | 671.6 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.93 | 1057.26 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.08 | 96.31 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.49 | 571.06 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 103.27 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.38 | 439.11 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.79 | 1957.02 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.15 | 171.57 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.4 | 464.97 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.45 | 519.29 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 50299.3792 | 80.7203 | 189.9943 | 0 | 0.0008 | 197517.2 | 20848.0168
February | 44890.868 | 72.6546 | 172.8872 | 0 | 0.0007 | 179737.4293 | 18666.5135
March | 49063.0786 | 80.3483 | 194.0495 | 0 | 0.0008 | 201745.3649 | 20493.7188
April | 47896.4196 | 80.2897 | 199.459 | 0 | 0.0008 | 207382.9501 | 20188.0611
May | 52747.3218 | 89.7964 | 227.1025 | 0 | 0.0009 | 236134.23 | 22367.5665
June | 54816.9476 | 93.9275 | 239.3032 | 0 | 0.0009 | 248824.2014 | 23304.8165
July | 60499.4054 | 103.9809 | 265.8236 | 0 | 0.001 | 276401.826 | 25751.7059
August | 58736.3854 | 100.9126 | 257.8706 | 0 | 0.001 | 268132.0991 | 24997.5284
September | 53223.6205 | 91.2059 | 232.3933 | 0 | 0.0009 | 241639.4199 | 22628.2602
October | 49918.2095 | 84.2101 | 210.7539 | 0 | 0.0008 | 219130.2959 | 21092.3444
November | 47351.2687 | 77.6485 | 187.8394 | 0 | 0.0007 | 195289.6642 | 19788.8459
December | 50487.2393 | 81.0114 | 190.648 | 0 | 0.0008 | 198196.6887 | 20924.8675
Annual Sum or Average | 619930.1435 | 1036.7062 | 2568.1244 | 0 | 0.0101 | 2670130 | 261052.2455
Minimum of Months | 44890.868 | 72.6546 | 172.8872 | 0 | 0.0007 | 179737.4293 | 18666.5135
Maximum of Months | 60499.4054 | 103.9809 | 265.8236 | 0 | 0.001 | 276401.826 | 25751.7059
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 156594000000 | 100289.798 | 21-JAN-08:00 | 26344.714 | 58181.634 | 7893.295 | 0 | 7785.377 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 142498000000 | 101193.478 | 20-FEB-08:00 | 26344.714 | 58181.634 | 8011.147 | 0 | 8571.204 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 159946000000 | 102520.129 | 26-MAR-07:00 | 26344.714 | 58181.634 | 8169.085 | 0 | 9739.918 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 164416000000 | 110688.296 | 22-APR-19:15 | 36357.328 | 38915.462 | 9550.764 | 0 | 23379.953 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 187210000000 | 117569.824 | 30-MAY-19:15 | 36525.994 | 38968.112 | 9904.245 | 0 | 29686.685 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 197271000000 | 124532.478 | 28-JUN-19:30 | 36525.994 | 38968.112 | 10334.003 | 0 | 36219.58 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 219135000000 | 132019.342 | 30-JUL-19:15 | 36441.661 | 38950.562 | 10809.065 | 0 | 43333.265 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 212578000000 | 130026.192 | 01-AUG-19:15 | 36525.994 | 38968.112 | 10725.783 | 0 | 41321.514 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 191575000000 | 121110.417 | 03-SEP-07:00 | 26344.714 | 58181.634 | 9526.009 | 0 | 26973.282 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 173729000000 | 110147.312 | 01-OCT-19:15 | 36441.661 | 38950.562 | 9692.567 | 0 | 22577.734 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 154828000000 | 102637.29 | 11-NOV-08:00 | 26344.714 | 58181.634 | 8198.063 | 0 | 9828.101 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 157133000000 | 99865.632 | 10-DEC-08:00 | 26344.714 | 58181.634 | 7847.614 | 43.188 | 7363.703 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2116910000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 142498000000 | 99865.632 |  | 26344.714 | 38915.462 | 7847.614 | 0 | 7363.703 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 219135000000 | 132019.342 |  | 36525.994 | 58181.634 | 10809.065 | 43.188 | 43333.265 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 21907.27 | 8182.23 | 0 | 30089.5
Cost per Total Building Area ($/m2) | 5.46 | 2.04 | 0 | 7.5
Cost per Net Conditioned Building Area ($/m2) | 5.54 | 2.07 | 0 | 7.61

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3279.25 | 817.04 | 829.48
Net Site Energy | 3279.25 | 817.04 | 829.48
Total Source Energy | 4813.1 | 1199.2 | 1217.46
Net Source Energy | 4813.1 | 1199.2 | 1217.46
Area [m2]
Total Building Area | 4013.59
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 60.2
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 8.87 | 660.72 | 0 | 0 | 0 | 0
Cooling | 196.52 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 628.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 37.66 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 815.05 | 189.47 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 206.2 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 533.43 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1895.63 | 1383.63 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 6.46 |  | 0
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 5.38 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.6 |  | 0
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 11.84 | 3.08 | 15.43
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 9.7 | 32.61 | 10.7631
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 14 | 1.87 | 12.9
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 16.16 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 12.9 | 2.96 | 77.16
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 6.46 | 8.89 | 206.12
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2157.2117
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 9.7 | 2.96 | 11.4999
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 11.84 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 6.46 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 8.6 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 11.8 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
Total | 4013.59 |  | 11621.74 |  | 1694.58 | 184.21 | 10.425 | 15.71 | 24.2519
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 10.5838 | 15.47 | 16.4088
Unconditioned Total | 60.2 |  | 174.32 |  | 21.18 | 0 | 0 |  | 539.3029
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_REARSTAIRSFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_CORRIDORFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.13 | 90 | 90 | E
W_CORRIDORFLR1_10_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.22 | 180 | 90 | S
S_CORRIDORFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 150.51 | 270 | 180
W_REARSTORAGEFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 163.06 | 90 | 180
W_RESTROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 80.27 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM101_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_EMPLOYEELOUNGEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_LAUNDRYROOMFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 97.83 | 90 | 180
W_ELEVATORCOREFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 15.05 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_FRONTSTORAGEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 12.54 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_CORRIDORFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.36 | 0 | 90 | N
W_CORRIDORFLR2_15_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 270 | 90 | W
W_REARSTORAGEFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 180 | 90 | S
W_GUESTROOM201_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
W_ELEVATORCOREFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_FRONTSTORAGEFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 4.18 | 0 | 90 | N
W_FRONTSTAIRSFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_REARSTAIRSFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_CORRIDORFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 270 | 90 | W
W_REARSTORAGEFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 180 | 90 | S
W_GUESTROOM301_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 4.18 | 0 | 90 | N
W_FRONTSTAIRSFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_REARSTAIRSFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
R_REARSTAIRSFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
W_CORRIDORFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 270 | 90 | W
R_CORRIDORFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 125.42 | 90 | 0
W_REARSTORAGEFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 180 | 90 | S
R_REARSTORAGEFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
W_GUESTROOM401_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
R_GUESTROOM401_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM402_405_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
R_GUESTROOM402_405_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.45 | 90 | 0
W_GUESTROOM406_408_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 35.12 | 180 | 90 | S
R_GUESTROOM406_408_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 105.36 | 90 | 0
W_GUESTROOM409_412_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
R_GUESTROOM409_412_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.45 | 90 | 0
W_GUESTROOM413_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
R_GUESTROOM413_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM414_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
R_GUESTROOM414_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM415_418_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
R_GUESTROOM415_418_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.44 | 90 | 0
W_ELEVATORCOREFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 0 | 90 | N
R_ELEVATORCOREFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 15.05 | 90 | 0
W_GUESTROOM419_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
R_GUESTROOM419_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM420_423_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
R_GUESTROOM420_423_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.44 | 90 | 0
W_GUESTROOM424_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
R_GUESTROOM424_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_FRONTSTORAGEFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 4.18 | 0 | 90 | N
R_FRONTSTORAGEFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12.54 | 90 | 0
W_FRONTSTAIRSFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
R_FRONTSTAIRSFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
W_CORRIDORFLR1_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 2.69 | 2.69 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
D_CORRIDORFLR1_16_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.44 | 4.44 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 2.69 | 2.69 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 2.97 | 2.97 | 3.18 | 0.402 | 0.495 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 2.97 | 2.97 | 3.18 | 0.402 | 0.495 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 2.97 | 2.97 | 3.18 | 0.402 | 0.495 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 2.97 | 2.97 | 3.18 | 0.402 | 0.495 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 2.96 | 2.96 | 3.18 | 0.402 | 0.495 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_GUESTROOM101_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_CORRIDORFLR2_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 1.31 | 1.31 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 1.31 | 1.31 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_GUESTROOM201_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 3.41 | 3.41 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_CORRIDORFLR3_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 1.31 | 1.31 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 1.31 | 1.31 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_GUESTROOM301_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 3.41 | 3.41 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_CORRIDORFLR4_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 1.31 | 1.31 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 1.31 | 1.31 | 3.18 | 0.402 | 0.495 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_GUESTROOM401_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 3.41 | 3.41 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.64 | 1.64 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1.65 | 1.65 | 3.18 | 0.402 | 0.495 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM424_3_0_0 | 0 | N
Total or Average |  |  | 184.21 | 3.18 | 0.441 | 0.545
North Total or Average |  |  | 72.38 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 111.83 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1595.34 | 1274.12 | 321.21 | 0.8 | 3.64
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1635.14 | 1305.91 | 329.23 | 0.8 | 3.63
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1673.54 | 1336.58 | 336.96 | 0.8 | 3.62
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1248.14 | 996.83 | 251.31 | 0.8 | 3.66
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1367.13 | 1091.86 | 275.26 | 0.8 | 3.61
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2270.29 | 1813.18 | 457.11 | 0.8 | 3.58
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8303.23 | 6631.42 | 1671.81 | 0.8 | 2.98
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6824.98 | 5450.81 | 1374.17 | 0.8 | 2.98
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8032.92 | 6415.54 | 1617.39 | 0.8 | 2.99
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2212.64 | 1767.13 | 445.5 | 0.8 | 3.57
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1774.48 | 1417.2 | 357.28 | 0.8 | 3.64
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7019.97 | 5606.53 | 1413.43 | 0.8 | 2.98
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2234.39 | 1784.51 | 449.88 | 0.8 | 3.56
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6352.98 | 5073.84 | 1279.14 | 0.8 | 2.98
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1791.82 | 1431.04 | 360.77 | 0.8 | 3.63
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2240.49 | 1789.38 | 451.11 | 0.8 | 3.59
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8297.63 | 6626.94 | 1670.68 | 0.8 | 2.98
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7015.25 | 5602.77 | 1412.48 | 0.8 | 2.98
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8286.49 | 6618.05 | 1668.44 | 0.8 | 2.98
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2288.27 | 1827.54 | 460.73 | 0.8 | 3.57
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1850.72 | 1478.09 | 372.63 | 0.8 | 3.61
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6726.72 | 5372.33 | 1354.39 | 0.8 | 2.99
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1787.78 | 1427.82 | 359.96 | 0.8 | 3.63
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6611.71 | 5280.48 | 1331.23 | 0.8 | 2.99
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1850.48 | 1477.89 | 372.58 | 0.8 | 3.62
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2652.61 | 2118.52 | 534.09 | 0.8 | 3.46
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9781.19 | 7811.8 | 1969.39 | 0.8 | 2.98
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8216.37 | 6562.05 | 1654.32 | 0.8 | 2.99
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9789.36 | 7818.32 | 1971.04 | 0.8 | 2.98
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2703.84 | 2159.44 | 544.4 | 0.8 | 3.44
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2298.76 | 1835.92 | 462.84 | 0.8 | 3.56
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8303.33 | 6631.5 | 1671.83 | 0.8 | 2.98
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2165.2 | 1729.24 | 435.95 | 0.8 | 3.59
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8235.35 | 6577.21 | 1658.14 | 0.8 | 2.99
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2298.45 | 1835.67 | 462.78 | 0.8 | 3.56
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7516.58 | 6003.16 | 1513.42 | 0.8 | 4.04
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 15344 | 11672.83 | 3671.17 | 0.76 | 3.9
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1201.81 | 959.84 | 241.98 | 0.8 | 4.01
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8684.99 | 6369.72 | 2315.27 | 0.73 | 3.83
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1739.75 | 1291.66 | 448.09 | 0.74 | 3.87
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4982.27 | 3979.12 | 1003.15 | 0.8 | 4.05
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 24295.76 | 19403.94 | 4891.82 | 0.8 | 3.75
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1866.74 | 1490.88 | 375.86 | 0.8 | 4.02
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4747.97 | 3791.99 | 955.98 | 0.8 | 4.07
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6633.9 | 4943.04 | 1690.86 | 0.75 | 3.87
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6576.69 | 4918.38 | 1658.31 | 0.75 | 3.87
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6395.63 | 4840.35 | 1555.28 | 0.76 | 3.9
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 762.15 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 769.13 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 947.92 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 964.94 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 768.77 | 1
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 76.78 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 77.72 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 46.34 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 1062.99 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 3048.6 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 2286.45 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 3048.6 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 925.31 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 898.59 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 3048.6 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 685.08 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 3048.6 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 820.26 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 187.38 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 108.66 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 84.7 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 1104.79 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 3048.6 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 2384.36 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 3048.6 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 969.56 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 946.89 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 3048.6 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 762.15 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 3048.6 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 884.03 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 234.24 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 470.88 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 345.83 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 1630.52 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 5071.86 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 4071.47 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 5071.86 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 1507.31 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 1486.6 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 5066.88 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 1353.73 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 5042.76 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 1471.34 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 627.35 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 7230.41 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 13237.77 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1156.06 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 6871.91 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1417.64 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 4415.02 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 21703.53 | 0.8
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 1795.67 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 4567.21 | 0.78
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 5452.1 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 5452.1 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 5452.1 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.1 | 61.33 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.1 | 62.86 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.1 | 64.33 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.08 | 47.98 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.08 | 52.56 | 1 | PTAC Fan
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0.52 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0.53 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0.31 | 1 | Unit Heater Fans
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 87.27 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.5 | 319.19 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.41 | 262.37 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.49 | 308.8 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.13 | 85.06 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 68.21 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.42 | 269.86 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.13 | 85.89 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.38 | 244.22 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 68.88 | 1 | PTAC Fan
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 1.27 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0.74 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0.57 | 1 | Unit Heater Fans
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 86.13 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.5 | 318.98 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.42 | 269.68 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.5 | 318.55 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 87.97 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 71.15 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.41 | 258.59 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 68.73 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.4 | 254.17 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 71.14 | 1 | PTAC Fan
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 1.59 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.02 | 3.19 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 2.34 | 1 | Unit Heater Fans
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.16 | 101.97 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.59 | 376.01 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.5 | 315.85 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.59 | 376.32 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.16 | 103.94 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 88.37 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.5 | 319.2 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.13 | 83.23 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.5 | 316.58 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 88.36 | 1 | PTAC Fan
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.02 | 4.25 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.45 | 526.69 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.83 | 947.06 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.07 | 84.21 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.43 | 500.57 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 103.27 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.3 | 349.11 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.47 | 1605.12 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.11 | 130.8 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.29 | 332.69 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 16694.3826 | 20.186 | 32.1999 | 0 | 0.0001 | 424986.5163 | 6316.9056
February | 14065.5337 | 17.3305 | 29.1928 | 0 | 0.0001 | 385371.1047 | 5356.801
March | 15270.8539 | 18.9698 | 32.6785 | 0 | 0.0001 | 431417.2769 | 5832.3488
April | 13559.6937 | 17.3631 | 32.3304 | 0 | 0.0001 | 426927.0463 | 5234.395
May | 12673.8654 | 17.0142 | 35.2329 | 0 | 0.0001 | 465398.7148 | 4976.559
June | 11623.0899 | 16.071 | 35.2965 | 0 | 0.0001 | 466310.8156 | 4614.0234
July | 11826.6962 | 16.757 | 38.4969 | 0 | 0.0002 | 508650.4073 | 4738.1624
August | 11759.7997 | 16.7261 | 38.6871 | 0 | 0.0002 | 511172.9211 | 4718.2058
September | 11744.1096 | 16.2281 | 35.5985 | 0 | 0.0001 | 470299.122 | 4660.9658
October | 12898.1514 | 17.0076 | 33.892 | 0 | 0.0001 | 447637.6306 | 5031.6753
November | 14588.5169 | 18.1507 | 31.4003 | 0 | 0.0001 | 414548.4816 | 5574.7982
December | 16486.0819 | 20.0216 | 32.3562 | 0 | 0.0001 | 427069.7689 | 6247.4497
Annual Sum or Average | 163190.7749 | 211.8259 | 407.362 | 0 | 0.0017 | 5379790 | 63302.2899
Minimum of Months | 11623.0899 | 16.071 | 29.1928 | 0 | 0.0001 | 385371.1047 | 4614.0234
Maximum of Months | 16694.3826 | 20.186 | 38.6871 | 0 | 0.0002 | 511172.9211 | 6316.9056
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 149749000000 | 97008.862 | 29-JAN-08:30 | 26344.714 | 58181.634 | 6516.138 | 0 | 5881.598 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 135790000000 | 97820.749 | 20-FEB-08:00 | 26344.714 | 58181.634 | 6620.677 | 0 | 6588.946 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 152015000000 | 100155.786 | 29-MAR-19:00 | 36525.994 | 38968.112 | 7780.749 | 0 | 14396.143 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 150432000000 | 104787.224 | 30-APR-07:00 | 26344.714 | 58181.634 | 7428.118 | 0 | 12747.979 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 163988000000 | 108062.709 | 07-MAY-07:00 | 26344.714 | 58181.634 | 7790.184 | 0 | 15661.399 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 164310000000 | 113270.204 | 18-JUN-07:00 | 26344.714 | 58181.634 | 8098.081 | 0 | 20560.996 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 179228000000 | 117491.199 | 24-JUL-19:15 | 36525.994 | 38968.112 | 8983.19 | 0 | 32929.124 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 180117000000 | 116167.505 | 06-AUG-19:45 | 36441.661 | 38950.562 | 8825.019 | 0 | 29465.474 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 165715000000 | 120733.044 | 02-SEP-19:15 | 36357.328 | 38915.462 | 9067.436 | 0 | 33908.029 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 157730000000 | 104858.899 | 01-OCT-07:00 | 26344.714 | 58181.634 | 7457.038 | 0 | 12790.735 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 146071000000 | 104306.169 | 04-NOV-08:00 | 26344.714 | 58181.634 | 7363.982 | 0 | 12331.06 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 150483000000 | 96986.468 | 31-DEC-08:00 | 26344.714 | 58181.634 | 6506.038 | 0 | 5869.304 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1895630000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 135790000000 | 96986.468 |  | 26344.714 | 38915.462 | 6506.038 | 0 | 5869.304 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 180117000000 | 120733.044 |  | 36525.994 | 58181.634 | 9067.436 | 0 | 33908.029 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 37853.21 | 11538.78 | 0 | 49391.99
Cost per Total Building Area ($/m2) | 9.43 | 2.87 | 0 | 12.31
Cost per Net Conditioned Building Area ($/m2) | 9.57 | 2.92 | 0 | 12.49

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3798.33 | 946.37 | 960.78
Net Site Energy | 3798.33 | 946.37 | 960.78
Total Source Energy | 9337.01 | 2326.35 | 2361.78
Net Source Energy | 9337.01 | 2326.35 | 2361.78
Area [m2]
Total Building Area | 4013.59
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 60.2
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 71.58 | 939.62 | 0 | 0 | 0 | 0
Cooling | 334.36 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 628.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 37.67 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 815.05 | 189.47 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 224.62 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 554.63 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2114.6 | 1683.72 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 6.46 |  | 0
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 5.38 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.6 |  | 0
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 11.84 | 3.08 | 15.43
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 9.7 | 32.61 | 10.7631
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 14 | 1.87 | 12.9
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 16.16 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 12.9 | 2.96 | 77.16
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 6.46 | 8.89 | 206.12
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2157.2117
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 9.7 | 2.96 | 11.4999
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 11.84 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 6.46 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 8.6 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 11.8 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
Total | 4013.59 |  | 11621.74 |  | 1694.58 | 184.21 | 10.425 | 15.71 | 24.2519
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 10.5838 | 15.47 | 16.4088
Unconditioned Total | 60.2 |  | 174.32 |  | 21.18 | 0 | 0 |  | 539.3029
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_REARSTAIRSFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_CORRIDORFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.13 | 90 | 90 | E
W_CORRIDORFLR1_10_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.22 | 180 | 90 | S
S_CORRIDORFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 150.51 | 270 | 180
W_REARSTORAGEFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 163.06 | 90 | 180
W_RESTROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 80.27 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM101_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_EMPLOYEELOUNGEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_LAUNDRYROOMFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 97.83 | 90 | 180
W_ELEVATORCOREFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 15.05 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_FRONTSTORAGEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 12.54 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_CORRIDORFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.36 | 0 | 90 | N
W_CORRIDORFLR2_15_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 270 | 90 | W
W_REARSTORAGEFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 180 | 90 | S
W_GUESTROOM201_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
W_ELEVATORCOREFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_FRONTSTORAGEFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 4.18 | 0 | 90 | N
W_FRONTSTAIRSFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_REARSTAIRSFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_CORRIDORFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 270 | 90 | W
W_REARSTORAGEFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 180 | 90 | S
W_GUESTROOM301_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 4.18 | 0 | 90 | N
W_FRONTSTAIRSFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_REARSTAIRSFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
R_REARSTAIRSFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
W_CORRIDORFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 270 | 90 | W
R_CORRIDORFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 125.42 | 90 | 0
W_REARSTORAGEFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 180 | 90 | S
R_REARSTORAGEFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
W_GUESTROOM401_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
R_GUESTROOM401_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM402_405_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
R_GUESTROOM402_405_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.45 | 90 | 0
W_GUESTROOM406_408_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 35.12 | 180 | 90 | S
R_GUESTROOM406_408_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 105.36 | 90 | 0
W_GUESTROOM409_412_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
R_GUESTROOM409_412_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.45 | 90 | 0
W_GUESTROOM413_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
R_GUESTROOM413_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM414_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
R_GUESTROOM414_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM415_418_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
R_GUESTROOM415_418_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.44 | 90 | 0
W_ELEVATORCOREFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 0 | 90 | N
R_ELEVATORCOREFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 15.05 | 90 | 0
W_GUESTROOM419_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
R_GUESTROOM419_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM420_423_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
R_GUESTROOM420_423_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.44 | 90 | 0
W_GUESTROOM424_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
R_GUESTROOM424_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_FRONTSTORAGEFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 4.18 | 0 | 90 | N
R_FRONTSTORAGEFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12.54 | 90 | 0
W_FRONTSTAIRSFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
R_FRONTSTAIRSFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
W_CORRIDORFLR1_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_EAST | 2.69 | 2.69 | 3.18 | 0.501 | 0.622 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
D_CORRIDORFLR1_16_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_WEST | 4.44 | 4.44 | 3.18 | 0.501 | 0.622 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 2.69 | 2.69 | 3.18 | 0.501 | 0.622 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 2.97 | 2.97 | 3.18 | 0.501 | 0.622 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 2.97 | 2.97 | 3.18 | 0.501 | 0.622 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 2.97 | 2.97 | 3.18 | 0.501 | 0.622 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 2.97 | 2.97 | 3.18 | 0.501 | 0.622 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 2.96 | 2.96 | 3.18 | 0.501 | 0.622 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_GUESTROOM101_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_CORRIDORFLR2_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_EAST | 1.31 | 1.31 | 3.18 | 0.501 | 0.622 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_WEST | 1.31 | 1.31 | 3.18 | 0.501 | 0.622 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_GUESTROOM201_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 3.41 | 3.41 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_CORRIDORFLR3_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_EAST | 1.31 | 1.31 | 3.18 | 0.501 | 0.622 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_WEST | 1.31 | 1.31 | 3.18 | 0.501 | 0.622 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_GUESTROOM301_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 3.41 | 3.41 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_CORRIDORFLR4_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_EAST | 1.31 | 1.31 | 3.18 | 0.501 | 0.622 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_WEST | 1.31 | 1.31 | 3.18 | 0.501 | 0.622 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_GUESTROOM401_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 3.41 | 3.41 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM424_3_0_0 | 0 | N
Total or Average |  |  | 184.21 | 3.18 | 0.501 | 0.622
North Total or Average |  |  | 72.38 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 111.83 | 3.18 | 0.501 | 0.622
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1845.99 | 1415.15 | 430.84 | 0.77 | 3.58
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1879.78 | 1445.04 | 434.75 | 0.77 | 3.57
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1951.92 | 1508.9 | 443.02 | 0.77 | 3.59
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1677.67 | 1304.05 | 373.61 | 0.78 | 3.62
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1731.42 | 1352.31 | 379.11 | 0.78 | 3.6
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2309.97 | 1844.87 | 465.1 | 0.8 | 3.57
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8535.69 | 6691.89 | 1843.81 | 0.78 | 2.96
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6853.59 | 5423.53 | 1430.07 | 0.79 | 2.98
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8324.99 | 6504.41 | 1820.58 | 0.78 | 2.97
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2285.14 | 1807.86 | 477.28 | 0.79 | 3.55
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2034.08 | 1624.53 | 409.55 | 0.8 | 3.61
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7819.68 | 6207.72 | 1611.97 | 0.79 | 2.98
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2409.81 | 1924.61 | 485.2 | 0.8 | 3.54
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7297.98 | 5737.28 | 1560.7 | 0.79 | 2.98
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2019.11 | 1610.05 | 409.06 | 0.8 | 3.61
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2284.84 | 1824.8 | 460.04 | 0.8 | 3.58
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8521.99 | 6679.69 | 1842.3 | 0.78 | 2.97
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6987.83 | 5543.38 | 1444.45 | 0.79 | 2.98
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8514.34 | 6672.88 | 1841.46 | 0.78 | 2.97
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2344.56 | 1860.92 | 483.64 | 0.79 | 3.55
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2113.73 | 1688.14 | 425.59 | 0.8 | 3.62
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7585.74 | 5996.57 | 1589.17 | 0.79 | 2.98
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1984.83 | 1579.05 | 405.78 | 0.8 | 3.62
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7491.11 | 5911.24 | 1579.87 | 0.79 | 2.98
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2073.37 | 1655.91 | 417.46 | 0.8 | 3.64
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2805.61 | 2240.72 | 564.9 | 0.8 | 3.43
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10345.86 | 8156.08 | 2189.78 | 0.79 | 2.97
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8487.01 | 6748.86 | 1738.14 | 0.8 | 2.98
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10354.32 | 8163.6 | 2190.72 | 0.79 | 2.97
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2848.33 | 2272.02 | 576.32 | 0.8 | 3.41
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2723.26 | 2174.95 | 548.31 | 0.8 | 3.43
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9535.98 | 7613.53 | 1922.46 | 0.8 | 2.99
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2496.98 | 1994.23 | 502.75 | 0.8 | 3.5
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9476.38 | 7559.77 | 1916.62 | 0.8 | 2.98
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2681.06 | 2141.25 | 539.82 | 0.8 | 3.45
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12866.15 | 8698.58 | 4167.56 | 0.68 | 3.67
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 21341.5 | 14428.63 | 6912.87 | 0.68 | 3.45
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1754.11 | 1225.45 | 528.66 | 0.7 | 3.76
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11034.84 | 7460.47 | 3574.37 | 0.68 | 3.67
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2210.8 | 1494.69 | 716.12 | 0.68 | 3.67
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6633.96 | 4818.96 | 1815 | 0.73 | 3.81
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 25700.23 | 20336.95 | 5363.28 | 0.79 | 3.72
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3200.41 | 2163.74 | 1036.67 | 0.68 | 3.67
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7448.67 | 5341.79 | 2106.88 | 0.72 | 3.78
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8502.54 | 5748.42 | 2754.11 | 0.68 | 3.66
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8502.54 | 5748.42 | 2754.11 | 0.68 | 3.66
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9227.77 | 6238.74 | 2989.03 | 0.68 | 3.66
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 500.08 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 281.1 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 1238.03 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 1261.2 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1479.45 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 1477.54 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 1263.34 | 1
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 611.34 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 507.06 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 350.32 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 1752.47 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 4720.78 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 3644.33 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 4643.67 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1404.18 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1374.88 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 4356.7 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 1029.53 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 4530.36 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 1305.85 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 629.86 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 540.16 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 385.73 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 1805.82 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 4880.18 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 3880.05 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 4864.62 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1456.29 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1433.13 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 4821.31 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 1200.78 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 4813.86 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1375.86 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 677.94 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1180.35 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 848.32 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 2654.35 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 8228.07 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 6605.59 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 8220.05 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 2320.05 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 2302.28 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 8221.16 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 2215.01 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 8186.63 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 2273.72 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 195.91 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1351.14 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 11144.55 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 18485.83 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1659.1 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 9558.28 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1914.98 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 6004.77 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 24763.51 | 0.8
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 2772.17 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 7003.18 | 0.78
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 7364.83 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 7364.83 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 7993.02 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.02 | 3.41 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 1.92 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.1 | 64.78 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.1 | 66.38 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 69.81 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.1 | 60.75 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.1 | 63.37 | 1 | PTAC Fan
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.02 | 4.17 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.02 | 3.46 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 2.39 | 1 | Unit Heater Fans
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 88.8 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.5 | 315.04 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.41 | 258.22 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.48 | 304.93 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 86.05 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.12 | 78.19 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.47 | 296.68 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.15 | 92.64 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.43 | 271 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.12 | 77.36 | 1 | PTAC Fan
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.02 | 4.3 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.02 | 3.69 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 2.63 | 1 | Unit Heater Fans
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 87.83 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.49 | 314.38 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.42 | 264.71 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.49 | 314.02 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 88.92 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.13 | 81.26 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.45 | 285.15 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.12 | 75.66 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.44 | 280.49 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.13 | 79.7 | 1 | PTAC Fan
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.02 | 4.63 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.04 | 8.06 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.03 | 5.79 | 1 | Unit Heater Fans
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.17 | 107.85 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.61 | 386.56 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.51 | 323.19 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.61 | 386.97 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.17 | 109.2 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.16 | 104.69 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.58 | 366.33 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.15 | 95.99 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.57 | 363.39 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.16 | 103.07 | 1 | PTAC Fan
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 1.34 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.05 | 9.22 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.52 | 600.97 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.86 | 979.05 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.08 | 89.47 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.44 | 515.43 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 103.27 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.32 | 373.5 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.52 | 1664.01 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.13 | 149.49 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.35 | 406.22 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.37 | 431.02 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 74640.5153 | 123.4351 | 334.118 | 0 | 0.001 | 76901.5692 | 31157.1422
February | 62729.1745 | 103.5375 | 279.603 | 0 | 0.0009 | 64353.9102 | 26165.9306
March | 64416.4341 | 106.9961 | 291.1622 | 0 | 0.0009 | 67015.4858 | 26934.1421
April | 59887.3102 | 102.5675 | 289.2402 | 0 | 0.0009 | 66577.9667 | 25336.2506
May | 65162.9405 | 114.5488 | 332.3794 | 0 | 0.001 | 76512.176 | 27849.8369
June | 70490.2321 | 125.5521 | 369.3755 | 0 | 0.0011 | 85030.7802 | 30283.3225
July | 78222.0919 | 139.8164 | 412.8453 | 0 | 0.0012 | 95038.2741 | 33652.1249
August | 75091.1806 | 134.1541 | 395.9254 | 0 | 0.0012 | 91143.1736 | 32298.8617
September | 65968.8805 | 117.2763 | 344.3483 | 0 | 0.001 | 79269.1825 | 28319.6137
October | 62500.9941 | 108.8366 | 312.6101 | 0 | 0.001 | 71959.9414 | 26613.4068
November | 60929.4349 | 102.52 | 283.2889 | 0 | 0.0009 | 65205.3883 | 25601.9447
December | 70243.1416 | 116.1065 | 314.0949 | 0 | 0.001 | 72292.9058 | 29316.1449
Annual Sum or Average | 810282.3302 | 1395.3471 | 3958.9913 | 0 | 0.0121 | 911300.7538 | 343528.7216
Minimum of Months | 59887.3102 | 102.52 | 279.603 | 0 | 0.0009 | 64353.9102 | 25336.2506
Maximum of Months | 78222.0919 | 139.8164 | 412.8453 | 0 | 0.0012 | 95038.2741 | 33652.1249
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 178444000000 | 129484.773 | 08-JAN-08:15 | 26344.714 | 58181.634 | 7581.06 | 37292.587 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 149328000000 | 109798.924 | 11-FEB-08:15 | 26344.714 | 58181.634 | 6819.521 | 18368.276 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 155504000000 | 99599.883 | 31-MAR-19:30 | 36525.994 | 38968.112 | 7845.426 | 0 | 13775.562 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 154489000000 | 107545.797 | 29-APR-07:00 | 26344.714 | 58181.634 | 7798.513 | 0 | 15136.158 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 177541000000 | 118255.214 | 28-MAY-07:00 | 26344.714 | 58181.634 | 8471.708 | 0 | 25172.379 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 197308000000 | 128412.108 | 16-JUN-19:30 | 36525.994 | 38968.112 | 9512.084 | 0 | 40921.129 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 220529000000 | 141431.764 | 09-JUL-07:00 | 26344.714 | 58181.634 | 9493.548 | 0 | 47327.089 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 211491000000 | 143276.434 | 04-AUG-19:15 | 36525.994 | 38968.112 | 10210.254 | 0 | 55087.286 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 183938000000 | 121326.23 | 16-SEP-07:00 | 26344.714 | 58181.634 | 8725.239 | 0 | 27989.865 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 166978000000 | 108514.194 | 29-OCT-07:00 | 26344.714 | 58181.634 | 7862.88 | 0 | 16040.188 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 151304000000 | 104851.205 | 02-NOV-20:15 | 36525.994 | 38968.112 | 8225.768 | 0 | 18646.542 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 167750000000 | 118126.154 | 31-DEC-08:15 | 26344.714 | 58181.634 | 7112.425 | 26402.603 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2114600000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 149328000000 | 99599.883 |  | 26344.714 | 38968.112 | 6819.521 | 0 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 220529000000 | 143276.434 |  | 36525.994 | 58181.634 | 10210.254 | 37292.587 | 55087.286 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 57413.68 | 14557.06 | 0 | 71970.74
Cost per Total Building Area ($/m2) | 14.3 | 3.63 | 0 | 17.93
Cost per Net Conditioned Building Area ($/m2) | 14.52 | 3.68 | 0 | 18.2

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3488.22 | 869.1 | 882.34
Net Site Energy | 3488.22 | 869.1 | 882.34
Total Source Energy | 8397.07 | 2092.16 | 2124.02
Net Source Energy | 8397.07 | 2092.16 | 2124.02
Area [m2]
Total Building Area | 4013.59
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 60.2
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 37.61 | 685.77 | 0 | 0 | 0 | 0
Cooling | 289.88 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 628.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 37.67 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 815.05 | 189.47 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 249.52 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 551.92 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2061.06 | 1427.16 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 6.46 |  | 0
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 5.38 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.6 |  | 0
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 11.84 | 3.08 | 15.43
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 9.7 | 32.61 | 10.7631
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 14 | 1.87 | 12.9
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 16.16 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 12.9 | 2.96 | 77.16
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 6.46 | 8.89 | 206.12
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2157.2117
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 9.7 | 2.96 | 11.4999
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 11.84 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 6.46 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 8.6 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 11.8 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
Total | 4013.59 |  | 11621.74 |  | 1694.58 | 184.21 | 10.425 | 15.71 | 24.2519
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 10.5838 | 15.47 | 16.4088
Unconditioned Total | 60.2 |  | 174.32 |  | 21.18 | 0 | 0 |  | 539.3029
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_REARSTAIRSFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_CORRIDORFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.13 | 90 | 90 | E
W_CORRIDORFLR1_10_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.22 | 180 | 90 | S
S_CORRIDORFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 150.51 | 270 | 180
W_REARSTORAGEFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 163.06 | 90 | 180
W_RESTROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 80.27 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM101_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_EMPLOYEELOUNGEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_LAUNDRYROOMFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 97.83 | 90 | 180
W_ELEVATORCOREFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 15.05 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_FRONTSTORAGEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 12.54 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_CORRIDORFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.36 | 0 | 90 | N
W_CORRIDORFLR2_15_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 270 | 90 | W
W_REARSTORAGEFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 180 | 90 | S
W_GUESTROOM201_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
W_ELEVATORCOREFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_FRONTSTORAGEFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 4.18 | 0 | 90 | N
W_FRONTSTAIRSFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_REARSTAIRSFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_CORRIDORFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 270 | 90 | W
W_REARSTORAGEFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 180 | 90 | S
W_GUESTROOM301_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 4.18 | 0 | 90 | N
W_FRONTSTAIRSFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_REARSTAIRSFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
R_REARSTAIRSFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
W_CORRIDORFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 270 | 90 | W
R_CORRIDORFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 125.42 | 90 | 0
W_REARSTORAGEFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 180 | 90 | S
R_REARSTORAGEFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
W_GUESTROOM401_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
R_GUESTROOM401_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM402_405_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
R_GUESTROOM402_405_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.45 | 90 | 0
W_GUESTROOM406_408_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 35.12 | 180 | 90 | S
R_GUESTROOM406_408_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 105.36 | 90 | 0
W_GUESTROOM409_412_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
R_GUESTROOM409_412_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.45 | 90 | 0
W_GUESTROOM413_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
R_GUESTROOM413_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM414_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
R_GUESTROOM414_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM415_418_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
R_GUESTROOM415_418_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.44 | 90 | 0
W_ELEVATORCOREFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 0 | 90 | N
R_ELEVATORCOREFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 15.05 | 90 | 0
W_GUESTROOM419_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
R_GUESTROOM419_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM420_423_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
R_GUESTROOM420_423_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.44 | 90 | 0
W_GUESTROOM424_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
R_GUESTROOM424_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_FRONTSTORAGEFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 4.18 | 0 | 90 | N
R_FRONTSTORAGEFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12.54 | 90 | 0
W_FRONTSTAIRSFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
R_FRONTSTAIRSFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
W_CORRIDORFLR1_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_EAST | 2.69 | 2.69 | 3.18 | 0.501 | 0.622 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
D_CORRIDORFLR1_16_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_WEST | 4.44 | 4.44 | 3.18 | 0.501 | 0.622 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 2.69 | 2.69 | 3.18 | 0.501 | 0.622 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 2.97 | 2.97 | 3.18 | 0.501 | 0.622 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 2.97 | 2.97 | 3.18 | 0.501 | 0.622 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 2.97 | 2.97 | 3.18 | 0.501 | 0.622 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 2.97 | 2.97 | 3.18 | 0.501 | 0.622 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 2.96 | 2.96 | 3.18 | 0.501 | 0.622 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_GUESTROOM101_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_CORRIDORFLR2_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_EAST | 1.31 | 1.31 | 3.18 | 0.501 | 0.622 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_WEST | 1.31 | 1.31 | 3.18 | 0.501 | 0.622 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_GUESTROOM201_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 3.41 | 3.41 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_CORRIDORFLR3_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_EAST | 1.31 | 1.31 | 3.18 | 0.501 | 0.622 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_WEST | 1.31 | 1.31 | 3.18 | 0.501 | 0.622 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_GUESTROOM301_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 3.41 | 3.41 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_CORRIDORFLR4_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_EAST | 1.31 | 1.31 | 3.18 | 0.501 | 0.622 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_WEST | 1.31 | 1.31 | 3.18 | 0.501 | 0.622 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_GUESTROOM401_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 3.41 | 3.41 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_NORTH | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM424_3_0_0 | 0 | N
Total or Average |  |  | 184.21 | 3.18 | 0.501 | 0.622
North Total or Average |  |  | 72.38 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 111.83 | 3.18 | 0.501 | 0.622
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1839.95 | 1469.48 | 370.46 | 0.8 | 3.63
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1884.46 | 1505.03 | 379.43 | 0.8 | 3.62
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1944.27 | 1552.8 | 391.47 | 0.8 | 3.65
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1711.56 | 1366.95 | 344.61 | 0.8 | 3.61
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1839.24 | 1468.92 | 370.32 | 0.8 | 3.62
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2648.73 | 2115.42 | 533.31 | 0.8 | 3.47
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9398.42 | 7506.09 | 1892.32 | 0.8 | 2.99
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7689.29 | 6141.1 | 1548.2 | 0.8 | 2.98
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9100.08 | 7267.82 | 1832.25 | 0.8 | 2.99
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2527.4 | 2018.52 | 508.88 | 0.8 | 3.51
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2318.24 | 1851.48 | 466.77 | 0.8 | 3.55
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9011.42 | 7197.02 | 1814.4 | 0.8 | 2.98
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2819.58 | 2251.87 | 567.71 | 0.8 | 3.41
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8204.09 | 6552.24 | 1651.85 | 0.8 | 2.99
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2309.24 | 1844.29 | 464.95 | 0.8 | 3.56
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2623.53 | 2095.3 | 528.23 | 0.8 | 3.48
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9397.85 | 7505.65 | 1892.21 | 0.8 | 2.99
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7892.21 | 6303.16 | 1589.06 | 0.8 | 2.99
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9386.99 | 7496.97 | 1890.02 | 0.8 | 2.99
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2615.15 | 2088.61 | 526.55 | 0.8 | 3.5
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2411.7 | 1926.11 | 485.58 | 0.8 | 3.54
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8653.77 | 6911.38 | 1742.39 | 0.8 | 2.98
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2291.5 | 1830.12 | 461.38 | 0.8 | 3.57
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8509.5 | 6796.15 | 1713.34 | 0.8 | 2.98
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2379.89 | 1900.71 | 479.18 | 0.8 | 3.52
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3203.49 | 2558.48 | 645.01 | 0.8 | 3.31
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11405.97 | 9109.44 | 2296.53 | 0.8 | 2.98
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9508.95 | 7594.37 | 1914.58 | 0.8 | 2.99
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11416.93 | 9118.19 | 2298.74 | 0.8 | 2.98
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3177.05 | 2537.37 | 639.68 | 0.8 | 3.33
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3082.59 | 2461.93 | 620.66 | 0.8 | 3.35
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10986.55 | 8774.46 | 2212.08 | 0.8 | 2.98
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2868.92 | 2291.28 | 577.64 | 0.8 | 3.39
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10897.05 | 8702.99 | 2194.06 | 0.8 | 2.99
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3045.87 | 2432.6 | 613.27 | 0.8 | 3.34
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9572.52 | 7645.14 | 1927.38 | 0.8 | 4.07
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 15916.67 | 12711.93 | 3204.74 | 0.8 | 4.03
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1386.36 | 1107.23 | 279.14 | 0.8 | 4.01
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8344.15 | 6664.1 | 1680.05 | 0.8 | 4.06
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1473.75 | 1177.01 | 296.73 | 0.8 | 4.07
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6215.13 | 4963.74 | 1251.38 | 0.8 | 4.07
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 29472.7 | 23538.53 | 5934.17 | 0.8 | 3.74
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2418.35 | 1931.43 | 486.92 | 0.8 | 4.09
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6384.71 | 5099.18 | 1285.53 | 0.8 | 4.07
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5667.89 | 4526.69 | 1141.2 | 0.8 | 4.05
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5667.89 | 4526.69 | 1141.2 | 0.8 | 4.05
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6910.41 | 5519.03 | 1391.37 | 0.8 | 4.07
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 355.32 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 205.24 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 1065.4 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 1088.14 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1305.13 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 1304.27 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 1091.02 | 1
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 461.23 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 375.4 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 275.58 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 1500.43 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 3971.32 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 3061.03 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 3897.41 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1215.5 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1187.59 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 3612 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 835.88 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 3788.67 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 1115.65 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 493.66 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 407.43 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 309.6 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 1550.62 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 4120.57 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 3286.95 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 4106.11 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1264.82 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1242.75 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 4066.99 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 1005.41 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 4060.79 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1182.59 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 541.04 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 964.67 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 728.81 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 2322.13 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 7153.18 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 5756.85 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 7146.05 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 2049.52 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 2032.71 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 7151.16 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 1932.97 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 7118 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 2005.06 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 154.55 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1134.23 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 10098.84 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 16791.81 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1401.81 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 8802.94 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1554.78 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 5189.61 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 23620.3 | 0.8
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 2551.32 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 5893.54 | 0.78
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 5979.53 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 5979.53 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 7290.36 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 2.89 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 1.67 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 70.73 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 72.44 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.12 | 74.74 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.1 | 65.8 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 70.7 | 1 | PTAC Fan
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.02 | 3.75 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.02 | 3.05 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 2.24 | 1 | Unit Heater Fans
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.16 | 101.82 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.57 | 361.3 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.46 | 295.59 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.55 | 349.83 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.15 | 97.16 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 89.12 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.54 | 346.42 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.17 | 108.39 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.5 | 315.38 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 88.77 | 1 | PTAC Fan
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.02 | 4.01 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.02 | 3.31 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 2.52 | 1 | Unit Heater Fans
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.16 | 100.85 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.57 | 361.27 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.48 | 303.39 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.57 | 360.86 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.16 | 100.53 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.15 | 92.71 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.52 | 332.67 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 88.09 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.51 | 327.12 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 91.49 | 1 | PTAC Fan
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.02 | 4.4 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.04 | 7.84 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.03 | 5.93 | 1 | Unit Heater Fans
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.19 | 123.15 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.69 | 438.47 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.57 | 365.54 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.69 | 438.89 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.19 | 122.13 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.19 | 118.5 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.66 | 422.35 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.17 | 110.29 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.66 | 418.91 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.18 | 117.09 | 1 | PTAC Fan
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 1.26 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.05 | 9.22 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.58 | 670.75 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.96 | 1095.36 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.08 | 97.14 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.5 | 584.67 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 103.27 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.38 | 435.49 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.78 | 1947.14 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.15 | 169.45 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.39 | 447.38 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.42 | 484.21 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 54258.7872 | 86.5114 | 201.9031 | 0 | 0.0008 | 209893.1832 | 22433.8872
February | 47427.129 | 75.6959 | 176.8989 | 0 | 0.0007 | 183900.0612 | 19616.8238
March | 50789.1112 | 81.8592 | 193.7549 | 0 | 0.0008 | 201429.4367 | 21085.6287
April | 48021.6338 | 79.2012 | 192.9528 | 0 | 0.0008 | 200609.1908 | 20113.4772
May | 50372.237 | 84.4917 | 210.0495 | 0 | 0.0008 | 218394.5061 | 21236.682
June | 51283.7846 | 87.176 | 220.1035 | 0 | 0.0009 | 228856.034 | 21734.3066
July | 58068.8921 | 99.4326 | 253.1366 | 0 | 0.001 | 263207.5005 | 24680.7663
August | 56020.0551 | 95.854 | 243.8244 | 0 | 0.001 | 253524.4515 | 23803.0584
September | 50549.8579 | 85.8314 | 216.4284 | 0 | 0.0008 | 225034.1025 | 21413.7467
October | 49917.4632 | 83.1513 | 205.0269 | 0 | 0.0008 | 213168.4283 | 20988.2974
November | 48496.2672 | 78.317 | 185.8371 | 0 | 0.0007 | 193199.1963 | 20148.7574
December | 54095.0708 | 86.1104 | 200.5365 | 0 | 0.0008 | 208471.413 | 22352.4708
Annual Sum or Average | 619300.2891 | 1023.6321 | 2500.4526 | 0 | 0.0099 | 2599690 | 259607.9024
Minimum of Months | 47427.129 | 75.6959 | 176.8989 | 0 | 0.0007 | 183900.0612 | 19616.8238
Maximum of Months | 58068.8921 | 99.4326 | 253.1366 | 0 | 0.001 | 263207.5005 | 24680.7663
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 166406000000 | 118239.02 | 08-JAN-08:15 | 26344.714 | 58181.634 | 8082.455 | 25545.438 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 145798000000 | 107389.696 | 16-FEB-07:15 | 24319.757 | 51459.268 | 8018.825 | 23507.068 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 159696000000 | 102111.238 | 26-MAR-19:15 | 36441.661 | 38950.562 | 9024.152 | 0 | 15210.074 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 159045000000 | 106993.954 | 25-APR-19:15 | 36525.994 | 38968.112 | 9434.681 | 0 | 19580.379 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 173146000000 | 116018.024 | 23-MAY-19:15 | 36525.994 | 38968.112 | 9885.915 | 0 | 28153.214 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 181440000000 | 119230.408 | 27-JUN-19:30 | 36525.994 | 38968.112 | 10113.526 | 0 | 31137.987 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 208674000000 | 126718.792 | 02-JUL-07:00 | 26344.714 | 58181.634 | 9764.117 | 0 | 32343.548 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 200997000000 | 122961.971 | 29-AUG-19:15 | 36525.994 | 38968.112 | 10328.96 | 0 | 34654.116 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 178410000000 | 121009.575 | 02-SEP-07:00 | 26344.714 | 58181.634 | 9475.195 | 0 | 26923.253 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 169002000000 | 109305.696 | 01-OCT-07:00 | 26344.714 | 58181.634 | 8941.696 | 0 | 15752.874 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 153171000000 | 105024.115 | 12-NOV-08:00 | 26344.714 | 58181.634 | 8454.654 | 0 | 11958.335 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 165279000000 | 113456.753 | 12-DEC-07:15 | 24319.757 | 51459.268 | 8190.5 | 27002.44 | 0 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2061060000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 145798000000 | 102111.238 |  | 24319.757 | 38950.562 | 8018.825 | 0 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 208674000000 | 126718.792 |  | 36525.994 | 58181.634 | 10328.96 | 27002.44 | 34654.116 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 21334.39 | 10110.35 | 0 | 31444.74
Cost per Total Building Area ($/m2) | 5.32 | 2.52 | 0 | 7.83
Cost per Net Conditioned Building Area ($/m2) | 5.4 | 2.56 | 0 | 7.95

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 4110.79 | 1024.22 | 1039.82
Net Site Energy | 4110.79 | 1024.22 | 1039.82
Total Source Energy | 9623.05 | 2397.62 | 2434.13
Net Source Energy | 9623.05 | 2397.62 | 2434.13
Area [m2]
Total Building Area | 4013.59
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 60.2
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 164.04 | 1132.35 | 0 | 0 | 0 | 0
Cooling | 311.96 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 628.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 37.7 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 815.05 | 189.47 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 229.28 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 599.6 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2189.37 | 1921.43 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 6.46 |  | 0
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 5.38 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.6 |  | 0
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 11.84 | 3.08 | 15.43
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 9.7 | 32.61 | 10.7631
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 14 | 1.87 | 12.9
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 16.16 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 12.9 | 2.96 | 77.16
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 6.46 | 8.89 | 206.12
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2157.2117
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 9.7 | 2.96 | 11.4999
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 11.84 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 6.46 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 8.6 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 11.8 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
Total | 4013.59 |  | 11621.74 |  | 1694.58 | 184.21 | 10.425 | 15.71 | 24.2519
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 10.5838 | 15.47 | 16.4088
Unconditioned Total | 60.2 |  | 174.32 |  | 21.18 | 0 | 0 |  | 539.3029
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_REARSTAIRSFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_CORRIDORFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.13 | 90 | 90 | E
W_CORRIDORFLR1_10_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.22 | 180 | 90 | S
S_CORRIDORFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 150.51 | 270 | 180
W_REARSTORAGEFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 163.06 | 90 | 180
W_RESTROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 80.27 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM101_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_EMPLOYEELOUNGEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_LAUNDRYROOMFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 97.83 | 90 | 180
W_ELEVATORCOREFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 15.05 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_FRONTSTORAGEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 12.54 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_CORRIDORFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.36 | 0 | 90 | N
W_CORRIDORFLR2_15_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 270 | 90 | W
W_REARSTORAGEFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 180 | 90 | S
W_GUESTROOM201_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
W_ELEVATORCOREFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_FRONTSTORAGEFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 4.18 | 0 | 90 | N
W_FRONTSTAIRSFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_REARSTAIRSFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_CORRIDORFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 270 | 90 | W
W_REARSTORAGEFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 180 | 90 | S
W_GUESTROOM301_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 4.18 | 0 | 90 | N
W_FRONTSTAIRSFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_REARSTAIRSFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
R_REARSTAIRSFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
W_CORRIDORFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 270 | 90 | W
R_CORRIDORFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 125.42 | 90 | 0
W_REARSTORAGEFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 180 | 90 | S
R_REARSTORAGEFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
W_GUESTROOM401_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
R_GUESTROOM401_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM402_405_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
R_GUESTROOM402_405_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.45 | 90 | 0
W_GUESTROOM406_408_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 35.12 | 180 | 90 | S
R_GUESTROOM406_408_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 105.36 | 90 | 0
W_GUESTROOM409_412_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
R_GUESTROOM409_412_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.45 | 90 | 0
W_GUESTROOM413_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
R_GUESTROOM413_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM414_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
R_GUESTROOM414_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM415_418_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
R_GUESTROOM415_418_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.44 | 90 | 0
W_ELEVATORCOREFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 0 | 90 | N
R_ELEVATORCOREFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 15.05 | 90 | 0
W_GUESTROOM419_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
R_GUESTROOM419_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM420_423_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
R_GUESTROOM420_423_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.44 | 90 | 0
W_GUESTROOM424_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
R_GUESTROOM424_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_FRONTSTORAGEFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 4.18 | 0 | 90 | N
R_FRONTSTORAGEFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12.54 | 90 | 0
W_FRONTSTAIRSFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
R_FRONTSTAIRSFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
W_CORRIDORFLR1_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_EAST | 2.69 | 2.69 | 3.18 | 0.501 | 0.622 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
D_CORRIDORFLR1_16_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_WEST | 4.44 | 4.44 | 3.18 | 0.501 | 0.622 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 2.69 | 2.69 | 3.18 | 0.501 | 0.622 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 2.97 | 2.97 | 3.18 | 0.501 | 0.622 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 2.97 | 2.97 | 3.18 | 0.501 | 0.622 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 2.97 | 2.97 | 3.18 | 0.501 | 0.622 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 2.97 | 2.97 | 3.18 | 0.501 | 0.622 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 2.96 | 2.96 | 3.18 | 0.501 | 0.622 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_GUESTROOM101_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.65 | 1.65 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.65 | 1.65 | 3.18 | 0.651 | 0.813 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.65 | 1.65 | 3.18 | 0.651 | 0.813 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_CORRIDORFLR2_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_EAST | 1.31 | 1.31 | 3.18 | 0.501 | 0.622 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_WEST | 1.31 | 1.31 | 3.18 | 0.501 | 0.622 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_GUESTROOM201_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 3.41 | 3.41 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.65 | 1.65 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.65 | 1.65 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.65 | 1.65 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_CORRIDORFLR3_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_EAST | 1.31 | 1.31 | 3.18 | 0.501 | 0.622 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_WEST | 1.31 | 1.31 | 3.18 | 0.501 | 0.622 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_GUESTROOM301_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 3.41 | 3.41 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.65 | 1.65 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.65 | 1.65 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.65 | 1.65 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_CORRIDORFLR4_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_EAST | 1.31 | 1.31 | 3.18 | 0.501 | 0.622 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_WEST | 1.31 | 1.31 | 3.18 | 0.501 | 0.622 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_GUESTROOM401_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 3.41 | 3.41 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.65 | 1.65 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.65 | 1.65 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.65 | 1.65 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM424_3_0_0 | 0 | N
Total or Average |  |  | 184.21 | 3.18 | 0.56 | 0.697
North Total or Average |  |  | 72.38 | 3.18 | 0.651 | 0.813
Non-North Total or Average |  |  | 111.83 | 3.18 | 0.501 | 0.622
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1819.32 | 1419.71 | 399.61 | 0.78 | 3.58
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1854.38 | 1450.96 | 403.42 | 0.78 | 3.58
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1926.34 | 1514.03 | 412.31 | 0.79 | 3.6
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1618.44 | 1283.86 | 334.58 | 0.79 | 3.59
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1675.61 | 1335.72 | 339.89 | 0.8 | 3.62
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2339.26 | 1867.11 | 472.15 | 0.8 | 3.56
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8471.84 | 6754.68 | 1717.16 | 0.8 | 2.98
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6941.79 | 5544.1 | 1397.69 | 0.8 | 2.99
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8257.08 | 6562.23 | 1694.85 | 0.79 | 2.98
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2297.38 | 1834.82 | 462.57 | 0.8 | 3.59
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2070.95 | 1653.97 | 416.97 | 0.8 | 3.61
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7853.71 | 6272.41 | 1581.3 | 0.8 | 2.99
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2453.12 | 1959.2 | 493.92 | 0.8 | 3.54
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7179.16 | 5733.67 | 1445.49 | 0.8 | 2.99
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2044.19 | 1632.6 | 411.59 | 0.8 | 3.62
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2313.1 | 1843.7 | 469.4 | 0.8 | 3.58
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8453.19 | 6737.97 | 1715.22 | 0.8 | 2.98
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7115.88 | 5683.13 | 1432.74 | 0.8 | 2.99
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8445.11 | 6730.72 | 1714.38 | 0.8 | 2.98
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2370.63 | 1893.31 | 477.31 | 0.8 | 3.55
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2150.35 | 1717.39 | 432.96 | 0.8 | 3.62
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7551.58 | 6031.11 | 1520.47 | 0.8 | 2.99
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2001.15 | 1598.23 | 402.92 | 0.8 | 3.63
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7427.49 | 5932 | 1495.49 | 0.8 | 2.98
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2105.12 | 1681.26 | 423.85 | 0.8 | 3.64
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2779.7 | 2220.02 | 559.68 | 0.8 | 3.45
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10180.31 | 8130.56 | 2049.75 | 0.8 | 2.98
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8551.61 | 6829.79 | 1721.82 | 0.8 | 2.98
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10190.64 | 8138.81 | 2051.83 | 0.8 | 2.98
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2863 | 2286.55 | 576.45 | 0.8 | 3.41
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2701.47 | 2157.54 | 543.93 | 0.8 | 3.45
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9479.88 | 7571.16 | 1908.72 | 0.8 | 2.99
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2478.06 | 1979.11 | 498.94 | 0.8 | 3.52
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9401.33 | 7508.42 | 1892.91 | 0.8 | 2.98
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2660.69 | 2124.97 | 535.72 | 0.8 | 3.47
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13105.55 | 8860.44 | 4245.11 | 0.68 | 3.66
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 21927.94 | 14825.11 | 7102.83 | 0.68 | 3.45
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1673.17 | 1197.71 | 475.46 | 0.72 | 3.81
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11273.44 | 7621.78 | 3651.66 | 0.68 | 3.67
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2210.8 | 1494.69 | 716.12 | 0.68 | 3.67
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6319.69 | 4703.33 | 1616.36 | 0.74 | 3.85
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 25379.43 | 20269.41 | 5110.01 | 0.8 | 3.74
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3316.62 | 2242.31 | 1074.31 | 0.68 | 3.65
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7069.85 | 5198.87 | 1870.98 | 0.74 | 3.84
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8502.54 | 5748.42 | 2754.11 | 0.68 | 3.66
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8502.54 | 5748.42 | 2754.11 | 0.68 | 3.66
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9031.85 | 6106.28 | 2925.57 | 0.68 | 3.66
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 680.87 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 405.7 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 1403.93 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 1428.03 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1653.16 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 1648.27 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 1429.78 | 1
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 797.14 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 652.57 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 454.07 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 1979.24 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 5314.7 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 4116.86 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 5228.88 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1557.07 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1527.28 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 4949 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 1112.62 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 5115.71 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 1461.8 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 784.4 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 686.13 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 490.88 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 2035.28 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 5479.33 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 4356.34 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 5460.67 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1611.1 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1588.23 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 5416.31 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 1360.56 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 5405.8 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1533.39 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 831.94 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1431.85 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1025.05 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 3001.08 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 9291.88 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 7457.63 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 9281.43 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 2593.86 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 2576.15 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 9282.36 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 2505.96 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 9244.85 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 2543.78 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 264.37 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1606.43 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 12268.09 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 20526.71 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1820.29 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 10553.05 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 2069.53 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 6473.97 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 17416.1 | 0.8
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 3104.68 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 7569.36 | 0.78
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 7959.21 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 7959.21 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 8454.71 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.02 | 4.68 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 2.79 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.1 | 66.46 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 68.14 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 71.5 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.1 | 61.3 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.1 | 64.15 | 1 | PTAC Fan
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.03 | 5.48 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.02 | 4.49 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.02 | 3.12 | 1 | Unit Heater Fans
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 89.81 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.51 | 324.48 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.42 | 266.86 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.49 | 314.04 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 88.32 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.13 | 79.61 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.47 | 301.91 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.15 | 94.3 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.43 | 275.98 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.12 | 78.58 | 1 | PTAC Fan
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.03 | 5.4 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.02 | 4.72 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.02 | 3.38 | 1 | Unit Heater Fans
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 88.54 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.51 | 323.58 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.43 | 273.55 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.51 | 323.18 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 91.13 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.13 | 82.66 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.46 | 290.3 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.12 | 76.93 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.45 | 285.53 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.13 | 80.93 | 1 | PTAC Fan
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.03 | 5.72 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.05 | 9.85 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.04 | 7.05 | 1 | Unit Heater Fans
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.17 | 106.86 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.61 | 391.35 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.52 | 328.74 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.62 | 391.75 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.17 | 110.06 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.16 | 103.85 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.57 | 364.43 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.15 | 95.26 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.57 | 361.41 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.16 | 102.28 | 1 | PTAC Fan
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 1.82 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.06 | 11.05 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.53 | 612.15 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.88 | 1005.95 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.08 | 90.83 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.45 | 526.58 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 103.27 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.33 | 377.27 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.53 | 1676.72 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.13 | 154.92 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.35 | 410.1 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.36 | 421.87 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 63837.5453 | 101.5681 | 142.3361 | 0 | 0.0011 | 93508.9265 | 26264.0094
February | 50751.403 | 79.859 | 110.2652 | 0 | 0.0008 | 72435.2644 | 20795.1823
March | 47190.8176 | 75.1514 | 105.4437 | 0 | 0.0008 | 69272.4965 | 19421.8023
April | 41511.8615 | 69.0282 | 102.2644 | 0 | 0.0008 | 67198.2263 | 17363.7437
May | 44610.6265 | 77.179 | 119.6603 | 0 | 0.0009 | 78642.576 | 18946.4812
June | 46357.3636 | 81.5973 | 128.8922 | 0 | 0.0009 | 84715.6375 | 19821.8007
July | 50195.0662 | 88.7787 | 140.9511 | 0 | 0.001 | 92643.1294 | 21503.5121
August | 49196.5978 | 87.0469 | 138.2586 | 0 | 0.001 | 90873.5532 | 21079.0353
September | 41962.6879 | 73.359 | 115.0357 | 0 | 0.0008 | 75606.3034 | 17894.6234
October | 42364.5185 | 71.0315 | 106.2713 | 0 | 0.0008 | 69833.7947 | 17776.3595
November | 45116.0361 | 72.1526 | 101.8021 | 0 | 0.0008 | 66881.6006 | 18597.0957
December | 56920.6186 | 89.8777 | 124.6822 | 0 | 0.0009 | 81907.6717 | 23352.7448
Annual Sum or Average | 580015.1425 | 966.6295 | 1435.8627 | 0 | 0.0107 | 943519.1802 | 242816.3904
Minimum of Months | 41511.8615 | 69.0282 | 101.8021 | 0 | 0.0008 | 66881.6006 | 17363.7437
Maximum of Months | 63837.5453 | 101.5681 | 142.3361 | 0 | 0.0011 | 93508.9265 | 26264.0094
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 216980000000 | 152790.438 | 07-JAN-06:15 | 18512.215 | 25779.061 | 10400.524 | 95613.85 | 0 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 168081000000 | 141310.657 | 04-FEB-08:15 | 26344.714 | 58181.634 | 7974.255 | 48725.275 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 160742000000 | 101718.17 | 04-MAR-08:15 | 26344.714 | 58181.634 | 6568.091 | 10418.227 | 120.726 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 155928000000 | 109317.795 | 02-APR-07:00 | 26344.714 | 58181.634 | 8018.843 | 0 | 16687.826 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 182484000000 | 134031.283 | 27-MAY-19:45 | 36357.328 | 38915.462 | 9976.817 | 0 | 46296.887 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 196576000000 | 136225.016 | 29-JUN-19:15 | 36525.994 | 38968.112 | 10245.324 | 0 | 50400.808 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 214971000000 | 140927.912 | 16-JUL-07:00 | 26344.714 | 58181.634 | 9619.34 | 0 | 46697.446 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 210865000000 | 140304.246 | 25-AUG-19:15 | 36525.994 | 38968.112 | 10195.866 | 0 | 52129.485 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 175439000000 | 118307.86 | 03-SEP-07:00 | 26344.714 | 58181.634 | 8660.019 | 0 | 25036.715 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 162044000000 | 112171.066 | 08-OCT-07:00 | 26344.714 | 58181.634 | 8322.276 | 0 | 19237.663 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 155194000000 | 101325.493 | 05-NOV-08:00 | 26344.714 | 58181.634 | 7242.71 | 0 | 9471.657 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 190061000000 | 156626.594 | 31-DEC-06:15 | 18512.215 | 25779.061 | 10506.235 | 99344.295 | 0 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2189370000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 155194000000 | 101325.493 |  | 18512.215 | 25779.061 | 6568.091 | 0 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 216980000000 | 156626.594 |  | 36525.994 | 58181.634 | 10506.235 | 99344.295 | 52129.485 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 33846.28 | 15185.8 | 0 | 49032.08
Cost per Total Building Area ($/m2) | 8.43 | 3.78 | 0 | 12.22
Cost per Net Conditioned Building Area ($/m2) | 8.56 | 3.84 | 0 | 12.4

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3824.65 | 952.93 | 967.44
Net Site Energy | 3824.65 | 952.93 | 967.44
Total Source Energy | 9048.44 | 2254.45 | 2288.78
Net Source Energy | 9048.44 | 2254.45 | 2288.78
Area [m2]
Total Building Area | 4013.59
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 60.2
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 101.06 | 983.8 | 0 | 0 | 0 | 0
Cooling | 220.87 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 628.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 37.65 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 815.05 | 189.47 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 237.63 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 607.78 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2043.59 | 1781.06 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 6.46 |  | 0
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 5.38 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.6 |  | 0
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 11.84 | 3.08 | 15.43
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 9.7 | 32.61 | 10.7631
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 14 | 1.87 | 12.9
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 16.16 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 12.9 | 2.96 | 77.16
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 6.46 | 8.89 | 206.12
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2157.2117
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 9.7 | 2.96 | 11.4999
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 11.84 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 6.46 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 8.6 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 11.8 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
Total | 4013.59 |  | 11621.74 |  | 1694.58 | 184.21 | 10.425 | 15.71 | 24.2519
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 10.5838 | 15.47 | 16.4088
Unconditioned Total | 60.2 |  | 174.32 |  | 21.18 | 0 | 0 |  | 539.3029
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_REARSTAIRSFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_CORRIDORFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.13 | 90 | 90 | E
W_CORRIDORFLR1_10_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.22 | 180 | 90 | S
S_CORRIDORFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 150.51 | 270 | 180
W_REARSTORAGEFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 163.06 | 90 | 180
W_RESTROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 80.27 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM101_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_EMPLOYEELOUNGEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_LAUNDRYROOMFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 97.83 | 90 | 180
W_ELEVATORCOREFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 15.05 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_FRONTSTORAGEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 12.54 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_CORRIDORFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.36 | 0 | 90 | N
W_CORRIDORFLR2_15_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 270 | 90 | W
W_REARSTORAGEFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 180 | 90 | S
W_GUESTROOM201_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
W_ELEVATORCOREFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_FRONTSTORAGEFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 4.18 | 0 | 90 | N
W_FRONTSTAIRSFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_REARSTAIRSFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_CORRIDORFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 270 | 90 | W
W_REARSTORAGEFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 180 | 90 | S
W_GUESTROOM301_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 4.18 | 0 | 90 | N
W_FRONTSTAIRSFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_REARSTAIRSFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
R_REARSTAIRSFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
W_CORRIDORFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 270 | 90 | W
R_CORRIDORFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 125.42 | 90 | 0
W_REARSTORAGEFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 180 | 90 | S
R_REARSTORAGEFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
W_GUESTROOM401_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
R_GUESTROOM401_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM402_405_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
R_GUESTROOM402_405_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.45 | 90 | 0
W_GUESTROOM406_408_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 35.12 | 180 | 90 | S
R_GUESTROOM406_408_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 105.36 | 90 | 0
W_GUESTROOM409_412_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
R_GUESTROOM409_412_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.45 | 90 | 0
W_GUESTROOM413_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
R_GUESTROOM413_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM414_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
R_GUESTROOM414_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM415_418_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
R_GUESTROOM415_418_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.44 | 90 | 0
W_ELEVATORCOREFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 0 | 90 | N
R_ELEVATORCOREFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 15.05 | 90 | 0
W_GUESTROOM419_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
R_GUESTROOM419_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM420_423_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
R_GUESTROOM420_423_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.44 | 90 | 0
W_GUESTROOM424_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
R_GUESTROOM424_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_FRONTSTORAGEFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 4.18 | 0 | 90 | N
R_FRONTSTORAGEFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12.54 | 90 | 0
W_FRONTSTAIRSFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
R_FRONTSTAIRSFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
W_CORRIDORFLR1_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_EAST | 2.69 | 2.69 | 3.18 | 0.501 | 0.622 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
D_CORRIDORFLR1_16_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_WEST | 4.44 | 4.44 | 3.18 | 0.501 | 0.622 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 2.69 | 2.69 | 3.18 | 0.501 | 0.622 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 2.97 | 2.97 | 3.18 | 0.501 | 0.622 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 2.97 | 2.97 | 3.18 | 0.501 | 0.622 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 2.97 | 2.97 | 3.18 | 0.501 | 0.622 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 2.97 | 2.97 | 3.18 | 0.501 | 0.622 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 2.96 | 2.96 | 3.18 | 0.501 | 0.622 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_GUESTROOM101_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.65 | 1.65 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.65 | 1.65 | 3.18 | 0.651 | 0.813 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.65 | 1.65 | 3.18 | 0.651 | 0.813 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_CORRIDORFLR2_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_EAST | 1.31 | 1.31 | 3.18 | 0.501 | 0.622 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_WEST | 1.31 | 1.31 | 3.18 | 0.501 | 0.622 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_GUESTROOM201_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 3.41 | 3.41 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.65 | 1.65 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.65 | 1.65 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.65 | 1.65 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_CORRIDORFLR3_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_EAST | 1.31 | 1.31 | 3.18 | 0.501 | 0.622 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_WEST | 1.31 | 1.31 | 3.18 | 0.501 | 0.622 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_GUESTROOM301_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 3.41 | 3.41 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.65 | 1.65 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.65 | 1.65 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.65 | 1.65 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_CORRIDORFLR4_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_EAST | 1.31 | 1.31 | 3.18 | 0.501 | 0.622 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622_WEST | 1.31 | 1.31 | 3.18 | 0.501 | 0.622 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_GUESTROOM401_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 3.41 | 3.41 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.64 | 1.64 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 1.65 | 1.65 | 3.18 | 0.501 | 0.622 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.65 | 1.65 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.65 | 1.65 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.65 | 1.65 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.813 | 1.64 | 1.64 | 3.18 | 0.651 | 0.813 | No | W_GUESTROOM424_3_0_0 | 0 | N
Total or Average |  |  | 184.21 | 3.18 | 0.56 | 0.697
North Total or Average |  |  | 72.38 | 3.18 | 0.651 | 0.813
Non-North Total or Average |  |  | 111.83 | 3.18 | 0.501 | 0.622
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1829.77 | 1461.35 | 368.41 | 0.8 | 3.64
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1876.47 | 1498.66 | 377.82 | 0.8 | 3.62
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1927.81 | 1539.65 | 388.15 | 0.8 | 3.61
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1615.22 | 1290.01 | 325.22 | 0.8 | 3.65
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1742.96 | 1392.02 | 350.94 | 0.8 | 3.61
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2576.27 | 2057.55 | 518.72 | 0.8 | 3.49
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9388.4 | 7498.09 | 1890.3 | 0.8 | 2.98
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7732.58 | 6175.66 | 1556.91 | 0.8 | 2.98
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9085.53 | 7256.2 | 1829.32 | 0.8 | 2.98
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2513.37 | 2007.32 | 506.05 | 0.8 | 3.52
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2228.58 | 1779.86 | 448.71 | 0.8 | 3.58
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8620.31 | 6884.66 | 1735.65 | 0.8 | 2.98
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2703.66 | 2159.3 | 544.37 | 0.8 | 3.45
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7854.09 | 6272.71 | 1581.38 | 0.8 | 2.99
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2208.24 | 1763.63 | 444.62 | 0.8 | 3.59
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2542.23 | 2030.37 | 511.87 | 0.8 | 3.5
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9380.1 | 7491.46 | 1888.63 | 0.8 | 2.98
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7938.88 | 6340.43 | 1598.45 | 0.8 | 2.98
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9368.33 | 7482.06 | 1886.26 | 0.8 | 2.98
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2599.22 | 2075.88 | 523.34 | 0.8 | 3.48
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2320.57 | 1853.34 | 467.24 | 0.8 | 3.57
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8293.76 | 6623.85 | 1669.9 | 0.8 | 2.98
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2195.43 | 1753.39 | 442.04 | 0.8 | 3.59
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8153.97 | 6512.21 | 1641.76 | 0.8 | 2.98
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2277.07 | 1818.59 | 458.48 | 0.8 | 3.59
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3065.53 | 2448.3 | 617.23 | 0.8 | 3.35
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11272.16 | 9002.57 | 2269.59 | 0.8 | 2.99
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9473.9 | 7566.38 | 1907.52 | 0.8 | 2.99
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11282.46 | 9010.79 | 2271.66 | 0.8 | 2.99
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3125.29 | 2496.03 | 629.26 | 0.8 | 3.35
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2909.1 | 2323.37 | 585.73 | 0.8 | 3.39
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10351.59 | 8267.35 | 2084.24 | 0.8 | 2.99
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2701.44 | 2157.52 | 543.92 | 0.8 | 3.45
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10264.87 | 8198.1 | 2066.78 | 0.8 | 2.98
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2867.17 | 2289.88 | 577.29 | 0.8 | 3.41
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9177.64 | 7329.77 | 1847.87 | 0.8 | 4.06
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 15816.01 | 12631.54 | 3184.47 | 0.8 | 4.03
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1353.37 | 1080.87 | 272.49 | 0.8 | 4.04
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8165.62 | 6521.52 | 1644.1 | 0.8 | 4.05
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1473.75 | 1177.01 | 296.73 | 0.8 | 4.07
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5896.69 | 4709.42 | 1187.27 | 0.8 | 4.04
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 27842.11 | 22236.25 | 5605.86 | 0.8 | 3.74
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2360.83 | 1885.49 | 475.34 | 0.8 | 4.05
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6017.5 | 4805.91 | 1211.59 | 0.8 | 4.07
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5667.89 | 4526.69 | 1141.2 | 0.8 | 4.05
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5667.89 | 4526.69 | 1141.2 | 0.8 | 4.05
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6511.67 | 5200.58 | 1311.09 | 0.8 | 4.05
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 652.08 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 404.33 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 1347.29 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 1371.51 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1598.79 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 1593.86 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 1373.64 | 1
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 766.54 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 621.65 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 447.22 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 1899.59 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 5036.13 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 3903.63 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 4948.62 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1488.78 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1458.99 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 4667.59 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 1013.87 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 4834.82 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 1392.79 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 755.6 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 656.64 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 484.82 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 1956.45 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 5203.1 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 4144.32 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 5183.69 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1543.46 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1519.91 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 5135.39 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 1290.73 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 5124.61 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1464.24 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 804.02 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1396.42 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1028.07 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 2933.38 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 9050.72 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 7273.78 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 9039.7 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 2536.76 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 2517.8 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 9035.5 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 2447.93 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 8997.53 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 2484.15 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 271.01 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1573.32 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 11743.94 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 20238.56 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1683.81 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 10448.93 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1885.84 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 6076.75 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 16630.32 | 0.8
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 3020.98 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 6952.45 | 0.78
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 7252.77 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 7252.77 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 8332.5 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.03 | 5.02 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.02 | 3.11 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 70.34 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 72.14 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.12 | 74.11 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.1 | 62.09 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 67 | 1 | PTAC Fan
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.03 | 5.9 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.02 | 4.79 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.02 | 3.44 | 1 | Unit Heater Fans
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.16 | 99.04 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.57 | 360.91 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.47 | 297.26 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.55 | 349.27 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.15 | 96.62 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.13 | 85.67 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.52 | 331.38 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.16 | 103.93 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.47 | 301.93 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.13 | 84.89 | 1 | PTAC Fan
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.03 | 5.82 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.03 | 5.05 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.02 | 3.73 | 1 | Unit Heater Fans
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.15 | 97.73 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.57 | 360.59 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.48 | 305.19 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.57 | 360.14 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.16 | 99.92 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 89.21 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.5 | 318.83 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.13 | 84.4 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.49 | 313.46 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 87.54 | 1 | PTAC Fan
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.03 | 6.19 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.05 | 10.75 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.04 | 7.91 | 1 | Unit Heater Fans
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.19 | 117.85 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.68 | 433.33 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.57 | 364.2 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.68 | 433.72 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.19 | 120.14 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.18 | 111.83 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.63 | 397.94 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.16 | 103.85 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.62 | 394.6 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.17 | 110.22 | 1 | PTAC Fan
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 2.09 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.06 | 12.11 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.55 | 643.08 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.96 | 1088.44 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.08 | 94.83 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.49 | 572.16 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 103.27 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.36 | 413.18 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.68 | 1839.42 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.14 | 165.42 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.36 | 421.65 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.39 | 456.27 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 58213.8629 | 91.3835 | 139.6536 | 0 | 0.001 | 3311370 | 23873.5617
February | 48334.5396 | 75.8467 | 115.8508 | 0 | 0.0008 | 2746970 | 19819.3013
March | 47871.4749 | 76.3501 | 119.1893 | 0 | 0.0008 | 2826350 | 19748.3234
April | 43594.1152 | 70.5505 | 112.2371 | 0 | 0.0008 | 2661680 | 18082.6202
May | 44619.0767 | 74.3079 | 122.4657 | 0 | 0.0009 | 2904610 | 18710.632
June | 45497.3621 | 77.2929 | 130.3818 | 0 | 0.0009 | 3092600 | 19226.088
July | 49769.3128 | 85.5197 | 146.1299 | 0 | 0.001 | 3466290 | 21125.0185
August | 48157.5153 | 82.6188 | 140.9226 | 0 | 0.001 | 3342750 | 20428.1854
September | 44027.6762 | 74.6362 | 125.5919 | 0 | 0.0009 | 2978960 | 18589.5788
October | 44333.5138 | 72.9597 | 118.526 | 0 | 0.0008 | 2811030 | 18506.5307
November | 45384.0779 | 72.0539 | 111.8063 | 0 | 0.0008 | 2651220 | 18690.3963
December | 55482.3998 | 87.1932 | 133.4536 | 0 | 0.001 | 3164380 | 22762.8141
Annual Sum or Average | 575284.9273 | 940.7129 | 1516.2085 | 0 | 0.0107 | 35958200 | 239563.0505
Minimum of Months | 43594.1152 | 70.5505 | 111.8063 | 0 | 0.0008 | 2651220 | 18082.6202
Maximum of Months | 58213.8629 | 91.3835 | 146.1299 | 0 | 0.001 | 3466290 | 23873.5617
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 188193000000 | 149289.884 | 07-JAN-08:15 | 26344.714 | 58181.634 | 8949.036 | 53329.711 | 0 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 156117000000 | 129498.076 | 26-FEB-08:15 | 26344.714 | 58181.634 | 8057.61 | 36829.34 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 160628000000 | 111802.134 | 04-MAR-08:15 | 26344.714 | 58181.634 | 7365.908 | 19825.099 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 151269000000 | 101755.019 | 30-APR-07:00 | 26344.714 | 58181.634 | 7843.053 | 0 | 9300.839 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 165076000000 | 106376.793 | 25-MAY-19:00 | 36525.994 | 38968.112 | 9210.521 | 0 | 19187.377 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 175760000000 | 127262.86 | 25-JUN-19:15 | 36441.661 | 38950.562 | 10503.071 | 0 | 41282.787 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 196998000000 | 124971.609 | 21-JUL-19:15 | 36525.994 | 38968.112 | 10307.115 | 0 | 39085.609 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 189976000000 | 120667.442 | 11-AUG-19:45 | 36525.994 | 38968.112 | 9903.785 | 0 | 32784.763 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 169302000000 | 117026.542 | 02-SEP-19:15 | 36357.328 | 38915.462 | 9692.095 | 0 | 29576.868 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 159757000000 | 103552.673 | 08-OCT-07:00 | 26344.714 | 58181.634 | 8070.266 | 0 | 10871.28 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 150675000000 | 99204.518 | 05-NOV-08:00 | 26344.714 | 58181.634 | 7369.181 | 733.404 | 6490.807 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 179839000000 | 142551.463 | 11-DEC-08:30 | 23685.52 | 40817.003 | 9745.631 | 68218.531 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2043590000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 150675000000 | 99204.518 |  | 23685.52 | 38915.462 | 7365.908 | 0 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 196998000000 | 149289.884 |  | 36525.994 | 58181.634 | 10503.071 | 68218.531 | 41282.787 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 40804.41 | 15090.54 | 0 | 55894.95
Cost per Total Building Area ($/m2) | 10.17 | 3.76 | 0 | 13.93
Cost per Net Conditioned Building Area ($/m2) | 10.32 | 3.82 | 0 | 14.14

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 4391.71 | 1094.21 | 1110.87
Net Site Energy | 4391.71 | 1094.21 | 1110.87
Total Source Energy | 9792.86 | 2439.93 | 2477.08
Net Source Energy | 9792.86 | 2439.93 | 2477.08
Area [m2]
Total Building Area | 4013.59
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 60.2
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 235.41 | 1397.49 | 0 | 0 | 0 | 0
Cooling | 195.66 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 628.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 37.64 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 815.05 | 189.47 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 215.87 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 673.78 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2130.96 | 2260.74 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 6.46 |  | 0
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 5.38 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.6 |  | 0
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 11.84 | 3.08 | 15.43
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 9.7 | 32.61 | 10.7631
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 14 | 1.87 | 12.9
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 16.16 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 12.9 | 2.96 | 77.16
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 6.46 | 8.89 | 206.12
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2157.2117
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 9.7 | 2.96 | 11.4999
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 11.84 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 6.46 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 8.6 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 11.8 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
Total | 4013.59 |  | 11621.74 |  | 1694.58 | 184.21 | 10.425 | 15.71 | 24.2519
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 10.5838 | 15.47 | 16.4088
Unconditioned Total | 60.2 |  | 174.32 |  | 21.18 | 0 | 0 |  | 539.3029
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_REARSTAIRSFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_CORRIDORFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.13 | 90 | 90 | E
W_CORRIDORFLR1_10_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.22 | 180 | 90 | S
S_CORRIDORFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 150.51 | 270 | 180
W_REARSTORAGEFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 163.06 | 90 | 180
W_RESTROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 80.27 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM101_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_EMPLOYEELOUNGEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_LAUNDRYROOMFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 97.83 | 90 | 180
W_ELEVATORCOREFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 15.05 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_FRONTSTORAGEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 12.54 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_CORRIDORFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.36 | 0 | 90 | N
W_CORRIDORFLR2_15_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 270 | 90 | W
W_REARSTORAGEFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 180 | 90 | S
W_GUESTROOM201_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
W_ELEVATORCOREFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_FRONTSTORAGEFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 4.18 | 0 | 90 | N
W_FRONTSTAIRSFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_REARSTAIRSFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_CORRIDORFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 270 | 90 | W
W_REARSTORAGEFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 180 | 90 | S
W_GUESTROOM301_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 4.18 | 0 | 90 | N
W_FRONTSTAIRSFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_REARSTAIRSFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
R_REARSTAIRSFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
W_CORRIDORFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 270 | 90 | W
R_CORRIDORFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 125.42 | 90 | 0
W_REARSTORAGEFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 180 | 90 | S
R_REARSTORAGEFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
W_GUESTROOM401_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
R_GUESTROOM401_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM402_405_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
R_GUESTROOM402_405_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.45 | 90 | 0
W_GUESTROOM406_408_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 35.12 | 180 | 90 | S
R_GUESTROOM406_408_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 105.36 | 90 | 0
W_GUESTROOM409_412_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 180 | 90 | S
R_GUESTROOM409_412_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.45 | 90 | 0
W_GUESTROOM413_5_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 180 | 90 | S
R_GUESTROOM413_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM414_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
R_GUESTROOM414_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM415_418_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
R_GUESTROOM415_418_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.44 | 90 | 0
W_ELEVATORCOREFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 5.02 | 0 | 90 | N
R_ELEVATORCOREFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 15.05 | 90 | 0
W_GUESTROOM419_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
R_GUESTROOM419_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_GUESTROOM420_423_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 43.48 | 0 | 90 | N
R_GUESTROOM420_423_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 130.44 | 90 | 0
W_GUESTROOM424_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 10.87 | 0 | 90 | N
R_GUESTROOM424_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 32.61 | 90 | 0
W_FRONTSTORAGEFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 4.18 | 0 | 90 | N
R_FRONTSTORAGEFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12.54 | 90 | 0
W_FRONTSTAIRSFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 22.58 | 270 | 90 | W
R_FRONTSTAIRSFLR4_1_0_0 | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 20.07 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
W_CORRIDORFLR1_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 2.69 | 2.69 | 3.18 | 0.501 | 0.49 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
D_CORRIDORFLR1_16_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 4.44 | 4.44 | 3.18 | 0.501 | 0.49 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 2.69 | 2.69 | 3.18 | 0.501 | 0.49 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 2.97 | 2.97 | 3.18 | 0.501 | 0.49 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 2.97 | 2.97 | 3.18 | 0.501 | 0.49 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 2.97 | 2.97 | 3.18 | 0.501 | 0.49 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 2.97 | 2.97 | 3.18 | 0.501 | 0.49 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 2.96 | 2.96 | 3.18 | 0.501 | 0.49 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 3.18 | 0.501 | 0.49 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 3.18 | 0.501 | 0.49 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.65 | 1.65 | 3.18 | 0.501 | 0.49 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_GUESTROOM101_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.65 | 1.65 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.65 | 1.65 | 3.18 | 0.651 | 0.64 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 3.18 | 0.651 | 0.64 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 3.18 | 0.651 | 0.64 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 3.18 | 0.651 | 0.64 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 3.18 | 0.651 | 0.64 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.65 | 1.65 | 3.18 | 0.651 | 0.64 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.65 | 1.65 | 3.18 | 0.651 | 0.64 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 3.18 | 0.651 | 0.64 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 3.18 | 0.651 | 0.64 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 3.18 | 0.651 | 0.64 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 3.18 | 0.651 | 0.64 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_CORRIDORFLR2_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 1.31 | 1.31 | 3.18 | 0.501 | 0.49 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 1.31 | 1.31 | 3.18 | 0.501 | 0.49 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_GUESTROOM201_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.65 | 1.65 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 3.41 | 3.41 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.65 | 1.65 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.65 | 1.65 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.65 | 1.65 | 3.18 | 0.651 | 0.64 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 3.18 | 0.651 | 0.64 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 3.18 | 0.651 | 0.64 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 3.18 | 0.651 | 0.64 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 3.18 | 0.651 | 0.64 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.65 | 1.65 | 3.18 | 0.651 | 0.64 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.65 | 1.65 | 3.18 | 0.651 | 0.64 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 3.18 | 0.651 | 0.64 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 3.18 | 0.651 | 0.64 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 3.18 | 0.651 | 0.64 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 3.18 | 0.651 | 0.64 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_CORRIDORFLR3_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 1.31 | 1.31 | 3.18 | 0.501 | 0.49 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 1.31 | 1.31 | 3.18 | 0.501 | 0.49 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_GUESTROOM301_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.65 | 1.65 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 3.41 | 3.41 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.65 | 1.65 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.65 | 1.65 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.65 | 1.65 | 3.18 | 0.651 | 0.64 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 3.18 | 0.651 | 0.64 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 3.18 | 0.651 | 0.64 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 3.18 | 0.651 | 0.64 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 3.18 | 0.651 | 0.64 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.65 | 1.65 | 3.18 | 0.651 | 0.64 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.65 | 1.65 | 3.18 | 0.651 | 0.64 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 3.18 | 0.651 | 0.64 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 3.18 | 0.651 | 0.64 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 3.18 | 0.651 | 0.64 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 3.18 | 0.651 | 0.64 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_CORRIDORFLR4_2_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 1.31 | 1.31 | 3.18 | 0.501 | 0.49 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 1.31 | 1.31 | 3.18 | 0.501 | 0.49 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_GUESTROOM401_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.65 | 1.65 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.65 | 1.65 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 3.41 | 3.41 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1.65 | 1.65 | 3.18 | 0.501 | 0.49 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.65 | 1.65 | 3.18 | 0.651 | 0.64 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 3.18 | 0.651 | 0.64 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 3.18 | 0.651 | 0.64 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 3.18 | 0.651 | 0.64 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 3.18 | 0.651 | 0.64 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.65 | 1.65 | 3.18 | 0.651 | 0.64 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.65 | 1.65 | 3.18 | 0.651 | 0.64 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 3.18 | 0.651 | 0.64 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 3.18 | 0.651 | 0.64 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 3.18 | 0.651 | 0.64 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 3.18 | 0.651 | 0.64 | No | W_GUESTROOM424_3_0_0 | 0 | N
Total or Average |  |  | 184.21 | 3.18 | 0.56 | 0.549
North Total or Average |  |  | 72.38 | 3.18 | 0.651 | 0.64
Non-North Total or Average |  |  | 111.83 | 3.18 | 0.501 | 0.49
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1598.7 | 1276.81 | 321.89 | 0.8 | 3.64
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1640.24 | 1309.99 | 330.25 | 0.8 | 3.63
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1674.04 | 1336.98 | 337.06 | 0.8 | 3.62
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1379.12 | 1101.44 | 277.68 | 0.8 | 3.6
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1516.79 | 1211.39 | 305.4 | 0.8 | 3.61
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2278.58 | 1819.8 | 458.78 | 0.8 | 3.57
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8437.05 | 6738.3 | 1698.76 | 0.8 | 2.99
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6944.42 | 5546.19 | 1398.22 | 0.8 | 2.99
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8163.6 | 6519.9 | 1643.7 | 0.8 | 2.98
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2250.82 | 1797.63 | 453.19 | 0.8 | 3.59
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1975.3 | 1577.58 | 397.72 | 0.8 | 3.63
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7732.27 | 6175.42 | 1556.85 | 0.8 | 2.99
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2424.14 | 1936.05 | 488.09 | 0.8 | 3.54
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7030.83 | 5615.21 | 1415.62 | 0.8 | 2.98
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1972.43 | 1575.29 | 397.14 | 0.8 | 3.63
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2249.29 | 1796.41 | 452.88 | 0.8 | 3.59
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8440.5 | 6741.05 | 1699.45 | 0.8 | 2.99
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7141.66 | 5703.72 | 1437.94 | 0.8 | 2.98
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8430.18 | 6732.81 | 1697.37 | 0.8 | 2.99
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2332.24 | 1862.65 | 469.58 | 0.8 | 3.55
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2061.77 | 1646.64 | 415.13 | 0.8 | 3.6
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7442.38 | 5943.9 | 1498.48 | 0.8 | 2.99
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1968.13 | 1571.86 | 396.27 | 0.8 | 3.63
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7317.11 | 5843.85 | 1473.26 | 0.8 | 2.98
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2039.11 | 1628.55 | 410.56 | 0.8 | 3.61
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2664.58 | 2128.08 | 536.5 | 0.8 | 3.45
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9947.91 | 7944.95 | 2002.96 | 0.8 | 2.98
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8366.82 | 6682.2 | 1684.61 | 0.8 | 2.99
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9957.34 | 7952.48 | 2004.86 | 0.8 | 2.98
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2747.34 | 2194.18 | 553.16 | 0.8 | 3.45
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2534.21 | 2023.96 | 510.25 | 0.8 | 3.48
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9114.13 | 7279.05 | 1835.08 | 0.8 | 2.98
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2371.77 | 1894.22 | 477.54 | 0.8 | 3.53
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9037.18 | 7217.59 | 1819.59 | 0.8 | 2.99
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2514.95 | 2008.58 | 506.37 | 0.8 | 3.49
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10729.17 | 7560.41 | 3168.76 | 0.7 | 3.74
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 18398.59 | 13075.3 | 5323.29 | 0.71 | 3.75
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1348.14 | 1014.18 | 333.96 | 0.75 | 3.88
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10897.17 | 7367.39 | 3529.78 | 0.68 | 3.67
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2210.8 | 1494.69 | 716.12 | 0.68 | 3.67
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5574.55 | 4351.33 | 1223.22 | 0.78 | 3.99
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 25282.36 | 20191.89 | 5090.47 | 0.8 | 3.75
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2817.29 | 1976.3 | 840.99 | 0.7 | 3.77
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5709.68 | 4377.12 | 1332.56 | 0.77 | 3.93
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8502.54 | 5748.42 | 2754.11 | 0.68 | 3.66
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8502.54 | 5748.42 | 2754.11 | 0.68 | 3.66
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8502.54 | 5748.42 | 2754.11 | 0.68 | 3.66
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 770.46 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 471.64 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 1482.35 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 1506.96 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1735.54 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 1730.02 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 1509.23 | 1
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 890.24 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 722.05 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 506.37 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 2085.42 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 5584.8 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 4335.37 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 5493.97 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1626.67 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1598.03 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 5220.66 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 1138.85 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 5385.75 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 1534.14 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 859.17 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 757.51 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 543.7 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 2142.74 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 5751.59 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 4577.12 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 5731.24 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1681.68 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1659.76 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 5689.54 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 1434.27 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 5677.38 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1606.18 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 906.88 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1549.88 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1109.91 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 3161.4 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 9773.43 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 7847.94 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 9761.68 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 2718.13 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 2701.03 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 9765.16 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 2638.78 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 9726.02 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 2666.61 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 296.42 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1726.03 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 11479.01 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 20116.69 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1693.36 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 10441.32 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 2118.32 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 6573.83 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 17460.55 | 0.8
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 2979.27 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 7482.58 | 0.78
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 8146.86 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 8146.86 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 8146.86 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.03 | 5.41 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.02 | 3.31 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.1 | 61.46 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.1 | 63.05 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.1 | 64.35 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.08 | 53.02 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.09 | 58.31 | 1 | PTAC Fan
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.03 | 6.25 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.03 | 5.07 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.02 | 3.56 | 1 | Unit Heater Fans
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 87.59 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.51 | 324.34 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.42 | 266.96 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.49 | 313.83 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 86.53 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.12 | 75.93 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.47 | 297.25 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.15 | 93.19 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.42 | 270.28 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.12 | 75.82 | 1 | PTAC Fan
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.03 | 6.04 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.03 | 5.32 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.02 | 3.82 | 1 | Unit Heater Fans
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 86.47 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.51 | 324.47 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.43 | 274.54 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.51 | 324.07 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 89.66 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.12 | 79.26 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.45 | 286.1 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.12 | 75.66 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.44 | 281.29 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.12 | 78.39 | 1 | PTAC Fan
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.03 | 6.37 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.05 | 10.89 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.04 | 7.8 | 1 | Unit Heater Fans
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.16 | 102.43 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.6 | 382.42 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.51 | 321.64 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.6 | 382.78 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.17 | 105.61 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.15 | 97.42 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.55 | 350.37 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 91.18 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.55 | 347.41 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.15 | 96.68 | 1 | PTAC Fan
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 2.08 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.06 | 12.12 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.48 | 559.59 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.85 | 963.15 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.07 | 82.55 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.44 | 509 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 103.27 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.32 | 371.39 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.53 | 1670.3 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.13 | 145.24 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.31 | 365.21 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 65231.7734 | 103.7558 | 145.345 | 0 | 0.0011 | 95485.5364 | 26834.6953
February | 56247.6806 | 89.3387 | 124.913 | 0 | 0.0009 | 82061.9272 | 23126.7061
March | 51719.1781 | 81.1622 | 111.6525 | 0 | 0.0008 | 73345.52 | 21170.7262
April | 43190.6096 | 69.2263 | 97.9555 | 0 | 0.0007 | 64355.2275 | 17818.0438
May | 42482.9518 | 70.95 | 105.6564 | 0 | 0.0008 | 69428.5164 | 17799.2836
June | 41946.3396 | 72.5302 | 112.3855 | 0 | 0.0008 | 73861.2614 | 17811.1692
July | 46210.018 | 80.8561 | 126.9136 | 0 | 0.0009 | 83413.2961 | 19712.7421
August | 44569.1751 | 77.5776 | 121.0805 | 0 | 0.0009 | 79577.8605 | 18973.8301
September | 40789.5801 | 69.4713 | 105.8387 | 0 | 0.0008 | 69554.2705 | 17218.7845
October | 43005.4744 | 70.574 | 102.8903 | 0 | 0.0008 | 67605.2945 | 17898.8566
November | 48427.4447 | 77.1242 | 108.2181 | 0 | 0.0008 | 71095.2144 | 19931.0791
December | 61071.825 | 96.7523 | 134.8168 | 0 | 0.001 | 88567.0083 | 25086.4297
Annual Sum or Average | 584892.0504 | 959.3188 | 1397.666 | 0 | 0.0104 | 918350.9329 | 243382.3463
Minimum of Months | 40789.5801 | 69.2263 | 97.9555 | 0 | 0.0007 | 64355.2275 | 17218.7845
Maximum of Months | 65231.7734 | 103.7558 | 145.345 | 0 | 0.0011 | 95485.5364 | 26834.6953
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 221567000000 | 161811.73 | 09-JAN-08:30 | 23685.52 | 40817.003 | 9415.14 | 87809.288 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 190419000000 | 164306.786 | 02-FEB-07:15 | 24319.757 | 51459.268 | 8885.907 | 77157.066 | 0 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 170193000000 | 123387.533 | 09-MAR-07:15 | 24319.757 | 51459.268 | 7283.528 | 40240.202 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 149331000000 | 100333.25 | 09-APR-07:00 | 26344.714 | 58181.634 | 6930.188 | 0 | 8791.935 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 161104000000 | 109060.819 | 28-MAY-07:00 | 26344.714 | 58181.634 | 7853.446 | 0 | 16596.247 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 171389000000 | 122091.329 | 14-JUN-19:00 | 36525.994 | 38968.112 | 9182.092 | 0 | 34930.343 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 193554000000 | 135294.247 | 08-JUL-07:00 | 26344.714 | 58181.634 | 9207.633 | 0 | 41475.488 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 184654000000 | 129797.31 | 13-AUG-19:30 | 36441.661 | 38950.562 | 9628.477 | 0 | 42291.82 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 161395000000 | 110284.142 | 03-SEP-07:00 | 26344.714 | 58181.634 | 7964.066 | 0 | 17708.95 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 156873000000 | 105271.664 | 07-OCT-07:00 | 26344.714 | 58181.634 | 7465.688 | 0 | 13194.85 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 164971000000 | 125015.492 | 25-NOV-08:15 | 26344.714 | 58181.634 | 7042.523 | 33361.842 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 205513000000 | 159440.493 | 31-DEC-08:15 | 26344.714 | 58181.634 | 8368.397 | 66460.971 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2130960000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 149331000000 | 100333.25 |  | 23685.52 | 38950.562 | 6930.188 | 0 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 221567000000 | 164306.786 |  | 36525.994 | 58181.634 | 9628.477 | 87809.288 | 42291.82 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 33246.2 | 17873.42 | 0 | 51119.62
Cost per Total Building Area ($/m2) | 8.28 | 4.45 | 0 | 12.74
Cost per Net Conditioned Building Area ($/m2) | 8.41 | 4.52 | 0 | 12.93

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 5390.07 | 1342.96 | 1363.41
Net Site Energy | 5390.07 | 1342.96 | 1363.41
Total Source Energy | 11894.5 | 2963.56 | 3008.69
Net Source Energy | 11894.5 | 2963.56 | 3008.69
Area [m2]
Total Building Area | 4013.59
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 60.2
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 578.18 | 2014.23 | 0 | 0 | 0 | 0
Cooling | 147.44 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 628.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 37.42 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 815.05 | 189.47 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 213.38 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 763.58 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2422.8 | 2967.28 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 6.46 |  | 0
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 5.38 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.6 |  | 0
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 11.84 | 3.08 | 15.43
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 9.7 | 32.61 | 10.7631
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 14 | 1.87 | 12.9
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 16.16 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 11.84 | 21.74 | 14.3
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 12.9 | 2.96 | 77.16
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 6.46 | 8.89 | 206.12
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2157.2117
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 9.7 | 2.96 | 11.4999
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 11.84 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 6.46 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 8.6 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 11.8 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 21.74 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 23.41 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 21.74 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 21.74 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 21.74 | 14.3
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
Total | 4013.59 |  | 11621.74 |  | 1694.58 | 184.21 | 10.425 | 15.71 | 24.2519
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 10.5838 | 15.47 | 16.4088
Unconditioned Total | 60.2 |  | 174.32 |  | 21.18 | 0 | 0 |  | 539.3029
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_REARSTAIRSFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_CORRIDORFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 6.13 | 90 | 90 | E
W_CORRIDORFLR1_10_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 10.22 | 180 | 90 | S
S_CORRIDORFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 150.51 | 270 | 180
W_REARSTORAGEFLR1_2_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 163.06 | 90 | 180
W_RESTROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 80.27 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM101_5_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_EMPLOYEELOUNGEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_LAUNDRYROOMFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 97.83 | 90 | 180
W_ELEVATORCOREFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 15.05 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 32.61 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 20.07 | 90 | 180
W_FRONTSTORAGEFLR1_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 12.54 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 6.69 | 0 | 90 | N
W_CORRIDORFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 8.36 | 0 | 90 | N
W_CORRIDORFLR2_15_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 5.02 | 270 | 90 | W
W_REARSTORAGEFLR2_2_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 6.69 | 180 | 90 | S
W_GUESTROOM201_4_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 43.48 | 0 | 90 | N
W_ELEVATORCOREFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 5.02 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 10.87 | 0 | 90 | N
W_FRONTSTORAGEFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 4.18 | 0 | 90 | N
W_FRONTSTAIRSFLR2_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 22.58 | 270 | 90 | W
W_REARSTAIRSFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 6.69 | 0 | 90 | N
W_CORRIDORFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 5.02 | 270 | 90 | W
W_REARSTORAGEFLR3_2_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 6.69 | 180 | 90 | S
W_GUESTROOM301_4_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 43.48 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 5.02 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 10.87 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 4.18 | 0 | 90 | N
W_FRONTSTAIRSFLR3_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 22.58 | 270 | 90 | W
W_REARSTAIRSFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 6.69 | 0 | 90 | N
R_REARSTAIRSFLR4_1_0_0 | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 20.07 | 90 | 0
W_CORRIDORFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 5.02 | 270 | 90 | W
R_CORRIDORFLR4_1_0_0 | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 125.42 | 90 | 0
W_REARSTORAGEFLR4_2_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 6.69 | 180 | 90 | S
R_REARSTORAGEFLR4_1_0_0 | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 20.07 | 90 | 0
W_GUESTROOM401_4_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 10.87 | 180 | 90 | S
R_GUESTROOM401_1_0_0 | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 32.61 | 90 | 0
W_GUESTROOM402_405_5_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 43.48 | 180 | 90 | S
R_GUESTROOM402_405_1_0_0 | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 130.45 | 90 | 0
W_GUESTROOM406_408_5_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 35.12 | 180 | 90 | S
R_GUESTROOM406_408_1_0_0 | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 105.36 | 90 | 0
W_GUESTROOM409_412_5_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 43.48 | 180 | 90 | S
R_GUESTROOM409_412_1_0_0 | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 130.45 | 90 | 0
W_GUESTROOM413_5_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 10.87 | 180 | 90 | S
R_GUESTROOM413_1_0_0 | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 32.61 | 90 | 0
W_GUESTROOM414_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 10.87 | 0 | 90 | N
R_GUESTROOM414_1_0_0 | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 32.61 | 90 | 0
W_GUESTROOM415_418_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 43.48 | 0 | 90 | N
R_GUESTROOM415_418_1_0_0 | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 130.44 | 90 | 0
W_ELEVATORCOREFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 5.02 | 0 | 90 | N
R_ELEVATORCOREFLR4_1_0_0 | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 15.05 | 90 | 0
W_GUESTROOM419_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 10.87 | 0 | 90 | N
R_GUESTROOM419_1_0_0 | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 32.61 | 90 | 0
W_GUESTROOM420_423_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 43.48 | 0 | 90 | N
R_GUESTROOM420_423_1_0_0 | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 130.44 | 90 | 0
W_GUESTROOM424_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 10.87 | 0 | 90 | N
R_GUESTROOM424_1_0_0 | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 32.61 | 90 | 0
W_FRONTSTORAGEFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 4.18 | 0 | 90 | N
R_FRONTSTORAGEFLR4_1_0_0 | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 12.54 | 90 | 0
W_FRONTSTAIRSFLR4_3_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | STEEL-FRAMED_R-13 + R-10 CI_EXT-WALL | 0.3 | 0.313 | 0.33 | 22.58 | 270 | 90 | W
R_FRONTSTAIRSFLR4_1_0_0 | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 20.07 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
W_CORRIDORFLR1_2_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 2.69 | 2.69 | 2.58 | 0.504 | 0.49 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
D_CORRIDORFLR1_16_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 4.44 | 4.44 | 2.58 | 0.504 | 0.49 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 2.69 | 2.69 | 2.58 | 0.504 | 0.49 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 2.97 | 2.97 | 2.58 | 0.504 | 0.49 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 2.97 | 2.97 | 2.58 | 0.504 | 0.49 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 2.97 | 2.97 | 2.58 | 0.504 | 0.49 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 2.97 | 2.97 | 2.58 | 0.504 | 0.49 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 2.96 | 2.96 | 2.58 | 0.504 | 0.49 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 2.58 | 0.504 | 0.49 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 2.58 | 0.504 | 0.49 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.65 | 1.65 | 2.58 | 0.504 | 0.49 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_GUESTROOM101_5_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.65 | 1.65 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.65 | 1.65 | 2.58 | 0.654 | 0.64 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 2.58 | 0.654 | 0.64 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 2.58 | 0.654 | 0.64 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 2.58 | 0.654 | 0.64 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 2.58 | 0.654 | 0.64 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.65 | 1.65 | 2.58 | 0.654 | 0.64 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.65 | 1.65 | 2.58 | 0.654 | 0.64 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 2.58 | 0.654 | 0.64 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 2.58 | 0.654 | 0.64 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 2.58 | 0.654 | 0.64 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 2.58 | 0.654 | 0.64 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_CORRIDORFLR2_2_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 1.31 | 1.31 | 2.58 | 0.504 | 0.49 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 1.31 | 1.31 | 2.58 | 0.504 | 0.49 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_GUESTROOM201_5_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.65 | 1.65 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 3.41 | 3.41 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.65 | 1.65 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.65 | 1.65 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.65 | 1.65 | 2.58 | 0.654 | 0.64 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 2.58 | 0.654 | 0.64 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 2.58 | 0.654 | 0.64 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 2.58 | 0.654 | 0.64 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 2.58 | 0.654 | 0.64 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.65 | 1.65 | 2.58 | 0.654 | 0.64 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.65 | 1.65 | 2.58 | 0.654 | 0.64 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 2.58 | 0.654 | 0.64 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 2.58 | 0.654 | 0.64 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 2.58 | 0.654 | 0.64 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 2.58 | 0.654 | 0.64 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_CORRIDORFLR3_2_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 1.31 | 1.31 | 2.58 | 0.504 | 0.49 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 1.31 | 1.31 | 2.58 | 0.504 | 0.49 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_GUESTROOM301_5_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.65 | 1.65 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 3.41 | 3.41 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.65 | 1.65 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.65 | 1.65 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.65 | 1.65 | 2.58 | 0.654 | 0.64 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 2.58 | 0.654 | 0.64 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 2.58 | 0.654 | 0.64 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 2.58 | 0.654 | 0.64 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 2.58 | 0.654 | 0.64 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.65 | 1.65 | 2.58 | 0.654 | 0.64 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.65 | 1.65 | 2.58 | 0.654 | 0.64 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 2.58 | 0.654 | 0.64 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 2.58 | 0.654 | 0.64 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 2.58 | 0.654 | 0.64 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 2.58 | 0.654 | 0.64 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_CORRIDORFLR4_2_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 1.31 | 1.31 | 2.58 | 0.504 | 0.49 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 1.31 | 1.31 | 2.58 | 0.504 | 0.49 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_GUESTROOM401_5_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.65 | 1.65 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.65 | 1.65 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 3.41 | 3.41 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.64 | 1.64 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1.65 | 1.65 | 2.58 | 0.504 | 0.49 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.65 | 1.65 | 2.58 | 0.654 | 0.64 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 2.58 | 0.654 | 0.64 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 2.58 | 0.654 | 0.64 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 2.58 | 0.654 | 0.64 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 2.58 | 0.654 | 0.64 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.65 | 1.65 | 2.58 | 0.654 | 0.64 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.65 | 1.65 | 2.58 | 0.654 | 0.64 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 2.58 | 0.654 | 0.64 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 2.58 | 0.654 | 0.64 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 2.58 | 0.654 | 0.64 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 1.64 | 1.64 | 2.58 | 0.654 | 0.64 | No | W_GUESTROOM424_3_0_0 | 0 | N
Total or Average |  |  | 184.21 | 2.58 | 0.563 | 0.549
North Total or Average |  |  | 72.38 | 2.58 | 0.654 | 0.64
Non-North Total or Average |  |  | 111.83 | 2.58 | 0.504 | 0.49
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1528.09 | 1220.42 | 307.67 | 0.8 | 3.61
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1574.11 | 1257.17 | 316.94 | 0.8 | 3.65
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1574.97 | 1257.86 | 317.11 | 0.8 | 3.65
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1194.5 | 953.99 | 240.51 | 0.8 | 3.61
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1356.75 | 1083.57 | 273.17 | 0.8 | 3.61
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2315.79 | 1849.52 | 466.27 | 0.8 | 3.55
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8774.87 | 7008.09 | 1766.77 | 0.8 | 2.99
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7306.54 | 5835.41 | 1471.13 | 0.8 | 2.98
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8471.45 | 6765.77 | 1705.68 | 0.8 | 2.98
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2310.44 | 1845.25 | 465.2 | 0.8 | 3.56
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1901.92 | 1518.98 | 382.94 | 0.8 | 3.6
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7500.71 | 5990.48 | 1510.23 | 0.8 | 2.98
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2373.49 | 1895.6 | 477.89 | 0.8 | 3.53
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6801.26 | 5431.86 | 1369.4 | 0.8 | 2.98
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1888.68 | 1508.4 | 380.28 | 0.8 | 3.6
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2296.56 | 1834.16 | 462.4 | 0.8 | 3.56
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8808.77 | 7035.17 | 1773.6 | 0.8 | 2.98
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7561.01 | 6038.64 | 1522.37 | 0.8 | 2.99
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8795.78 | 7024.8 | 1770.98 | 0.8 | 2.98
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2409.8 | 1924.6 | 485.2 | 0.8 | 3.54
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1996.54 | 1594.54 | 401.99 | 0.8 | 3.62
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7234.77 | 5778.09 | 1456.68 | 0.8 | 2.99
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1904.02 | 1520.66 | 383.37 | 0.8 | 3.65
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7110.34 | 5678.71 | 1431.63 | 0.8 | 2.99
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1964.37 | 1568.85 | 395.52 | 0.8 | 3.63
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2447.55 | 1954.75 | 492.8 | 0.8 | 3.52
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9402.89 | 7509.66 | 1893.22 | 0.8 | 2.99
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8058.36 | 6435.85 | 1622.51 | 0.8 | 2.99
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9411.71 | 7516.71 | 1895 | 0.8 | 2.99
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2568.9 | 2051.66 | 517.23 | 0.8 | 3.5
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2246.08 | 1793.85 | 452.24 | 0.8 | 3.59
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8078.01 | 6451.55 | 1626.47 | 0.8 | 2.99
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2071.68 | 1654.56 | 417.12 | 0.8 | 3.64
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8001.66 | 6390.57 | 1611.09 | 0.8 | 2.98
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2207.3 | 1762.87 | 444.43 | 0.8 | 3.57
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7016.29 | 5603.6 | 1412.69 | 0.8 | 4.04
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13897.33 | 11099.18 | 2798.15 | 0.8 | 4.03
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1096.07 | 875.38 | 220.69 | 0.8 | 4.13
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7044.49 | 5626.12 | 1418.37 | 0.8 | 4.07
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1473.75 | 1177.01 | 296.73 | 0.8 | 4.07
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5001.22 | 3994.25 | 1006.97 | 0.8 | 4.05
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 23959.38 | 19135.28 | 4824.09 | 0.8 | 3.75
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1910.98 | 1526.21 | 384.76 | 0.8 | 4.11
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4531.85 | 3619.38 | 912.46 | 0.8 | 4.04
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5667.89 | 4526.69 | 1141.2 | 0.8 | 4.05
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5667.89 | 4526.69 | 1141.2 | 0.8 | 4.05
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5667.89 | 4526.69 | 1141.2 | 0.8 | 4.05
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1204.43 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 737.51 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 1886.62 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 1911.48 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 2147.81 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 2146.88 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 1920.03 | 1
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1339.21 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1058.79 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 704.52 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 2574.04 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 6943.86 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 5376.64 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 6848.19 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1971.16 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1944.76 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 6596.26 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 1449.72 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 6755.51 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 1889.47 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1209.75 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1093.65 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 740.38 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 2626.73 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 7086.8 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 5594.05 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 7064.19 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 2020.7 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1999.03 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 7024.39 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 1785.06 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 7010.18 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1952.24 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1255.16 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 2097.35 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1420.02 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 3817.98 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 11806.23 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 9428.63 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 11792.5 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 3234.05 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 3215.98 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 11795.19 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 3183.83 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 11753.27 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 3178.29 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 401.23 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 2279.54 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 12488.72 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 24736.69 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1950.96 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 12538.91 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 2623.21 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 7937.59 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 19626.08 | 0.8
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 3401.46 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 8066.5 | 0.78
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 10088.61 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 10088.61 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 10088.61 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.04 | 8.17 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.03 | 5 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.09 | 58.74 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.1 | 60.51 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.1 | 60.55 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.07 | 45.92 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.08 | 52.16 | 1 | PTAC Fan
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.05 | 9.08 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.04 | 7.18 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.02 | 4.78 | 1 | Unit Heater Fans
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 89.02 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.53 | 337.32 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.44 | 280.88 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.51 | 325.66 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 88.82 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 73.11 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.45 | 288.34 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 91.24 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.41 | 261.46 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.11 | 72.6 | 1 | PTAC Fan
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.04 | 8.21 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.04 | 7.42 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.03 | 5.02 | 1 | Unit Heater Fans
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 88.28 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.53 | 338.63 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.46 | 290.66 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.53 | 338.13 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.15 | 92.64 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.12 | 76.75 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.44 | 278.12 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.12 | 73.19 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.43 | 273.34 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.12 | 75.51 | 1 | PTAC Fan
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.04 | 8.51 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.07 | 14.22 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.05 | 9.63 | 1 | Unit Heater Fans
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.15 | 94.09 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.57 | 361.47 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.49 | 309.78 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.57 | 361.81 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.16 | 98.75 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.14 | 86.34 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.49 | 310.54 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.13 | 79.64 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.48 | 307.6 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 330.9 | 0.13 | 84.85 | 1 | PTAC Fan
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.01 | 2.72 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.25 | 50 | 0.08 | 15.46 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.42 | 491.63 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.84 | 956.4 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.07 | 76.8 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.43 | 493.61 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 103.27 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.3 | 350.44 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.45 | 1582.9 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.12 | 133.9 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.27 | 317.55 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.15 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 83429.6322 | 97.4955 | 455.5108 | 0 | 0.0016 | 91403.2662 | 32223.8265
February | 69368.5037 | 80.564 | 368.2855 | 0 | 0.0013 | 73898.5671 | 26715.9665
March | 56021.7329 | 63.9229 | 273.5686 | 0 | 0.001 | 54888.4446 | 21400.2263
April | 43491.5746 | 49.8855 | 217.8209 | 0 | 0.0008 | 43704.4574 | 16653.7395
May | 39227.1554 | 46.4955 | 227.8728 | 0 | 0.0008 | 45727.7912 | 15251.8486
June | 38147.5187 | 46.0205 | 238.4354 | 0 | 0.0008 | 47850.4102 | 14955.9024
July | 39900.5283 | 48.3875 | 254.6685 | 0 | 0.0009 | 51109.023 | 15681.9868
August | 38628.65 | 46.5106 | 239.5527 | 0 | 0.0008 | 48074.3254 | 15130.6305
September | 38202.7127 | 44.9402 | 214.7864 | 0 | 0.0007 | 43100.4418 | 14801.0521
October | 46361.3922 | 53.1487 | 231.5975 | 0 | 0.0008 | 46468.5266 | 17748.2593
November | 61857.404 | 71.1224 | 313.3813 | 0 | 0.0011 | 62878.8175 | 23712.6778
December | 74341.897 | 86.1709 | 391.1489 | 0 | 0.0014 | 78485.5675 | 28605.33
Annual Sum or Average | 628978.7017 | 734.6642 | 3426.6294 | 0 | 0.0119 | 687589.6385 | 242881.4463
Minimum of Months | 38147.5187 | 44.9402 | 214.7864 | 0 | 0.0007 | 43100.4418 | 14801.0521
Maximum of Months | 83429.6322 | 97.4955 | 455.5108 | 0 | 0.0016 | 91403.2662 | 32223.8265
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 322069000000 | 236206.946 | 13-JAN-08:00 | 23685.52 | 40817.003 | 11042.216 | 158177.418 | 0 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 260390000000 | 228892.809 | 04-FEB-08:15 | 26344.714 | 58181.634 | 10017.152 | 131864.52 | 0 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 193405000000 | 149630.19 | 14-MAR-07:45 | 23685.52 | 40817.003 | 8049.582 | 76993.306 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 153997000000 | 105411.361 | 02-APR-07:15 | 26344.714 | 58181.634 | 6095.922 | 14668.111 | 36.202 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 161127000000 | 104565.667 | 29-MAY-07:00 | 26344.714 | 58181.634 | 7251.684 | 0 | 12702.856 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 168606000000 | 112542.547 | 24-JUN-07:00 | 26344.714 | 58181.634 | 8038.389 | 0 | 19893.031 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 180088000000 | 116657.098 | 29-JUL-19:45 | 36357.328 | 38915.462 | 8945.947 | 0 | 32353.582 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 169395000000 | 109865.276 | 15-AUG-19:15 | 36525.994 | 38968.112 | 8498.135 | 0 | 25788.257 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 151869000000 | 102342.376 | 04-SEP-07:00 | 26344.714 | 58181.634 | 6930.692 | 0 | 10800.557 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 163737000000 | 110579.782 | 22-OCT-07:15 | 26344.714 | 58181.634 | 6177.366 | 17352.648 | 38.632 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 221560000000 | 147869.018 | 23-NOV-08:15 | 26344.714 | 58181.634 | 7222.782 | 53635.1 | 0 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 276552000000 | 200004.233 | 29-DEC-08:00 | 23685.52 | 40817.003 | 9769.443 | 123247.479 | 0 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2422800000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 151869000000 | 102342.376 |  | 23685.52 | 38915.462 | 6095.922 | 0 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 322069000000 | 236206.946 |  | 36525.994 | 58181.634 | 11042.216 | 158177.418 | 32353.582 | 2400.01 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 62883.45 | 12386.54 | 0 | 75269.99
Cost per Total Building Area ($/m2) | 15.67 | 3.09 | 0 | 18.75
Cost per Net Conditioned Building Area ($/m2) | 15.91 | 3.13 | 0 | 19.04

## Picture
DOE Commercial Building Benchmark - Small Hotel
First Floor
Upper Floors

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | 8.55 | 58.7 | 3060.79
|  |  | Sat | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | 7.85
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3 | 8.1
GuestRoom_Ltg_Sch_Base | Fraction | Through 12/31 | WD | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33 | 9.51 | 58.28 | 3038.89
|  |  | Sat, Sun, Hol | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41 | 10.73
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Lobby_Ltg_Sch | Fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.6 | 0.5 | 0.5 | 19.7 | 118.2 | 6163.29
|  |  | Sat, Sun, Hol | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.6 | 0.5 | 0.5 | 19.7
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Office_Ltg_Sch_Base | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.61 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.61 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 15.72 | 78.6 | 4098.43
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
EmployeeLounge_Ltg_Sch | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.4 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.4 | 0.15 | 0.15 | 0.05 | 0.05 | 12.6 | 71.2 | 3712.57
|  |  | Sat, Sun, Hol | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.3 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.3 | 0.15 | 0.15 | 0.05 | 0.05 | 8.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MeetingRoom_Ltg_Sch_Base | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0 | 12.05 | 60.25 | 3141.61
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Storage_Ltg_Sch | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9 | 35.4 | 1845.86
|  |  | Sat, Sun, Hol | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MechanicalRoom_Ltg_Sch | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9 | 35.4 | 1845.86
|  |  | Sat, Sun, Hol | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
ExerciseRoom_Ltg_Sch_Base | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | 16 | 112 | 5840
LaundryRoom_Ltg_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 63 | 3285
Corridor_Ltg_Sch | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Exterior_Ltg_Sch | Fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 12 | 84 | 4380
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4 | 10.9 | 75.25 | 3923.75
|  |  | Sat | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4 | 10.25
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4 | 10.5
GuestRoom_Eqp_Sch | Fraction | Through 12/31 | WD | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.11 | 8.19 | 49.33 | 2572.21
|  |  | Sat, Sun, Hol | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.11 | 8.38
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Lobby_Eqp_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.68 | 1 | 1 | 1 | 1 | 0.32 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.21 | 9.02 | 45.1 | 2351.64
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Office_Eqp_Sch | Fraction | Through 12/31 | WD | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.43 | 0.43 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.75 | 0.63 | 0.63 | 0.48 | 0.48 | 0.33 | 0.33 | 14.27 | 83.07 | 4331.51
|  |  | Sat, Sun, Hol | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.48 | 0.48 | 0.48 | 0.48 | 0.33 | 0.33 | 11.72
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
EmployeeLounge_Eqp_Sch | Fraction | Through 12/31 | WD | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11 | 11.08 | 66.48 | 3466.46
|  |  | Sat, Sun, Hol | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11 | 11.08
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
LaundryRoom_Eqp_Elec_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 2085.71
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
LaundryRoom_Eqp_Gas_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 2085.71
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MeetingRoom_Eqp_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.26 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 3.66 | 25.62 | 1335.9
ExerciseRoom_Eqp_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0 | 10.5 | 73.5 | 3832.5
Kitchen_Elec_Equip_SCH | Fraction | Through 12/31 | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 5.95 | 23.8 | 1241
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 5.95
|  |  | SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 7.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 5.95
Kitchen_Gas_Equip_SCH | Fraction | Through 12/31 | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65 | 21.9 | 1141.93
|  |  | SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65
Kitchen_Exhaust_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 2.72 | 19.04 | 992.8
BLDG_ELEVATORS | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | 5.9 | 41.3 | 2153.5
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9 | 13.9 | 96.4 | 5026.57
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 13.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 13
GuestRoom_Occ_Sch | Fraction | Through 12/31 | WD | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.43 | 0.43 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.31 | 0.54 | 0.54 | 0.54 | 0.77 | 0.77 | 0.89 | 1 | 1 | 15.19 | 90.86 | 4737.7
|  |  | Sat, Sun, Hol | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.53 | 0.53 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.53 | 0.54 | 0.65 | 0.65 | 0.77 | 0.77 | 0.77 | 14.91
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Lobby_Occ_Sch | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 6.6 | 38.6 | 2012.71
|  |  | Sat, Sun, Hol | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Office_Occ_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 12.1 | 68.2 | 3556.14
|  |  | Sat, Sun, Hol | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 7.7
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
EmployeeLounge_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 3.1 | 16.85 | 878.61
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 1.35
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MeetingRoom_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 3.2 | 19.2 | 1001.14
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 3.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
LaundryRoom_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.17 | 7.02 | 366.04
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.17
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
ExerciseRoom_Occ_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | 14.5 | 101.5 | 5292.5
INFIL_SCH | fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INFIL_HALF_ON_SCH | fraction | Through 12/31 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84 | 4380
INFIL_QUARTER_ON_SCH | fraction | Through 12/31 | All | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6 | 42 | 2190
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.5 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | 9 | 63.3 | 3300.64
|  |  | Sat, WinterDesign | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.4 | 0.5 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3 | 9.3
|  |  | Sun, Hol, Other | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.55 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2 | 9
GuestRoom_SWH_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25 | 8 | 40 | 2085.71
|  |  | Other | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35 | 7.8
LaundryRoom_SWH_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 56 | 2920
Hours_of_operation | on/off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | on/off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | All | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 3528 | 183960
HTGSETP_SCH_KEYCARD | Temperature | Through 12/31 | SummerDesign, WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 0 | 0
|  |  | Other | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 486
CLGSETP_SCH | Temperature | Through 12/31 | All | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 4032 | 210240
CLGSETP_SCH_KEYCARD | Temperature | Through 12/31 | SummerDesign, WinterDesign | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 0 | 0
|  |  | Other | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 25 | 25 | 25 | 26 | 26 | 26 | 26 | 26 | 26 | 25 | 25 | 25 | 24 | 24 | 24 | 24 | 24 | 594
SemiHeated_HtgSP_Sch | Temperature | Through 12/31 | All | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 172.8 | 1209.6 | 63072
Base_OccGuestRoom_HtgSP_Sch | Temperature | Through 12/31 | All | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 506.4 | 3544.8 | 184836
Base_OccGuestRoom_ClgSP_Sch | Temperature | Through 12/31 | All | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 506.4 | 3544.8 | 184836
VacGuestRoom_HtgSP_Sch | Temperature | Through 12/31 | All | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 453.6 | 3175.2 | 165564
VacGuestRoom_ClgSP_Sch | Temperature | Through 12/31 | All | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 559.2 | 3914.4 | 204108
CommonArea_HtgSP_Sch | Temperature | Through 12/31 | All | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 506.4 | 3544.8 | 184836
CommonArea_ClgSP_Sch | Temperature | Through 12/31 | All | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 573.6 | 4015.2 | 209364
Off During Unoccupied Period | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 70 | 3650
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SHWSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SHWSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SHWSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720