## BuildingSummary
Building Summary Strip Mall new construction version 1.1_3.1
|  | Value | Data Source
Program
| Building Name | Benchmark Strip Mall
| Available Fuel Types | gas, electricity
| Principal Building Activity | Strip Mall
Form
| Total Floor Area (ft2) | 22500 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 4
| Number of Floors | 1
| Window Fraction (Window to Wall Ratio) | South: 0.26 East: 0.00 North: 0.00 West: 0.00 Total: 0.105
| Skylight/TDD Percentage | 0.00%
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | 10 stores
| Floor to Ceiling Height (ft) | 5.1816
| Roof type | Insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel-frame | 2003 CBECS
| Gross Dimensions - Total Area (ft2) | 12746.08
| Net Dimensions - Total Area (ft2) | 10906.86
| Wall to Skin Ratio | 0.36
Roof
| Construction Type | Insulation entirely above deck | 2003 CBECS
| Gross Dimensions - Total Area (ft2) | 22500
| Net Dimensions - Total Area (ft2) | 22500
| Roof to Skin Ratio | 0.64
Window
| Dimensions - Total Area (ft2) | South: 1,338 East: 0.00 North: 0.00 West: 0.00 Total: 1,338
| Operable area (ft2) | 0
Skylights/TDD
| Dimensions - Total Area (ft2) | 0
| Operable area (ft2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab-on-grade
| Dimensions - Total Area (ft2) | 22500
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
Internal Mass
| Construction | 6 inch wood
| Dimensions - Total Area (ft2) | 45000
| Thermal Properties (lb/ft2 ) | 16.6
Air Barrier System
| Infiltration (ACH) | 0.33 | See Benchmark Technical Report
HVAC
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | Unitary DX | 2003 CBECS
| Fan Control | Constant volume | 2003 CBECS
Service Water Heating
| SWH Type | N/A
| Fuel | N/A
| Thermal Efficiency (%) | N/A
| Temperature Setpoint (ºF ) | N/A
| Water Consumption (gal ) | N/A

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (ft2) | Volume (ft3) | Floor-to-Ceiling Height (ft) | Gross Wall Area (ft2) | Window Glass Area (ft2) | People (ft2/per) | People | Lights (W/ft2) | Elec Plug and Process (W/ft2) | Gas Plug and Process (W/ft2) | SWH (gal/h) | Ventilation (cfm/Person) | Ventilation (cfm/ft2) | Ventilation Total (cfm) | Exhaust (cfm) | Infiltration (ACH)
LGStore1 | Yes | 1 | 348.3864 | 1805.1988 | 5.1816 | 276.3 | 20.75 | 6.1938 | 56.2472 | 23.9948 | 4.304 | 0 | 0 | 3.8 | 0.6 | 422.7712 | 0 | 0.37663
SMStore1 | Yes | 1 | 174.1932 | 902.5994 | 5.1816 | 78.94 | 10.37 | 6.1938 | 28.1236 | 23.9948 | 4.304 | 0 | 0 | 3.8 | 0.6 | 211.3856 | 0 | 0.30523
SMStore2 | Yes | 1 | 174.1932 | 902.5994 | 5.1816 | 78.94 | 10.37 | 6.1938 | 28.1236 | 18.292 | 4.304 | 0 | 0 | 3.8 | 0.6 | 211.3856 | 0 | 0.30523
SMStore3 | Yes | 1 | 174.1932 | 902.5994 | 5.1816 | 78.94 | 10.37 | 6.1938 | 28.1236 | 18.292 | 4.304 | 0 | 0 | 3.8 | 0.6 | 211.3856 | 0 | 0.30523
SMStore4 | Yes | 1 | 174.1932 | 902.5994 | 5.1816 | 78.94 | 10.37 | 6.1938 | 28.1236 | 18.292 | 4.304 | 0 | 0 | 3.8 | 0.6 | 211.3856 | 0 | 0.30523
LGStore2 | Yes | 1 | 348.3864 | 1805.1988 | 5.1816 | 157.89 | 20.75 | 6.1938 | 56.2472 | 13.7728 | 4.304 | 0 | 0 | 3.8 | 0.6 | 422.7712 | 0 | 0.30524
SMStore5 | Yes | 1 | 174.1932 | 902.5994 | 5.1816 | 78.94 | 10.37 | 6.1938 | 28.1236 | 13.7728 | 4.304 | 0 | 0 | 3.8 | 0.6 | 211.3856 | 0 | 0.30523
SMStore6 | Yes | 1 | 174.1932 | 902.5994 | 5.1816 | 78.94 | 10.37 | 6.1938 | 28.1236 | 13.7728 | 4.304 | 0 | 0 | 3.8 | 0.6 | 211.3856 | 0 | 0.30523
SMStore7 | Yes | 1 | 174.1932 | 902.5994 | 5.1816 | 78.94 | 10.37 | 6.1938 | 28.1236 | 13.7728 | 4.304 | 0 | 0 | 3.8 | 0.6 | 211.3856 | 0 | 0.30523
SMStore8 | Yes | 1 | 174.1932 | 902.5994 | 5.1816 | 197.36 | 10.37 | 6.1938 | 28.1236 | 13.7728 | 4.304 | 0 | 0 | 3.8 | 0.6 | 211.3856 | 0 | 0.44802
Total Conditioned Zones |  |  | 2090.3185 | 10831.1928 |  | 1184.13 | 124.46 |  | 337.4831
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7A | 8A
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fabric
Exterior walls
| Construction Type | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame
| R-value (m2·K / W) | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 2.0964 | 2.0964 | 2.0964 | 2.0964 | 2.7473 | 2.7473
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 3.663
Window
| U-Factor (W / m2·K) | 6.49 | 6.49 | 6.49 | 3.18 | 3.18 | 3.18 | 6.49 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 2.58
| SHGC | 0.25 | 0.25 | 0.25 | 0.402 | 0.402 | 0.402 | 0.61 | 0.402 | 0.402 | 0.402 | 0.501 | 0.501 | 0.501 | 0.501 | 0.501 | 0.504
| Visible transmittance | 0.25 | 0.25 | 0.25 | 0.495 | 0.495 | 0.495 | 0.61 | 0.495 | 0.495 | 0.495 | 0.622 | 0.622 | 0.622 | 0.622 | 0.49 | 0.49
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade
| R-value (m2·K / W) | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | 41.9238 | 40.1729 | 31.2044 | 39.8055 | 25.367 | 34.0913 | 21.2957 | 39.5059 | 30.3616 | 23.6997 | 36.8634 | 26.3129 | 34.6022 | 25.0267 | 29.718 | 28.4412
| PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | 22.6812 | 21.8364 | 16.4736 | 20.0819 | 12.1836 | 12.986 | 9.9166 | 19.6944 | 13.4918 | 11.1376 | 17.9231 | 12.6643 | 17.0977 | 12.1555 | 12.9022 | 12.0861
| PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | 20.3768 | 19.5421 | 14.9816 | 18.1215 | 10.7921 | 11.4052 | 8.8961 | 17.4453 | 12.222 | 10.195 | 15.7566 | 11.43 | 15.5784 | 10.9847 | 13.1023 | 12.0242
| PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | 20.0092 | 19.1776 | 14.7348 | 17.7598 | 10.5697 | 11.1427 | 8.7876 | 17.0865 | 12.0909 | 10.0954 | 15.4819 | 11.2985 | 15.3947 | 10.8605 | 13.1505 | 12.0218
| PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | 19.741 | 18.9097 | 14.5579 | 17.4912 | 10.3967 | 10.9518 | 8.7281 | 16.8175 | 12.0262 | 10.043 | 15.4052 | 11.2301 | 15.3181 | 10.7965 | 13.1993 | 12.0386
| PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | 33.1686 | 31.6381 | 25.1486 | 28.9378 | 19.2446 | 26.5239 | 14.981 | 27.9053 | 21.2025 | 17.8338 | 28.3667 | 19.6183 | 28.2229 | 20.3556 | 27.2109 | 23.7641
| PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | 17.718 | 16.8957 | 13.2133 | 15.5076 | 9.9926 | 13.65 | 7.9053 | 14.853 | 11.0277 | 9.276 | 14.8165 | 10.2262 | 14.7555 | 10.3429 | 13.624 | 12.0388
| PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | 17.6453 | 16.8242 | 13.1804 | 15.4358 | 9.9546 | 13.614 | 7.8703 | 14.7813 | 10.9852 | 9.243 | 14.7539 | 10.1823 | 14.6925 | 10.3302 | 13.6273 | 12.0261
| PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | 17.6059 | 16.7751 | 13.2743 | 15.3672 | 9.9974 | 13.7298 | 7.9013 | 14.7038 | 11.072 | 9.2858 | 14.8265 | 10.2313 | 14.7661 | 10.4187 | 13.7026 | 12.1043
| PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | 17.318 | 18.948 | 18.5749 | 18.647 | 10.8726 | 16.1221 | 8.7054 | 17.8952 | 12.9851 | 10.221 | 16.9404 | 12.0035 | 19.3005 | 14.3273 | 18.1236 | 16.6544
Heating (kW)
| PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | 20.2322 | 30.5543 | 24.6904 | 35.723 | 21.0423 | 29.5205 | 24.2488 | 41.6847 | 34.9837 | 33.0892 | 51.7798 | 43.8911 | 58.5641 | 55.8708 | 60.3925 | 78.3775
| PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | 10.1161 | 13.9928 | 11.4078 | 16.3089 | 10.5212 | 13.5799 | 11.6294 | 19.0395 | 15.9663 | 15.1469 | 23.9158 | 20.2648 | 27.0235 | 25.761 | 28.0594 | 36.2704
| PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | 10.1161 | 13.9339 | 11.358 | 16.2409 | 10.5212 | 13.521 | 11.6294 | 18.9642 | 15.894 | 15.084 | 23.8437 | 20.195 | 26.9439 | 25.6794 | 27.9886 | 36.1857
| PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | 10.1161 | 13.9311 | 11.3558 | 16.2377 | 10.5212 | 13.5184 | 11.6294 | 18.9607 | 15.8908 | 15.0811 | 23.8407 | 20.1921 | 26.9406 | 25.6761 | 27.9858 | 36.1825
| PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | 10.1161 | 13.9434 | 11.3687 | 16.2518 | 10.5212 | 13.5331 | 11.6294 | 18.9766 | 15.9072 | 15.0947 | 23.8586 | 20.2103 | 26.9604 | 25.697 | 28.0059 | 36.2054
| PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | 20.2322 | 27.6398 | 22.5344 | 32.226 | 21.0423 | 26.7695 | 23.2587 | 37.6421 | 31.4901 | 29.9185 | 47.3735 | 40.0705 | 53.5425 | 50.9971 | 55.6297 | 71.9831
| PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | 10.1161 | 13.9437 | 11.369 | 16.2521 | 10.5212 | 13.5334 | 11.6294 | 18.977 | 15.9075 | 15.095 | 23.8589 | 20.2106 | 26.9607 | 25.6973 | 28.0062 | 36.2058
| PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | 10.1161 | 13.9362 | 11.3598 | 16.2436 | 10.5212 | 13.5231 | 11.6294 | 18.967 | 15.8967 | 15.0865 | 23.8462 | 20.1973 | 26.9465 | 25.6821 | 27.9907 | 36.1883
| PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | 10.1161 | 14.0179 | 11.4248 | 16.3396 | 10.5212 | 13.6015 | 11.6294 | 19.0731 | 15.9964 | 15.1743 | 23.9409 | 20.2879 | 27.0513 | 25.7886 | 28.0777 | 36.2953
| PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | 10.1161 | 16.8106 | 13.5516 | 19.6938 | 10.5455 | 16.2269 | 13.3164 | 22.9581 | 19.3395 | 18.2164 | 28.1989 | 23.9676 | 31.91 | 30.4977 | 32.6972 | 42.5164
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | 3.19 | 3.19 | 3.65 | 3.23 | 3.74 | 3.62 | 3.79 | 3.44 | 3.74 | 3.75 | 3.43 | 3.74 | 3.46 | 3.74 | 3.55 | 3.74
| PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | 3.45 | 3.45 | 3.9 | 3.46 | 4 | 4.02 | 4.06 | 3.45 | 4.04 | 3.97 | 3.65 | 4.04 | 3.68 | 4.02 | 3.78 | 4.03
| PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | 3.45 | 3.45 | 3.88 | 3.65 | 4.03 | 4.06 | 4.06 | 3.66 | 4.04 | 3.96 | 3.66 | 4.05 | 3.67 | 4.05 | 3.75 | 4.04
| PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | 3.45 | 3.45 | 3.88 | 3.66 | 4.02 | 4.05 | 4.05 | 3.67 | 4.03 | 3.95 | 3.66 | 4.05 | 3.66 | 4.06 | 3.75 | 4.04
| PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | 3.45 | 3.65 | 3.88 | 3.66 | 4.02 | 4.05 | 4.06 | 3.67 | 4.04 | 3.96 | 3.66 | 4.06 | 3.67 | 4.05 | 3.74 | 4.04
| PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | 3.45 | 3.45 | 3.62 | 3.45 | 3.75 | 3.56 | 4.04 | 3.45 | 3.79 | 3.91 | 3.45 | 3.79 | 3.45 | 3.79 | 3.49 | 3.75
| PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | 3.65 | 3.66 | 3.87 | 3.66 | 4 | 3.8 | 4.06 | 3.67 | 4.06 | 3.94 | 3.67 | 4.06 | 3.66 | 4.05 | 3.72 | 4.04
| PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | 3.65 | 3.67 | 3.87 | 3.66 | 4.01 | 3.8 | 4.07 | 3.67 | 4.05 | 3.92 | 3.66 | 4.07 | 3.66 | 4.05 | 3.72 | 4.04
| PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | 3.65 | 3.67 | 3.88 | 3.67 | 4 | 3.79 | 4.06 | 3.66 | 4.06 | 3.94 | 3.67 | 4.06 | 3.66 | 4.06 | 3.73 | 4.03
| PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | 3.67 | 3.65 | 3.74 | 3.65 | 4.02 | 3.83 | 4.07 | 3.65 | 4.02 | 3.96 | 3.66 | 4.04 | 3.45 | 4.04 | 3.73 | 4.04
Heating Efficiency (%)
| PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78
| PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78
| PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
HVAC Control - Economizer
| PSZ-AC_1:1_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ-AC_2:2_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC_3:3_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC_4:4_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC_5:5_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC_6:6_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ-AC_7:7_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC_8:8_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC_9:9_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC_10:10_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
Fan Max Flow Rate (m3/s )
| PSZ-AC_1:1_UNITARY_PACKAGE_FAN | 1.69 | 1.62 | 1.71 | 1.72 | 1.53 | 1.8 | 1.29 | 1.64 | 1.83 | 1.38 | 1.48 | 1.59 | 1.47 | 1.51 | 1.39 | 1.72
| PSZ-AC_2:2_UNITARY_PACKAGE_FAN | 0.91 | 0.88 | 0.89 | 0.82 | 0.72 | 0.78 | 0.6 | 0.79 | 0.82 | 0.63 | 0.72 | 0.77 | 0.72 | 0.73 | 0.6 | 0.73
| PSZ-AC_3:3_UNITARY_PACKAGE_FAN | 0.82 | 0.79 | 0.79 | 0.73 | 0.64 | 0.69 | 0.54 | 0.7 | 0.74 | 0.57 | 0.63 | 0.69 | 0.63 | 0.66 | 0.59 | 0.73
| PSZ-AC_4:4_UNITARY_PACKAGE_FAN | 0.81 | 0.77 | 0.78 | 0.72 | 0.62 | 0.67 | 0.53 | 0.69 | 0.73 | 0.56 | 0.62 | 0.68 | 0.62 | 0.66 | 0.59 | 0.73
| PSZ-AC_5:5_UNITARY_PACKAGE_FAN | 0.79 | 0.76 | 0.77 | 0.7 | 0.61 | 0.66 | 0.53 | 0.68 | 0.73 | 0.56 | 0.62 | 0.68 | 0.62 | 0.65 | 0.59 | 0.73
| PSZ-AC_6:6_UNITARY_PACKAGE_FAN | 1.34 | 1.27 | 1.28 | 1.17 | 1.12 | 1.25 | 0.91 | 1.12 | 1.28 | 0.97 | 1.14 | 1.19 | 1.14 | 1.23 | 1.17 | 1.44
| PSZ-AC_7:7_UNITARY_PACKAGE_FAN | 0.71 | 0.68 | 0.68 | 0.62 | 0.58 | 0.65 | 0.48 | 0.6 | 0.67 | 0.51 | 0.6 | 0.62 | 0.59 | 0.62 | 0.59 | 0.73
| PSZ-AC_8:8_UNITARY_PACKAGE_FAN | 0.71 | 0.68 | 0.68 | 0.62 | 0.58 | 0.65 | 0.48 | 0.6 | 0.66 | 0.5 | 0.59 | 0.62 | 0.59 | 0.62 | 0.59 | 0.73
| PSZ-AC_9:9_UNITARY_PACKAGE_FAN | 0.71 | 0.68 | 0.69 | 0.62 | 0.58 | 0.65 | 0.48 | 0.59 | 0.67 | 0.51 | 0.6 | 0.62 | 0.59 | 0.63 | 0.6 | 0.73
| PSZ-AC_10:10_UNITARY_PACKAGE_FAN | 0.7 | 0.76 | 0.84 | 0.75 | 0.64 | 0.81 | 0.53 | 0.72 | 0.78 | 0.57 | 0.68 | 0.73 | 0.78 | 0.87 | 0.81 | 1.01
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.088512 | 0.12777 | 0.11069 | 0.10383 | 0.13395 | 0.10134 | 0.15195 | 0.080117 | 0.037795 | 0.072342 | 0.053574 | 0.037839 | 0.064979 | 0.077479 | 0.062585 | 0.099798
| Total Cost ($/m2) | 12.8 | 16.5 | 13.78 | 12 | 13.97 | 11.78 | 14.63 | 8.78 | 4.02 | 6.98 | 5.64 | 3.83 | 6.8 | 7.65 | 6.11 | 9.69
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.01146 | 0.0080426 | 0.0080675 | 0.0094962 | 0.0086678 | 0.0076204 | 0.008552 | 0.0096574 | 0.0068721 | 0.0084131 | 0.0082859 | 0.0069005 | 0.0079036 | 0.0080623 | 0.0078934 | 0.0041099
| Total Cost ($/m2) | 0.01 | 0.32 | 0.39 | 0.76 | 0.24 | 0.52 | 0.71 | 1.42 | 0.85 | 1.11 | 1.63 | 1.18 | 2.42 | 2.21 | 3.17 | 3.18
Total Utility Costs
| Cost Intensity ($/m2) | 12.8 | 16.82 | 14.17 | 12.76 | 14.21 | 12.31 | 15.34 | 10.2 | 4.86 | 8.09 | 7.28 | 5.01 | 9.22 | 9.86 | 9.28 | 12.87
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 95105.5556 | 66791.6667 | 55366.6667 | 41591.6667 | 18263.8889 | 40247.2222 | 5841.6667 | 30280.5556 | 21286.1111 | 6244.4444 | 22350 | 12733.3333 | 19794.4444 | 7966.6667 | 6366.6667 | 1600
| Interior Lighting | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725
| Exterior Lighting | 16391.6667 | 16386.1111 | 16380.5556 | 16380.5556 | 16366.6667 | 16363.8889 | 16372.2222 | 16361.1111 | 16366.6667 | 16336.1111 | 16363.8889 | 16355.5556 | 16352.7778 | 16350 | 16341.6667 | 16241.6667
| Interior Equipment | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 16480.5556 | 12530.5556 | 14275 | 9333.3333 | 9177.7778 | 12275 | 4863.8889 | 8211.1111 | 10225 | 4947.2222 | 7269.4444 | 8044.4444 | 8261.1111 | 7875 | 7308.3333 | 10836.1111
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 302177.7778 | 269911.1111 | 260225 | 241505.5556 | 218011.1111 | 243086.1111 | 201280.5556 | 229055.5556 | 222080.5556 | 201730.5556 | 220186.1111 | 211336.1111 | 218611.1111 | 206394.4444 | 204216.6667 | 202880.5556
Gas (MJ)
| Heating | 1630 | 84240 | 101350 | 168050 | 57770 | 143800 | 173670 | 307320 | 257420 | 276440 | 411870 | 357980 | 641290 | 572570 | 839650 | 1619670
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1630 | 84240 | 101350 | 168050 | 57770 | 143800 | 173670 | 307320 | 257420 | 276440 | 411870 | 357980 | 641290 | 572570 | 839650 | 1619670
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 1089480 | 1055920 | 1038160 | 1037470 | 842610 | 1018910 | 898280 | 1131920 | 1056910 | 1002670 | 1204540 | 1118790 | 1428290 | 1315590 | 1574830 | 2350040
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 163.7931 | 115.0302 | 95.3538 | 71.6302 | 31.4545 | 69.3147 | 10.0607 | 52.1499 | 36.6595 | 10.7543 | 38.4917 | 21.9297 | 34.0905 | 13.7204 | 10.9648 | 2.7556
| Interior Lighting (elec) | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822
| Exterior Lighting (elec) | 28.2301 | 28.2206 | 28.211 | 28.211 | 28.1871 | 28.1823 | 28.1966 | 28.1775 | 28.1871 | 28.1344 | 28.1823 | 28.1679 | 28.1632 | 28.1584 | 28.144 | 27.9718
| Interior Equipment (elec) | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 28.3832 | 21.5804 | 24.5848 | 16.0741 | 15.8062 | 21.1403 | 8.3767 | 14.1414 | 17.6097 | 8.5202 | 12.5196 | 13.8543 | 14.2275 | 13.5625 | 12.5866 | 18.6622
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 520.4179 | 464.8475 | 448.1658 | 415.9267 | 375.464 | 418.6488 | 346.6503 | 394.4851 | 382.4725 | 347.4253 | 379.2099 | 363.9682 | 376.4974 | 355.4575 | 351.7069 | 349.4058
Gas (MJ/m2)
| Heating (gas) | 0.77978 | 40.3 | 48.4854 | 80.3944 | 27.6369 | 68.7933 | 83.083 | 147.0206 | 123.1486 | 132.2477 | 197.0368 | 171.2561 | 306.7903 | 273.915 | 401.6849 | 774.8431
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0.77978 | 40.3 | 48.4854 | 80.3944 | 27.6369 | 68.7933 | 83.083 | 147.0206 | 123.1486 | 132.2477 | 197.0368 | 171.2561 | 306.7903 | 273.915 | 401.6849 | 774.8431
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 521.2025 | 505.1475 | 496.6512 | 496.3211 | 403.101 | 487.4421 | 429.7332 | 541.5056 | 505.6211 | 479.673 | 576.2467 | 535.2243 | 683.2877 | 629.3725 | 753.3918 | 1124.2489
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 73.451 | 61.3022 | 51.1777 | 51.2931 | 54.0006 | 47.3266 | 46.132 | 46.3776 | 45.78 | 45.0969 | 46.2587 | 45.6107 | 47.0857 | 46.8985 | 47.0158 | 50.7909
| Feb | 76.8931 | 63.0445 | 54.0796 | 53.4409 | 51.5947 | 49.3109 | 52.4431 | 45.0785 | 48.9812 | 44.9212 | 45.3385 | 46.0339 | 46.2714 | 46.0129 | 46.9128 | 50.507
| Mar | 78.8645 | 67.0418 | 66.7913 | 57.3514 | 54.2638 | 51.9215 | 47.5484 | 52.3184 | 49.1506 | 48.297 | 47.084 | 49.9735 | 45.5197 | 46.6124 | 45.7231 | 45.6916
| Apr | 86.6933 | 84.3408 | 72.5035 | 67.5238 | 58.2516 | 69.72 | 53.2843 | 55.4038 | 57.2541 | 51.4336 | 51.925 | 53.3873 | 49.5823 | 45.3646 | 43.7862 | 43.889
| May | 92.7953 | 92.6896 | 91.3121 | 78.4289 | 58.3702 | 79.8288 | 53.4978 | 66.8734 | 63.6617 | 55.1439 | 62.116 | 57.3879 | 81.8304 | 52.6222 | 50.9294 | 46.2896
| Jun | 100.1688 | 93.4185 | 103.8387 | 87.1227 | 58.9792 | 98.3447 | 54.7064 | 94.1507 | 77.2684 | 58.4826 | 87.4857 | 67.9702 | 86.4882 | 71.1388 | 63.6618 | 51.8591
| Jul | 94.8516 | 100.2349 | 102.0505 | 100.0135 | 65.774 | 97.7476 | 60.2166 | 100.1099 | 82.6115 | 66.3963 | 92.4188 | 77.1146 | 95.2314 | 73.9017 | 76.0581 | 57.2297
| Aug | 100.1989 | 99.8769 | 103.3705 | 93.3354 | 73.6593 | 93.5505 | 57.2736 | 102.8301 | 80.542 | 64.0166 | 92.7745 | 78.3564 | 88.1434 | 67.0774 | 75.5674 | 51.9121
| Sep | 93.8353 | 101.4602 | 94.8155 | 84.9282 | 71.7179 | 91.6085 | 73.4216 | 81.3875 | 70.1991 | 77.9022 | 72.5899 | 68.958 | 68.4397 | 60.4267 | 58.9609 | 43.1844
| Oct | 91.9508 | 81.5019 | 72.6315 | 70.4641 | 63.7859 | 71.6767 | 55.8905 | 65.4391 | 57.6818 | 49.8517 | 55.0857 | 58.3915 | 57.9295 | 50.7822 | 53.4122 | 47.8408
| Nov | 81.3925 | 68.2534 | 61.7982 | 54.2382 | 55.5487 | 51.6175 | 48.3683 | 56.1134 | 49.396 | 48.9942 | 53.2575 | 49.3751 | 48.4367 | 45.1271 | 46.2339 | 48.5524
| Dec | 73.6608 | 62.6221 | 50.1497 | 48.6098 | 53.5027 | 49.4476 | 46.6255 | 45.3156 | 45.7182 | 45.2857 | 45.541 | 46.3888 | 46.4653 | 46.824 | 46.6313 | 50.1756
Time of Peak Electrical Demand
| Jan | 23-JAN-15:00 | 03-JAN-15:09 | 28-JAN-17:00 | 23-JAN-15:00 | 25-JAN-15:30 | 18-JAN-16:49 | 27-JAN-17:30 | 17-JAN-17:00 | 25-JAN-17:30 | 30-JAN-17:00 | 26-JAN-17:00 | 05-JAN-17:00 | 04-JAN-17:00 | 06-JAN-17:00 | 09-JAN-17:00 | 13-JAN-09:09
| Feb | 22-FEB-15:00 | 23-FEB-15:00 | 28-FEB-15:00 | 18-FEB-16:40 | 11-FEB-17:30 | 27-FEB-17:30 | 15-FEB-15:00 | 23-FEB-17:00 | 14-FEB-15:00 | 27-FEB-17:00 | 03-FEB-17:00 | 15-FEB-17:00 | 01-FEB-17:00 | 22-FEB-17:00 | 01-FEB-17:00 | 03-FEB-09:09
| Mar | 13-MAR-14:00 | 25-MAR-15:00 | 17-MAR-15:00 | 28-MAR-15:00 | 31-MAR-14:00 | 31-MAR-14:00 | 20-MAR-14:00 | 09-MAR-15:00 | 02-MAR-15:00 | 29-MAR-14:00 | 31-MAR-14:00 | 30-MAR-14:00 | 01-MAR-17:00 | 30-MAR-15:00 | 08-MAR-17:00 | 02-MAR-17:00
| Apr | 01-APR-15:00 | 29-APR-14:00 | 01-APR-15:00 | 15-APR-15:00 | 11-APR-15:00 | 21-APR-14:00 | 29-APR-14:30 | 05-APR-15:00 | 22-APR-14:39 | 29-APR-15:30 | 07-APR-14:00 | 25-APR-14:00 | 26-APR-14:00 | 14-APR-15:00 | 04-APR-15:00 | 10-APR-08:09
| May | 24-MAY-14:00 | 18-MAY-14:00 | 27-MAY-15:00 | 15-MAY-14:00 | 30-MAY-14:30 | 31-MAY-15:00 | 17-MAY-14:09 | 15-MAY-14:00 | 31-MAY-15:00 | 04-MAY-14:00 | 30-MAY-15:00 | 23-MAY-15:00 | 27-MAY-14:00 | 16-MAY-15:00 | 31-MAY-15:00 | 24-MAY-14:00
| Jun | 27-JUN-14:00 | 13-JUN-14:00 | 28-JUN-15:00 | 19-JUN-14:00 | 28-JUN-14:20 | 27-JUN-15:00 | 16-JUN-14:00 | 30-JUN-14:00 | 29-JUN-14:00 | 17-JUN-15:00 | 08-JUN-12:00 | 27-JUN-15:00 | 29-JUN-14:00 | 30-JUN-14:00 | 14-JUN-14:00 | 21-JUN-15:00
| Jul | 13-JUL-14:00 | 18-JUL-12:00 | 19-JUL-16:00 | 03-JUL-14:00 | 24-JUL-14:00 | 24-JUL-15:00 | 03-JUL-14:09 | 25-JUL-14:09 | 31-JUL-14:00 | 24-JUL-14:00 | 13-JUL-14:00 | 17-JUL-14:00 | 15-JUL-14:00 | 21-JUL-15:00 | 08-JUL-15:30 | 29-JUL-15:00
| Aug | 21-AUG-14:00 | 31-AUG-15:00 | 01-AUG-16:00 | 17-AUG-14:30 | 08-AUG-14:00 | 04-AUG-14:00 | 26-AUG-14:20 | 17-AUG-14:00 | 01-AUG-14:00 | 07-AUG-14:00 | 04-AUG-14:00 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-15:00 | 12-AUG-14:00 | 15-AUG-14:00
| Sep | 11-SEP-14:00 | 16-SEP-14:00 | 09-SEP-15:00 | 11-SEP-13:00 | 25-SEP-14:00 | 01-SEP-14:00 | 28-SEP-14:00 | 09-SEP-14:00 | 02-SEP-15:20 | 02-SEP-15:00 | 05-SEP-14:00 | 02-SEP-15:09 | 14-SEP-14:00 | 02-SEP-15:50 | 07-SEP-14:00 | 02-SEP-15:00
| Oct | 06-OCT-14:00 | 06-OCT-15:00 | 02-OCT-15:00 | 12-OCT-15:00 | 05-OCT-14:30 | 03-OCT-14:00 | 13-OCT-14:00 | 12-OCT-14:00 | 13-OCT-14:00 | 17-OCT-14:00 | 05-OCT-14:09 | 05-OCT-14:00 | 07-OCT-15:09 | 06-OCT-15:00 | 07-OCT-14:00 | 27-OCT-08:09
| Nov | 07-NOV-15:09 | 01-NOV-15:00 | 13-NOV-15:00 | 22-NOV-15:30 | 20-NOV-15:09 | 09-NOV-16:40 | 14-NOV-16:00 | 04-NOV-14:20 | 08-NOV-17:10 | 04-NOV-16:49 | 02-NOV-16:49 | 04-NOV-16:00 | 02-NOV-16:00 | 27-NOV-17:00 | 24-NOV-17:00 | 09-NOV-09:09
| Dec | 15-DEC-15:00 | 19-DEC-15:39 | 09-DEC-17:19 | 01-DEC-15:00 | 19-DEC-12:00 | 05-DEC-16:30 | 07-DEC-16:49 | 14-DEC-17:19 | 09-DEC-16:49 | 13-DEC-17:00 | 14-DEC-17:00 | 01-DEC-17:00 | 30-DEC-17:00 | 11-DEC-17:00 | 30-DEC-17:00 | 29-DEC-09:09
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emissions
| Carbon Equivalent (kg) | 82901.9194 | 91550.5819 | 80383.4647 | 77423.2298 | 26519.867 | 84580.3346 | 26654.4636 | 67353.8457 | 95361.3795 | 19677.7864 | 124818.7765 | 92785.6157 | 86393.4032 | 85748.9644 | 85043.032 | 86294.9255
| CO2 (kg) | 191980.7398 | 230303.7461 | 190019.9577 | 177597.3745 | 71032.0961 | 201679.7365 | 71849.9162 | 154626.9523 | 224796.5431 | 49305.0397 | 292312.8443 | 219808.7056 | 205921.9894 | 205257.2492 | 204897.1187 | 227390.9263
| NOX (kg) | 338.5055 | 300.929 | 317.0339 | 333.9824 | 60.9443 | 325.2557 | 61.9587 | 291.6849 | 383.0592 | 69.1549 | 512.6788 | 369.8716 | 345.1336 | 338.481 | 333.787 | 255.7697
| SO2 (kg) | 1293.447 | 1287.4947 | 1046.4489 | 847.7326 | 634.4032 | 1337.2124 | 585.7456 | 836.2287 | 969.8505 | 155.9953 | 1483.9823 | 922.9563 | 516.1299 | 551.2492 | 482.208 | 1033.1743
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0059 | 0.0036 | 0.0028 | 0.0031 | 0.0003 | 0.0025 | 0.0003 | 0.0034 | 0.0038 | 0.0006 | 0.0045 | 0.0036 | 0.0038 | 0.0039 | 0.0036 | 0.0037
| Water for Electricity (m3) | 160.0817 | 439.1757 | 7729.86 | 1507.87 | 3827.8 | 6668.85 | 3534.02 | 52.0043 | 1008.42 | 2061.04 | 341.6041 | 959.6325 | 339.1626 | 13073.8 | 316.8292 | 207.2784

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1089.48 | 521.2 | 521.2
Net Site Energy | 1089.48 | 521.2 | 521.2
Total Source Energy | 3610.16 | 1727.09 | 1727.09
Net Source Energy | 3610.16 | 1727.09 | 1727.09
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1.63 | 0 | 0 | 0 | 0
Cooling | 342.38 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 59.01 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 59.33 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1087.84 | 1.63 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 23.99 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 23.99 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 13.77 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 13.77 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_2 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
LGSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.9 | 3.9 | 6.49 | 0.25 | 0.25 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.9 | 3.9 | 6.49 | 0.25 | 0.25 | No | LGSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW_SOUTH | 3.9 | 3.9 | 6.49 | 0.25 | 0.25 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 6.49 | 0.25 | 0.25 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 6.49 | 0.25 | 0.25 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 6.49 | 0.25 | 0.25 | No | SMSTORE4_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.88 | 3.88 | 6.49 | 0.25 | 0.25 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.88 | 3.88 | 6.49 | 0.25 | 0.25 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 6.49 | 0.25 | 0.25 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 6.49 | 0.25 | 0.25 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 6.49 | 0.25 | 0.25 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 6.49 | 0.25 | 0.25 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 6.49 | 0.25 | 0.25
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 6.49 | 0.25 | 0.25
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 41923.81 | 28343.98 | 13579.82 | 0.68 | 3.19
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 22681.19 | 15334.37 | 7346.82 | 0.68 | 3.45
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20376.85 | 13776.44 | 6600.4 | 0.68 | 3.45
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20009.22 | 13527.9 | 6481.32 | 0.68 | 3.45
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19740.98 | 13346.55 | 6394.43 | 0.68 | 3.45
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 33168.56 | 22424.71 | 10743.85 | 0.68 | 3.45
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17717.97 | 11978.82 | 5739.15 | 0.68 | 3.65
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17645.26 | 11929.66 | 5715.6 | 0.68 | 3.65
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17605.89 | 11903.05 | 5702.84 | 0.68 | 3.65
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17317.98 | 11708.39 | 5609.58 | 0.68 | 3.67
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20232.16 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10116.08 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10116.08 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10116.08 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10116.08 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20232.16 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10116.08 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10116.08 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10116.08 | 0.8
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10116.08 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.69 | 1846.34 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.91 | 1040.51 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.82 | 934.79 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.81 | 917.93 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.79 | 905.62 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.34 | 1521.62 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.71 | 812.82 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.71 | 809.48 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.71 | 807.68 | 1 | Unitary Fans
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.7 | 808.91 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 13649.2542 | 24.0179 | 91.5763 | 0 | 0.0004 | 11333.7732 | 5889.1897
February | 12713.1714 | 22.4121 | 85.6211 | 0 | 0.0004 | 10596.7713 | 5489.4422
March | 14709.2798 | 25.9335 | 99.0837 | 0 | 0.0005 | 12262.9612 | 6351.5899
April | 15204.7216 | 26.8151 | 102.4853 | 0 | 0.0005 | 12683.9615 | 6566.3435
May | 17186.5383 | 30.3103 | 115.8435 | 0 | 0.0005 | 14337.2168 | 7422.2152
June | 17831.0608 | 31.447 | 120.1878 | 0 | 0.0005 | 14874.8852 | 7700.56
July | 18752.4316 | 33.0719 | 126.3982 | 0 | 0.0006 | 15643.5038 | 8098.4652
August | 19172.2286 | 33.8122 | 129.2278 | 0 | 0.0006 | 15993.7035 | 8279.7596
September | 17598.7715 | 31.0373 | 118.6221 | 0 | 0.0005 | 14681.1067 | 7600.2431
October | 16747.9233 | 29.5367 | 112.8871 | 0 | 0.0005 | 13971.3189 | 7232.7939
November | 14690.9417 | 25.909 | 99.0223 | 0 | 0.0005 | 12255.3601 | 6344.4614
December | 13724.4171 | 24.2025 | 92.4918 | 0 | 0.0004 | 11447.1241 | 5926.8557
Annual Sum or Average | 191980.7398 | 338.5055 | 1293.447 | 0 | 0.0059 | 160081.6863 | 82901.9194
Minimum of Months | 12713.1714 | 22.4121 | 85.6211 | 0 | 0.0004 | 10596.7713 | 5489.4422
Maximum of Months | 19172.2286 | 33.8122 | 129.2278 | 0 | 0.0006 | 15993.7035 | 8279.7596
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 77019300000 | 73451.022 | 23-JAN-15:00 | 32837.857 | 8089.532 | 4885.02 | 0 | 27638.613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 72010900000 | 76893.149 | 22-FEB-15:00 | 32837.857 | 8089.532 | 5314.045 | 0 | 30651.715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 83333600000 | 78864.491 | 13-MAR-14:00 | 32837.857 | 8089.532 | 5494.569 | 0 | 32442.533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 86194600000 | 86693.302 | 01-APR-15:00 | 32837.857 | 8089.532 | 6590.646 | 0 | 39175.266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 97429400000 | 92795.336 | 24-MAY-14:00 | 32837.857 | 8089.532 | 7156.099 | 0 | 44711.848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 101083000000 | 100168.836 | 27-JUN-14:00 | 32837.857 | 8089.532 | 8285.682 | 0 | 50955.764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 106306000000 | 94851.596 | 13-JUL-14:00 | 32837.857 | 8089.532 | 7574.1 | 0 | 46350.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 108686000000 | 100198.895 | 21-AUG-14:00 | 32837.857 | 8089.532 | 8183.513 | 0 | 51087.992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 99766300000 | 93835.283 | 11-SEP-14:00 | 32837.857 | 8089.532 | 7429.411 | 0 | 45478.483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 94942900000 | 91950.774 | 06-OCT-14:00 | 32837.857 | 8089.532 | 7281.495 | 0 | 43741.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 83282000000 | 81392.536 | 07-NOV-15:09 | 32837.857 | 8089.532 | 5913.943 | 0 | 34551.204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 77789600000 | 73660.782 | 15-DEC-15:00 | 32837.857 | 8089.532 | 4881.778 | 0 | 27851.614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1087840000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 72010900000 | 73451.022 |  | 32837.857 | 8089.532 | 4881.778 | 0 | 27638.613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 108686000000 | 100198.895 |  | 32837.857 | 8089.532 | 8285.682 | 0 | 51087.992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 26746.38 | 18.68 | 0 | 26765.06
Cost per Total Building Area ($/m2) | 12.8 | 0.01 | 0 | 12.8
Cost per Net Conditioned Building Area ($/m2) | 12.8 | 0.01 | 0 | 12.8

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1055.92 | 505.15 | 505.15
Net Site Energy | 1055.92 | 505.15 | 505.15
Total Source Energy | 91.99 | 44.01 | 44.01
Net Source Energy | 91.99 | 44.01 | 44.01
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 84.24 | 0 | 0 | 0 | 0
Cooling | 240.45 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.99 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 45.11 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 971.68 | 84.24 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 23.99 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 23.99 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 13.77 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 13.77 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_2 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
LGSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.9 | 3.9 | 6.49 | 0.25 | 0.25 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.9 | 3.9 | 6.49 | 0.25 | 0.25 | No | LGSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW_SOUTH | 3.9 | 3.9 | 6.49 | 0.25 | 0.25 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 6.49 | 0.25 | 0.25 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 6.49 | 0.25 | 0.25 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 6.49 | 0.25 | 0.25 | No | SMSTORE4_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.88 | 3.88 | 6.49 | 0.25 | 0.25 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.88 | 3.88 | 6.49 | 0.25 | 0.25 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 6.49 | 0.25 | 0.25 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 6.49 | 0.25 | 0.25 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 6.49 | 0.25 | 0.25 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 6.49 | 0.25 | 0.25 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 6.49 | 0.25 | 0.25
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 6.49 | 0.25 | 0.25
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 40172.92 | 27160.24 | 13012.68 | 0.68 | 3.19
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 21836.4 | 14763.22 | 7073.17 | 0.68 | 3.45
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19542.13 | 13212.1 | 6330.02 | 0.68 | 3.45
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19177.59 | 12965.65 | 6211.94 | 0.68 | 3.45
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18909.67 | 12784.51 | 6125.16 | 0.68 | 3.65
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 31638.06 | 21389.96 | 10248.1 | 0.68 | 3.45
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16895.75 | 11422.93 | 5472.82 | 0.68 | 3.66
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16824.24 | 11374.58 | 5449.65 | 0.68 | 3.67
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16775.05 | 11341.33 | 5433.72 | 0.68 | 3.67
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18947.97 | 12810.4 | 6137.56 | 0.68 | 3.65
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 30554.3 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13992.76 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13933.91 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13931.09 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13943.36 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 27639.81 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13943.68 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13936.21 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 14017.91 | 0.8
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 16810.61 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.62 | 1769.23 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.88 | 1001.75 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.79 | 896.5 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.77 | 879.78 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.76 | 867.49 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.27 | 1451.41 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.68 | 789.19 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.68 | 785.85 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.68 | 783.55 | 1 | Unitary Fans
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.76 | 869.24 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 16001.4067 | 20.4771 | 83.4143 | 0 | 0.0002 | 28451.4523 | 6305.3045
February | 14297.9526 | 18.3192 | 74.8418 | 0 | 0.0002 | 25527.6015 | 5636.8938
March | 15956.705 | 20.8017 | 88.5277 | 0 | 0.0002 | 30197.3582 | 6336.8952
April | 17254.5616 | 22.6654 | 98.134 | 0 | 0.0003 | 33474.9067 | 6874.4557
May | 20937.3105 | 27.5196 | 119.3126 | 0 | 0.0003 | 40699.2763 | 8343.8598
June | 23299.8241 | 30.6255 | 132.7839 | 0 | 0.0004 | 45294.5574 | 9285.4376
July | 25135.9836 | 33.039 | 143.2481 | 0 | 0.0004 | 48864.0277 | 10017.1832
August | 25085.2361 | 32.9723 | 142.9589 | 0 | 0.0004 | 48765.3753 | 9996.9593
September | 21699.8588 | 28.5225 | 123.6659 | 0 | 0.0003 | 42184.2455 | 8647.82
October | 19286.4387 | 25.3427 | 109.8063 | 0 | 0.0003 | 37456.5141 | 7685.0522
November | 15799.2279 | 20.669 | 88.6716 | 0 | 0.0002 | 30246.7751 | 6283.7217
December | 15549.2406 | 19.9751 | 82.1295 | 0 | 0.0002 | 28013.5866 | 6136.9988
Annual Sum or Average | 230303.7461 | 300.929 | 1287.4947 | 0 | 0.0036 | 439175.6768 | 91550.5819
Minimum of Months | 14297.9526 | 18.3192 | 74.8418 | 0 | 0.0002 | 25527.6015 | 5636.8938
Maximum of Months | 25135.9836 | 33.039 | 143.2481 | 0 | 0.0004 | 48864.0277 | 10017.1832
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 62948900000 | 61302.213 | 03-JAN-15:09 | 32837.857 | 8089.532 | 3050.543 | 0 | 17324.281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 56479900000 | 63044.502 | 23-FEB-15:00 | 32837.857 | 8089.532 | 3262.822 | 0 | 18854.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 66811700000 | 67041.824 | 25-MAR-15:00 | 32837.857 | 8089.532 | 3872.351 | 0 | 22242.084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 74063300000 | 84340.774 | 29-APR-14:00 | 32837.857 | 8089.532 | 6212.123 | 0 | 37201.262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 90047200000 | 92689.648 | 18-MAY-14:00 | 32837.857 | 8089.532 | 7227.729 | 0 | 44534.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 100214000000 | 93418.533 | 13-JUN-14:00 | 32837.857 | 8089.532 | 7152.44 | 0 | 45338.703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 108112000000 | 100234.931 | 18-JUL-12:00 | 32837.857 | 8089.532 | 8210.805 | 0 | 51096.736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 107893000000 | 99876.923 | 31-AUG-15:00 | 32837.857 | 8089.532 | 8082.493 | 0 | 50867.041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 93332700000 | 101460.189 | 16-SEP-14:00 | 32837.857 | 8089.532 | 8575.124 | 0 | 51957.675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 82872600000 | 81501.867 | 06-OCT-15:00 | 32837.857 | 8089.532 | 5756.242 | 0 | 34818.235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 66921000000 | 68253.356 | 01-NOV-15:00 | 32837.857 | 8089.532 | 4119.834 | 0 | 23206.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 61980100000 | 62622.107 | 19-DEC-15:39 | 32837.857 | 8089.532 | 3225.386 | 0 | 18469.332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 971677000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 56479900000 | 61302.213 |  | 32837.857 | 8089.532 | 3050.543 | 0 | 17324.281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 108112000000 | 101460.189 |  | 32837.857 | 8089.532 | 8575.124 | 0 | 51957.675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 34485.23 | 677.51 | 0 | 35162.74
Cost per Total Building Area ($/m2) | 16.5 | 0.32 | 0 | 16.82
Cost per Net Conditioned Building Area ($/m2) | 16.5 | 0.32 | 0 | 16.82

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1038.16 | 496.65 | 496.65
Net Site Energy | 1038.16 | 496.65 | 496.65
Total Source Energy | 3073.81 | 1470.5 | 1470.5
Net Source Energy | 3073.81 | 1470.5 | 1470.5
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 101.35 | 0 | 0 | 0 | 0
Cooling | 199.32 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.97 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 51.39 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 936.81 | 101.35 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 23.99 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 23.99 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 13.77 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 13.77 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_2 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
LGSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.9 | 3.9 | 6.49 | 0.25 | 0.25 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.9 | 3.9 | 6.49 | 0.25 | 0.25 | No | LGSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW_SOUTH | 3.9 | 3.9 | 6.49 | 0.25 | 0.25 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 6.49 | 0.25 | 0.25 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 6.49 | 0.25 | 0.25 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 6.49 | 0.25 | 0.25 | No | SMSTORE4_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.88 | 3.88 | 6.49 | 0.25 | 0.25 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.88 | 3.88 | 6.49 | 0.25 | 0.25 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 6.49 | 0.25 | 0.25 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 6.49 | 0.25 | 0.25 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 6.49 | 0.25 | 0.25 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.25 | 0.25 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 6.49 | 0.25 | 0.25 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 6.49 | 0.25 | 0.25
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 6.49 | 0.25 | 0.25
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 31204.39 | 23865.14 | 7339.25 | 0.76 | 3.65
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16473.63 | 12512.42 | 3961.21 | 0.76 | 3.9
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14981.6 | 11281.05 | 3700.55 | 0.75 | 3.88
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14734.78 | 11077.74 | 3657.04 | 0.75 | 3.88
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14557.94 | 10932.61 | 3625.32 | 0.75 | 3.88
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 25148.61 | 18655.5 | 6493.11 | 0.74 | 3.62
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13213.3 | 9853.99 | 3359.32 | 0.75 | 3.87
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13180.41 | 9827.97 | 3352.44 | 0.75 | 3.87
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13274.28 | 9902.26 | 3372.03 | 0.75 | 3.88
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18574.94 | 13147.57 | 5427.37 | 0.71 | 3.74
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 24690.43 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11407.79 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11357.96 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11355.75 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11368.71 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 22534.44 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11368.96 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11359.79 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11424.82 | 0.8
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13551.61 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.71 | 1871.72 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.89 | 1013.09 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.79 | 902.97 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.78 | 884.82 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.77 | 871.92 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.28 | 1463.1 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.68 | 792.66 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.68 | 790.4 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.69 | 796.85 | 1 | Unitary Fans
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.84 | 962.45 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 13500.5074 | 21.6731 | 68.1885 | 0 | 0.0002 | 503649.5208 | 5624.9713
February | 12272.5423 | 19.6998 | 61.9721 | 0 | 0.0002 | 457733.7416 | 5113.1419
March | 13835.2497 | 23.0998 | 76.3125 | 0 | 0.0002 | 563702.5688 | 5854.3691
April | 14297.3325 | 24.1117 | 80.6003 | 0 | 0.0002 | 595387.5989 | 6074.2084
May | 16401.8376 | 27.7196 | 92.8895 | 0 | 0.0003 | 686169.8526 | 6974.2492
June | 19501.0423 | 32.9599 | 110.4598 | 0 | 0.0003 | 815960.5933 | 8292.3231
July | 20364.1592 | 34.4187 | 115.3487 | 0 | 0.0003 | 852075.0424 | 8659.3416
August | 20327.5165 | 34.3568 | 115.1412 | 0 | 0.0003 | 850541.8408 | 8643.7602
September | 17954.9558 | 30.3468 | 101.7023 | 0 | 0.0003 | 751269.4034 | 7634.8891
October | 15108.0738 | 25.5127 | 85.4143 | 0 | 0.0002 | 630950.1816 | 6422.0555
November | 12795.6806 | 21.3056 | 70.155 | 0 | 0.0002 | 518215.9582 | 5408.5582
December | 13661.0601 | 21.8293 | 68.2649 | 0 | 0.0002 | 504207.8823 | 5681.5971
Annual Sum or Average | 190019.9577 | 317.0339 | 1046.4489 | 0 | 0.0028 | 7729860 | 80383.4647
Minimum of Months | 12272.5423 | 19.6998 | 61.9721 | 0 | 0.0002 | 457733.7416 | 5113.1419
Maximum of Months | 20364.1592 | 34.4187 | 115.3487 | 0 | 0.0003 | 852075.0424 | 8659.3416
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 61039400000 | 51177.72 | 28-JAN-17:00 | 32837.857 | 8089.532 | 1396.74 | 0 | 5103.636 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 55474700000 | 54079.632 | 28-FEB-15:00 | 32837.857 | 8089.532 | 2691.038 | 0 | 10461.205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 68317500000 | 66791.321 | 17-MAR-15:00 | 32837.857 | 8089.532 | 4963.862 | 0 | 20900.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 72157500000 | 72503.464 | 01-APR-15:00 | 32837.857 | 8089.532 | 5932.544 | 0 | 25643.531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 83159800000 | 91312.137 | 27-MAY-15:00 | 32837.857 | 8089.532 | 8894.968 | 0 | 41489.779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 98889700000 | 103838.749 | 28-JUN-15:00 | 32837.857 | 8089.532 | 10334.16 | 0 | 52577.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 103267000000 | 102050.508 | 19-JUL-16:00 | 32837.857 | 8089.532 | 10058.514 | 0 | 51064.605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 103081000000 | 103370.494 | 01-AUG-16:00 | 32837.857 | 8089.532 | 10277.214 | 0 | 52165.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 91049500000 | 94815.488 | 09-SEP-15:00 | 32837.857 | 8089.532 | 9261.533 | 0 | 44626.566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 76467500000 | 72631.521 | 02-OCT-15:00 | 32837.857 | 8089.532 | 6019.995 | 0 | 25684.137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 62804800000 | 61798.208 | 13-NOV-15:00 | 32837.857 | 8089.532 | 4094.599 | 0 | 16776.219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 61107100000 | 50149.743 | 09-DEC-17:19 | 32837.857 | 8089.532 | 1197.13 | 0 | 4275.27 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 936814000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 55474700000 | 50149.743 |  | 32837.857 | 8089.532 | 1197.13 | 0 | 4275.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 103267000000 | 103838.749 |  | 32837.857 | 8089.532 | 10334.16 | 0 | 52577.2 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 28805.21 | 817.64 | 0 | 29622.85
Cost per Total Building Area ($/m2) | 13.78 | 0.39 | 0 | 14.17
Cost per Net Conditioned Building Area ($/m2) | 13.78 | 0.39 | 0 | 14.17

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1037.47 | 496.32 | 496.32
Net Site Energy | 1037.47 | 496.32 | 496.32
Total Source Energy | 3108.25 | 1486.97 | 1486.97
Net Source Energy | 3108.25 | 1486.97 | 1486.97
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 168.05 | 0 | 0 | 0 | 0
Cooling | 149.73 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.97 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 33.6 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 869.42 | 168.05 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 23.99 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 23.99 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 13.77 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 13.77 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_2 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
LGSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.9 | 3.9 | 3.18 | 0.402 | 0.495 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.9 | 3.9 | 3.18 | 0.402 | 0.495 | No | LGSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW_SOUTH | 3.9 | 3.9 | 3.18 | 0.402 | 0.495 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE4_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 3.18 | 0.402 | 0.495
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 39805.51 | 27612.64 | 12192.87 | 0.69 | 3.23
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20081.92 | 13651.34 | 6430.58 | 0.68 | 3.46
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18121.5 | 12251.64 | 5869.86 | 0.68 | 3.65
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17759.82 | 12007.12 | 5752.7 | 0.68 | 3.66
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17491.18 | 11825.49 | 5665.69 | 0.68 | 3.66
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 28937.79 | 19564.35 | 9373.44 | 0.68 | 3.45
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15507.57 | 10484.41 | 5023.16 | 0.68 | 3.66
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15435.81 | 10435.89 | 4999.92 | 0.68 | 3.66
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15367.18 | 10389.5 | 4977.69 | 0.68 | 3.67
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18647.02 | 12606.94 | 6040.08 | 0.68 | 3.65
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 35722.96 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 16308.94 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 16240.94 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 16237.74 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 16251.77 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 32225.95 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 16252.12 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 16243.61 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 16339.58 | 0.8
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 19693.81 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.72 | 1878.98 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.82 | 935.17 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.73 | 831.33 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.72 | 814.74 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.7 | 817 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.17 | 1327.53 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.62 | 724.35 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.62 | 721 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.62 | 717.79 | 1 | Unitary Fans
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.75 | 855.44 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 14204.8699 | 24.9415 | 59.1202 | 0 | 0.0002 | 105141.0232 | 6028.9747
February | 12640.0079 | 22.4384 | 53.8062 | 0 | 0.0002 | 95693.0081 | 5387.3861
March | 13126.3814 | 24.4055 | 61.2866 | 0 | 0.0002 | 109008.4399 | 5696.6095
April | 12839.1029 | 24.3581 | 62.3316 | 0 | 0.0002 | 110871.7627 | 5616.8919
May | 15045.5547 | 29.0504 | 75.5254 | 0 | 0.0003 | 134344.7564 | 6628.9343
June | 16852.2115 | 32.5416 | 84.6082 | 0 | 0.0003 | 150501.2691 | 7425.1901
July | 18313.0284 | 35.3624 | 91.9423 | 0 | 0.0003 | 163547.3192 | 8068.8352
August | 18695.2085 | 36.1004 | 93.8611 | 0 | 0.0003 | 166960.4377 | 8237.2262
September | 16494.2334 | 31.8503 | 82.8109 | 0 | 0.0003 | 147304.2913 | 7267.4628
October | 13381.4675 | 25.605 | 66.0327 | 0 | 0.0002 | 117457.0848 | 5874.2883
November | 12418.4923 | 23.0187 | 57.6353 | 0 | 0.0002 | 102513.2864 | 5382.8762
December | 13586.8162 | 24.31 | 58.772 | 0 | 0.0002 | 104526.5615 | 5808.5544
Annual Sum or Average | 177597.3745 | 333.9824 | 847.7326 | 0 | 0.0031 | 1507870 | 77423.2298
Minimum of Months | 12418.4923 | 22.4384 | 53.8062 | 0 | 0.0002 | 95693.0081 | 5382.8762
Maximum of Months | 18695.2085 | 36.1004 | 93.8611 | 0 | 0.0003 | 166960.4377 | 8237.2262
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 60623300000 | 51293.064 | 23-JAN-15:00 | 32837.857 | 8089.532 | 1748.064 | 0 | 8617.611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 55175700000 | 53440.924 | 18-FEB-16:40 | 32837.857 | 8089.532 | 2085.322 | 0 | 10428.213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 62853200000 | 57351.415 | 28-MAR-15:00 | 32837.857 | 8089.532 | 2644.829 | 0 | 13779.196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 63927600000 | 67523.842 | 15-APR-15:00 | 32837.857 | 8089.532 | 3981.22 | 0 | 22615.233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 77461900000 | 78428.91 | 15-MAY-14:00 | 32837.857 | 8089.532 | 5561.892 | 0 | 31939.629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 86777600000 | 87122.704 | 19-JUN-14:00 | 32837.857 | 8089.532 | 6553.339 | 0 | 39641.975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 94299800000 | 100013.505 | 03-JUL-14:00 | 32837.857 | 8089.532 | 8144.156 | 0 | 50941.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 96267800000 | 93335.449 | 17-AUG-14:30 | 32837.857 | 8089.532 | 7477.153 | 0 | 44930.906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 84934300000 | 84928.183 | 11-SEP-13:00 | 32837.857 | 8089.532 | 6502.749 | 0 | 37498.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 67724600000 | 70464.108 | 12-OCT-15:00 | 32837.857 | 8089.532 | 4305.428 | 0 | 25231.291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 59108200000 | 54238.198 | 22-NOV-15:30 | 32837.857 | 8089.532 | 2162.162 | 0 | 11148.646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 60269000000 | 48609.798 | 01-DEC-15:00 | 32837.857 | 8089.532 | 1315.117 | 0 | 6367.291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 869423000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 55175700000 | 48609.798 |  | 32837.857 | 8089.532 | 1315.117 | 0 | 6367.291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 96267800000 | 100013.505 |  | 32837.857 | 8089.532 | 8144.156 | 0 | 50941.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 25075.17 | 1595.84 | 0 | 26671.01
Cost per Total Building Area ($/m2) | 12 | 0.76 | 0 | 12.76
Cost per Net Conditioned Building Area ($/m2) | 12 | 0.76 | 0 | 12.76

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 842.61 | 403.1 | 403.1
Net Site Energy | 842.61 | 403.1 | 403.1
Total Source Energy | 2492.17 | 1192.24 | 1192.24
Net Source Energy | 2492.17 | 1192.24 | 1192.24
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 57.77 | 0 | 0 | 0 | 0
Cooling | 65.75 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.92 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 33.04 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 784.84 | 57.77 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 23.99 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 23.99 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 13.77 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 13.77 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_2 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
LGSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.9 | 3.9 | 3.18 | 0.402 | 0.495 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.9 | 3.9 | 3.18 | 0.402 | 0.495 | No | LGSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW_SOUTH | 3.9 | 3.9 | 3.18 | 0.402 | 0.495 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE4_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 3.18 | 0.402 | 0.495
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 25367.02 | 20259.51 | 5107.52 | 0.8 | 3.74
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12183.55 | 9645.68 | 2537.87 | 0.79 | 4
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10792.1 | 8522.67 | 2269.43 | 0.79 | 4.03
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10569.66 | 8343.35 | 2226.31 | 0.79 | 4.02
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10396.71 | 8205.08 | 2191.64 | 0.79 | 4.02
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19244.58 | 15081.63 | 4162.95 | 0.78 | 3.75
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 9992.56 | 7854.34 | 2138.22 | 0.79 | 4
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 9954.61 | 7822.58 | 2132.03 | 0.79 | 4.01
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 9997.44 | 7858.48 | 2138.96 | 0.79 | 4
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10872.56 | 8601.09 | 2271.47 | 0.79 | 4.02
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21042.31 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10521.16 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10521.16 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10521.16 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10521.16 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21042.31 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10521.16 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10521.16 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10521.16 | 0.8
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10545.49 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.53 | 1675.9 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.72 | 822.59 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.64 | 737.81 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.62 | 721.91 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.61 | 709.76 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.12 | 1270.45 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.58 | 676.11 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.58 | 673.18 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.58 | 676.5 | 1 | Unitary Fans
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.64 | 746.15 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 5969.4341 | 5.1436 | 49.3911 | 0 | 0 | 297997.3036 | 2216.7215
February | 5343.9084 | 4.6018 | 44.7154 | 0 | 0 | 269788.8661 | 1985.9607
March | 5946.3347 | 5.1141 | 50.913 | 0 | 0 | 307185.7175 | 2213.3699
April | 5518.9729 | 4.7398 | 48.4637 | 0 | 0 | 292412.5963 | 2057.9868
May | 5683.9011 | 4.8712 | 51.7543 | 0 | 0 | 312273.3656 | 2125.1082
June | 5638.1163 | 4.8267 | 52.2763 | 0 | 0 | 315425.9096 | 2110.8544
July | 6304.6266 | 5.3953 | 58.798 | 0 | 0 | 354777.9004 | 2361.4322
August | 6885.7678 | 5.8927 | 64.2179 | 0 | 0 | 387480.7542 | 2579.1021
September | 6364.5107 | 5.4466 | 59.3566 | 0 | 0 | 358148.2085 | 2383.8624
October | 5974.7745 | 5.1138 | 55.588 | 0 | 0 | 335408.6267 | 2237.4762
November | 5531.3718 | 4.7465 | 49.2853 | 0 | 0 | 297371.8348 | 2064.7845
December | 5870.3772 | 5.0522 | 49.6436 | 0 | 0 | 299524.7698 | 2183.2081
Annual Sum or Average | 71032.0961 | 60.9443 | 634.4032 | 0 | 0.0003 | 3827800 | 26519.867
Minimum of Months | 5343.9084 | 4.6018 | 44.7154 | 0 | 0 | 269788.8661 | 1985.9607
Maximum of Months | 6885.7678 | 5.8927 | 64.2179 | 0 | 0 | 387480.7542 | 2579.1021
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 61100600000 | 54000.598 | 25-JAN-15:30 | 32837.857 | 8089.532 | 3092.511 | 0 | 9980.698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 55316900000 | 51594.717 | 11-FEB-17:30 | 32837.857 | 8089.532 | 3729.188 | 0 | 3188.186 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 62984600000 | 54263.847 | 31-MAR-14:00 | 32837.857 | 8089.532 | 3259.146 | 0 | 10077.312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 59955600000 | 58251.621 | 11-APR-15:00 | 32837.857 | 8089.532 | 3895.224 | 0 | 13429.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 64027800000 | 58370.186 | 30-MAY-14:30 | 32837.857 | 8089.532 | 4086.55 | 0 | 13356.247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 64674200000 | 58979.156 | 28-JUN-14:20 | 32837.857 | 8089.532 | 4211.834 | 0 | 13839.933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 72742800000 | 65774.038 | 24-JUL-14:00 | 32837.857 | 8089.532 | 5764.276 | 0 | 19082.372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 79448100000 | 73659.324 | 08-AUG-14:00 | 32837.857 | 8089.532 | 7381.596 | 0 | 25350.338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 73433800000 | 71717.885 | 25-SEP-14:00 | 32837.857 | 8089.532 | 6928.17 | 0 | 23862.325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 68771400000 | 63785.896 | 05-OCT-14:30 | 32837.857 | 8089.532 | 5308.121 | 0 | 17550.386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 60972400000 | 55548.728 | 20-NOV-15:09 | 32837.857 | 8089.532 | 3462.598 | 0 | 11158.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 61413800000 | 53502.681 | 19-DEC-12:00 | 32837.857 | 8089.532 | 2895.894 | 0 | 9679.398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 784842000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 55316900000 | 51594.717 |  | 32837.857 | 8089.532 | 2895.894 | 0 | 3188.186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 79448100000 | 73659.324 |  | 32837.857 | 8089.532 | 7381.596 | 0 | 25350.338 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 29201.77 | 500.74 | 0 | 29702.51
Cost per Total Building Area ($/m2) | 13.97 | 0.24 | 0 | 14.21
Cost per Net Conditioned Building Area ($/m2) | 13.97 | 0.24 | 0 | 14.21

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1018.91 | 487.44 | 487.44
Net Site Energy | 1018.91 | 487.44 | 487.44
Total Source Energy | 3287.31 | 1572.64 | 1572.64
Net Source Energy | 3287.31 | 1572.64 | 1572.64
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 143.8 | 0 | 0 | 0 | 0
Cooling | 144.89 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.91 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 44.19 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 875.11 | 143.8 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 23.99 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 23.99 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 13.77 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 13.77 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_2 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
LGSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.9 | 3.9 | 3.18 | 0.402 | 0.495 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.9 | 3.9 | 3.18 | 0.402 | 0.495 | No | LGSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW_SOUTH | 3.9 | 3.9 | 3.18 | 0.402 | 0.495 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE4_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 3.18 | 0.402 | 0.495
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 34091.28 | 25623.44 | 8467.84 | 0.75 | 3.62
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12985.99 | 10371.33 | 2614.66 | 0.8 | 4.02
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 11405.21 | 9108.83 | 2296.38 | 0.8 | 4.06
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 11142.7 | 8899.17 | 2243.52 | 0.8 | 4.05
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10951.82 | 8746.73 | 2205.09 | 0.8 | 4.05
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 26523.86 | 19057.57 | 7466.29 | 0.72 | 3.56
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13650.03 | 9839.48 | 3810.56 | 0.72 | 3.8
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13614.03 | 9810.62 | 3803.41 | 0.72 | 3.8
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13729.76 | 9903.42 | 3826.33 | 0.72 | 3.79
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16122.14 | 11871.17 | 4250.97 | 0.74 | 3.83
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 29520.47 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13579.92 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13521 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13518.4 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13533.15 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 26769.49 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13533.43 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13523.15 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13601.48 | 0.8
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 16226.91 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.8 | 1964.09 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.78 | 893.68 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.69 | 799.16 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.67 | 780.77 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.66 | 767.39 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.25 | 1427.42 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.65 | 754.02 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.65 | 751.48 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.65 | 759.66 | 1 | Unitary Fans
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.81 | 921.41 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 15574.8143 | 23.9996 | 92.7547 | 0 | 0.0002 | 462539.3295 | 6415.5135
February | 13253.7739 | 20.9271 | 83.6691 | 0 | 0.0002 | 417252.2836 | 5511.8233
March | 15037.9872 | 23.7745 | 95.2173 | 0 | 0.0002 | 474843.7004 | 6256.9697
April | 14743.2583 | 24.0368 | 100.196 | 0 | 0.0002 | 499700.0514 | 6210.0305
May | 16616.8809 | 27.2157 | 114.0962 | 0 | 0.0002 | 569027.9397 | 7012.1264
June | 20097.7974 | 32.9587 | 138.3911 | 0 | 0.0003 | 690194.4698 | 8485.3879
July | 21281.6431 | 34.9004 | 146.5451 | 0 | 0.0003 | 730860.4401 | 8985.2368
August | 21710.3425 | 35.6034 | 149.4971 | 0 | 0.0003 | 745582.9629 | 9166.2363
September | 18569.8896 | 30.4533 | 127.8719 | 0 | 0.0002 | 637732.0635 | 7840.3171
October | 15641.1208 | 25.5579 | 106.8362 | 0 | 0.0002 | 532817.9789 | 6594.1723
November | 13894.1839 | 22.1509 | 89.7109 | 0 | 0.0002 | 447390.8186 | 5800.2551
December | 15258.0446 | 23.6773 | 92.4268 | 0 | 0.0002 | 460910.7528 | 6302.2657
Annual Sum or Average | 201679.7365 | 325.2557 | 1337.2124 | 0 | 0.0025 | 6668850 | 84580.3346
Minimum of Months | 13253.7739 | 20.9271 | 83.6691 | 0 | 0.0002 | 417252.2836 | 5511.8233
Maximum of Months | 21710.3425 | 35.6034 | 149.4971 | 0 | 0.0003 | 745582.9629 | 9166.2363
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 60696300000 | 47326.621 | 18-JAN-16:49 | 32837.857 | 8089.532 | 1729.598 | 0 | 919.679 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 54753500000 | 49310.888 | 27-FEB-17:30 | 32837.857 | 8089.532 | 2950.452 | 0 | 1683.092 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 62310900000 | 51921.502 | 31-MAR-14:00 | 32837.857 | 8089.532 | 2387.113 | 0 | 8607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 65572700000 | 69720.042 | 21-APR-14:00 | 32837.857 | 8089.532 | 5636.499 | 0 | 23156.154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 74670100000 | 79828.798 | 31-MAY-15:00 | 32837.857 | 8089.532 | 7324.09 | 0 | 31577.318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 90570100000 | 98344.724 | 27-JUN-15:00 | 32837.857 | 8089.532 | 9819.071 | 0 | 47598.264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 95906500000 | 97747.645 | 24-JUL-15:00 | 32837.857 | 8089.532 | 9808.918 | 0 | 47011.337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 97838400000 | 93550.461 | 04-AUG-14:00 | 32837.857 | 8089.532 | 9109.366 | 0 | 43513.706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 83685800000 | 91608.507 | 01-SEP-14:00 | 32837.857 | 8089.532 | 8999.933 | 0 | 41681.185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 69918500000 | 71676.729 | 03-OCT-14:00 | 32837.857 | 8089.532 | 6042.251 | 0 | 24707.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 58708400000 | 51617.515 | 09-NOV-16:40 | 32837.857 | 8089.532 | 2589.99 | 0 | 4350.181 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 60482600000 | 49447.593 | 05-DEC-16:30 | 32837.857 | 8089.532 | 3103.964 | 0 | 1666.286 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 875114000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 54753500000 | 47326.621 |  | 32837.857 | 8089.532 | 1729.598 | 0 | 919.679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 97838400000 | 98344.724 |  | 32837.857 | 8089.532 | 9819.071 | 0 | 47598.264 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 24633.23 | 1095.81 | 0 | 25729.04
Cost per Total Building Area ($/m2) | 11.78 | 0.52 | 0 | 12.31
Cost per Net Conditioned Building Area ($/m2) | 11.78 | 0.52 | 0 | 12.31

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 898.28 | 429.73 | 429.73
Net Site Energy | 898.28 | 429.73 | 429.73
Total Source Energy | 2432.31 | 1163.61 | 1163.61
Net Source Energy | 2432.31 | 1163.61 | 1163.61
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 173.67 | 0 | 0 | 0 | 0
Cooling | 21.03 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.94 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 17.51 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 724.61 | 173.67 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 23.99 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 23.99 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 13.77 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 13.77 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_2 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
LGSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.61 | 0.61 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.61 | 0.61 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.61 | 0.61 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.61 | 0.61 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.9 | 3.9 | 6.49 | 0.61 | 0.61 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.9 | 3.9 | 6.49 | 0.61 | 0.61 | No | LGSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.61 | 0.61 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.61 | 0.61 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW_SOUTH | 3.9 | 3.9 | 6.49 | 0.61 | 0.61 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.61 | 0.61 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.61 | 0.61 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 6.49 | 0.61 | 0.61 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.61 | 0.61 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.61 | 0.61 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 6.49 | 0.61 | 0.61 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.61 | 0.61 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.61 | 0.61 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 6.49 | 0.61 | 0.61 | No | SMSTORE4_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.61 | 0.61 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.61 | 0.61 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.61 | 0.61 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.61 | 0.61 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.88 | 3.88 | 6.49 | 0.61 | 0.61 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.88 | 3.88 | 6.49 | 0.61 | 0.61 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.61 | 0.61 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.61 | 0.61 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 6.49 | 0.61 | 0.61 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.61 | 0.61 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.61 | 0.61 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 6.49 | 0.61 | 0.61 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.61 | 0.61 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.61 | 0.61 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 6.49 | 0.61 | 0.61 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.61 | 0.61 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 6.49 | 0.61 | 0.61 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 6.49 | 0.61 | 0.61 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 6.49 | 0.61 | 0.61
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 6.49 | 0.61 | 0.61
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 21295.69 | 17007.91 | 4287.77 | 0.8 | 3.79
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 9916.64 | 7919.97 | 1996.66 | 0.8 | 4.06
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 8896.09 | 7104.91 | 1791.18 | 0.8 | 4.06
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 8787.59 | 7018.25 | 1769.33 | 0.8 | 4.05
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 8728.06 | 6970.71 | 1757.35 | 0.8 | 4.06
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14981.04 | 11964.69 | 3016.35 | 0.8 | 4.04
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 7905.33 | 6313.63 | 1591.7 | 0.8 | 4.06
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 7870.32 | 6285.67 | 1584.65 | 0.8 | 4.07
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 7901.29 | 6310.41 | 1590.88 | 0.8 | 4.06
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 8705.35 | 6952.58 | 1752.78 | 0.8 | 4.07
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 24248.76 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11629.35 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11629.35 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11629.35 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11629.35 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23258.71 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11629.35 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11629.35 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11629.35 | 0.8
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13316.39 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.29 | 1465.54 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.6 | 694.86 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.54 | 623.35 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.53 | 615.75 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.53 | 611.58 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.91 | 1030.98 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.48 | 553.93 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.48 | 551.47 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.48 | 553.64 | 1 | Unitary Fans
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.53 | 609.98 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 6917.9508 | 6.0087 | 48.6859 | 0 | 0 | 293710.0971 | 2542.8531
February | 5662.7489 | 4.8937 | 44.2855 | 0 | 0 | 267183.1877 | 2095.0001
March | 6396.97 | 5.5302 | 49.6634 | 0 | 0 | 299627.7986 | 2365.5231
April | 5908.581 | 5.1004 | 47.2372 | 0 | 0 | 284995.8066 | 2189.0887
May | 5868.3829 | 5.0538 | 49.0395 | 0 | 0 | 295877.8231 | 2180.6748
June | 5571.7382 | 4.7887 | 48.2934 | 0 | 0 | 291382.7435 | 2075.7293
July | 5623.1075 | 4.8265 | 49.8664 | 0 | 0 | 300877.5901 | 2098.3075
August | 5907.5282 | 5.0741 | 51.7729 | 0 | 0 | 312378.7517 | 2202.5626
September | 5759.7944 | 4.9434 | 51.1553 | 0 | 0 | 308654.4239 | 2149.5473
October | 5898.489 | 5.0731 | 50.4807 | 0 | 0 | 304577.4489 | 2195.4915
November | 5789.8397 | 4.9944 | 46.919 | 0 | 0 | 283078.1005 | 2147.0212
December | 6544.7855 | 5.6718 | 48.3464 | 0 | 0 | 291672.4271 | 2412.6643
Annual Sum or Average | 71849.9162 | 61.9587 | 585.7456 | 0 | 0.0003 | 3534020 | 26654.4636
Minimum of Months | 5571.7382 | 4.7887 | 44.2855 | 0 | 0 | 267183.1877 | 2075.7293
Maximum of Months | 6917.9508 | 6.0087 | 51.7729 | 0 | 0 | 312378.7517 | 2542.8531
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 60221600000 | 46132.021 | 27-JAN-17:30 | 32837.857 | 8089.532 | 697.745 | 0 | 756.932 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 54782600000 | 52443.063 | 15-FEB-15:00 | 32837.857 | 8089.532 | 2887.273 | 0 | 8628.401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 61435000000 | 47548.431 | 20-MAR-14:00 | 32837.857 | 8089.532 | 2537.551 | 0 | 4083.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 58434800000 | 53284.253 | 29-APR-14:30 | 32837.857 | 8089.532 | 3053.438 | 0 | 9303.426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 60666100000 | 53497.835 | 17-MAY-14:09 | 32837.857 | 8089.532 | 3040.998 | 0 | 9529.447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 59744400000 | 54706.447 | 16-JUN-14:00 | 32837.857 | 8089.532 | 3350.023 | 0 | 10429.035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 61691200000 | 60216.577 | 03-JUL-14:09 | 32837.857 | 8089.532 | 4519.367 | 0 | 14769.821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 64049400000 | 57273.552 | 26-AUG-14:20 | 32837.857 | 8089.532 | 3911.161 | 0 | 12435.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 63285800000 | 73421.604 | 28-SEP-14:00 | 32837.857 | 8089.532 | 7201.701 | 0 | 25292.513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 62449800000 | 55890.484 | 13-OCT-14:00 | 32837.857 | 8089.532 | 3702.273 | 0 | 11260.822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 58041600000 | 48368.336 | 14-NOV-16:00 | 32837.857 | 8089.532 | 1551.226 | 0 | 2139.766 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 59803800000 | 46625.516 | 07-DEC-16:49 | 32837.857 | 8089.532 | 795.388 | 0 | 1152.784 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 724606000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 54782600000 | 46132.021 |  | 32837.857 | 8089.532 | 697.745 | 0 | 756.932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 64049400000 | 73421.604 |  | 32837.857 | 8089.532 | 7201.701 | 0 | 25292.513 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 30584.03 | 1485.22 | 0 | 32069.25
Cost per Total Building Area ($/m2) | 14.63 | 0.71 | 0 | 15.34
Cost per Net Conditioned Building Area ($/m2) | 14.63 | 0.71 | 0 | 15.34

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1131.92 | 541.51 | 541.51
Net Site Energy | 1131.92 | 541.51 | 541.51
Total Source Energy | 3284.37 | 1571.23 | 1571.23
Net Source Energy | 3284.37 | 1571.23 | 1571.23
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 307.32 | 0 | 0 | 0 | 0
Cooling | 109.01 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.9 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 29.56 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 824.6 | 307.32 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 23.99 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 23.99 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 13.77 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 13.77 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_2 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
LGSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.9 | 3.9 | 3.18 | 0.402 | 0.495 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.9 | 3.9 | 3.18 | 0.402 | 0.495 | No | LGSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW_SOUTH | 3.9 | 3.9 | 3.18 | 0.402 | 0.495 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE4_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 3.18 | 0.402 | 0.495
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 39505.87 | 27003.3 | 12502.57 | 0.68 | 3.44
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19694.35 | 13315.02 | 6379.33 | 0.68 | 3.45
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17445.34 | 11794.5 | 5650.84 | 0.68 | 3.66
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17086.46 | 11551.87 | 5534.59 | 0.68 | 3.67
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16817.49 | 11370.02 | 5447.47 | 0.68 | 3.67
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27905.31 | 18866.32 | 9039 | 0.68 | 3.45
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14853.02 | 10041.88 | 4811.14 | 0.68 | 3.67
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14781.27 | 9993.37 | 4787.9 | 0.68 | 3.67
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14703.8 | 9941 | 4762.81 | 0.68 | 3.66
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17895.23 | 12098.67 | 5796.57 | 0.68 | 3.65
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 41684.66 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 19039.54 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 18964.16 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 18960.72 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 18976.58 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 37642.1 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 18976.95 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 18967.04 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 19073.12 | 0.8
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 22958.14 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.64 | 1792.69 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.79 | 903.49 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.7 | 814.86 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.69 | 798.1 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.68 | 785.54 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.12 | 1280.17 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.6 | 693.78 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.6 | 690.43 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.59 | 686.81 | 1 | Unitary Fans
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.72 | 820.95 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 14924.2837 | 24.8262 | 62.3427 | 0 | 0.0003 | 3875.9508 | 6196.6773
February | 12298.4346 | 21.2235 | 55.6 | 0 | 0.0002 | 3457.068 | 5176.3894
March | 12155.0114 | 22.2944 | 62.2312 | 0 | 0.0003 | 3869.8955 | 5236.5731
April | 10700.8114 | 20.34 | 58.7221 | 0 | 0.0002 | 3651.9287 | 4675.2633
May | 11260.3008 | 22.203 | 66.2069 | 0 | 0.0003 | 4117.6646 | 4992.8125
June | 13882.8294 | 27.7558 | 83.7342 | 0 | 0.0003 | 5207.8711 | 6190.544
July | 15270.1643 | 30.5312 | 92.1113 | 0 | 0.0004 | 5728.8888 | 6809.3316
August | 15795.8208 | 31.5821 | 95.2816 | 0 | 0.0004 | 5926.0638 | 7043.7251
September | 12364.9837 | 24.6982 | 74.4524 | 0 | 0.0003 | 4630.5785 | 5511.6135
October | 11352.6778 | 22.0368 | 64.8266 | 0 | 0.0003 | 4031.7111 | 5001.9194
November | 11138.5768 | 20.8337 | 59.256 | 0 | 0.0002 | 3685.0223 | 4835.5854
December | 13483.0577 | 23.3599 | 61.4637 | 0 | 0.0003 | 3821.6994 | 5683.4113
Annual Sum or Average | 154626.9523 | 291.6849 | 836.2287 | 0 | 0.0034 | 52004.3426 | 67353.8457
Minimum of Months | 10700.8114 | 20.34 | 55.6 | 0 | 0.0002 | 3457.068 | 4675.2633
Maximum of Months | 15795.8208 | 31.5821 | 95.2816 | 0 | 0.0004 | 5926.0638 | 7043.7251
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 61458600000 | 46377.632 | 17-JAN-17:00 | 32837.857 | 8089.532 | 1700.289 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 54816700000 | 45078.525 | 23-FEB-17:00 | 32837.857 | 8089.532 | 401.181 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 61362600000 | 52318.381 | 09-MAR-15:00 | 32837.857 | 8089.532 | 1772.891 | 0 | 9618.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 57906500000 | 55403.772 | 05-APR-15:00 | 32837.857 | 8089.532 | 2351.866 | 0 | 12124.517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 65291400000 | 66873.368 | 15-MAY-14:00 | 32837.857 | 8089.532 | 3976.837 | 0 | 21969.142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 82578100000 | 94150.664 | 30-JUN-14:00 | 32837.857 | 8089.532 | 7523.128 | 0 | 45700.146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 90839600000 | 100109.931 | 25-JUL-14:09 | 32837.857 | 8089.532 | 8324.442 | 0 | 50858.099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 93966100000 | 102830.079 | 17-AUG-14:00 | 32837.857 | 8089.532 | 8767 | 0 | 53135.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 73424300000 | 81387.472 | 09-SEP-14:00 | 32837.857 | 8089.532 | 5929.92 | 0 | 34530.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 63928400000 | 65439.12 | 12-OCT-14:00 | 32837.857 | 8089.532 | 3801.691 | 0 | 20710.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 58431200000 | 56113.373 | 04-NOV-14:20 | 32837.857 | 8089.532 | 2373.072 | 0 | 12812.912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 60598400000 | 45315.597 | 14-DEC-17:19 | 32837.857 | 8089.532 | 638.253 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 824602000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 54816700000 | 45078.525 |  | 32837.857 | 8089.532 | 401.181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 93966100000 | 102830.079 |  | 32837.857 | 8089.532 | 8767 | 0 | 53135.69 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 18351.3 | 2967.92 | 0 | 21319.22
Cost per Total Building Area ($/m2) | 8.78 | 1.42 | 0 | 10.2
Cost per Net Conditioned Building Area ($/m2) | 8.78 | 1.42 | 0 | 10.2

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1056.91 | 505.62 | 505.62
Net Site Energy | 1056.91 | 505.62 | 505.62
Total Source Energy | 2933.81 | 1403.52 | 1403.52
Net Source Energy | 2933.81 | 1403.52 | 1403.52
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 257.42 | 0 | 0 | 0 | 0
Cooling | 76.63 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.92 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 36.81 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 799.49 | 257.42 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 23.99 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 23.99 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 13.77 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 13.77 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_2 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
LGSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.9 | 3.9 | 3.18 | 0.402 | 0.495 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.9 | 3.9 | 3.18 | 0.402 | 0.495 | No | LGSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW_SOUTH | 3.9 | 3.9 | 3.18 | 0.402 | 0.495 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE4_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 3.18 | 0.402 | 0.495
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 30361.64 | 24248.49 | 6113.16 | 0.8 | 3.74
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13491.78 | 10775.28 | 2716.5 | 0.8 | 4.04
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12221.95 | 9761.12 | 2460.82 | 0.8 | 4.04
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12090.94 | 9656.49 | 2434.45 | 0.8 | 4.03
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12026.24 | 9604.82 | 2421.42 | 0.8 | 4.04
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 21202.53 | 16933.51 | 4269.02 | 0.8 | 3.79
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 11027.74 | 8807.36 | 2220.38 | 0.8 | 4.06
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10985.2 | 8773.39 | 2211.81 | 0.8 | 4.05
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 11072.03 | 8842.74 | 2229.3 | 0.8 | 4.06
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12985.14 | 10370.65 | 2614.49 | 0.8 | 4.02
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 34983.66 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15966.33 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15894 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15890.79 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15907.21 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 31490.09 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15907.55 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15896.68 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15996.35 | 0.8
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 19339.51 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.83 | 2005.87 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.82 | 928.49 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.74 | 841.1 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.73 | 832.08 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.73 | 827.63 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.28 | 1459.13 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.67 | 772.71 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.66 | 769.73 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.67 | 775.82 | 1 | Unitary Fans
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.78 | 893.62 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 19075.5842 | 30.9652 | 73.9631 | 0 | 0.0003 | 76894.4193 | 7941.0269
February | 16565.7245 | 27.3213 | 66.5603 | 0 | 0.0003 | 69201.435 | 6938.3956
March | 18204.0783 | 30.396 | 75.1601 | 0 | 0.0003 | 78145.2031 | 7661.1582
April | 16586.7614 | 28.3173 | 71.848 | 0 | 0.0003 | 74705.9129 | 7041.5029
May | 18248.7506 | 31.847 | 82.7942 | 0 | 0.0003 | 86092.1361 | 7814.9662
June | 19918.2463 | 34.9435 | 91.3593 | 0 | 0.0004 | 94999.5358 | 8547.8743
July | 21607.2231 | 37.9107 | 99.1284 | 0 | 0.0004 | 103078.3036 | 9273.0998
August | 21860.2738 | 38.3546 | 100.2887 | 0 | 0.0004 | 104284.8207 | 9381.689
September | 19210.0443 | 33.6992 | 88.1006 | 0 | 0.0003 | 91611.009 | 8243.7633
October | 17218.5745 | 29.6273 | 75.8372 | 0 | 0.0003 | 78855.2878 | 7332.4198
November | 17219.8983 | 28.7339 | 70.995 | 0 | 0.0003 | 73814.4991 | 7245.1242
December | 19081.3838 | 30.9432 | 73.8155 | 0 | 0.0003 | 76740.7515 | 7940.3591
Annual Sum or Average | 224796.5431 | 383.0592 | 969.8505 | 0 | 0.0038 | 1008420 | 95361.3795
Minimum of Months | 16565.7245 | 27.3213 | 66.5603 | 0 | 0.0003 | 69201.435 | 6938.3956
Maximum of Months | 21860.2738 | 38.3546 | 100.2887 | 0 | 0.0004 | 104284.8207 | 9381.689
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 60962800000 | 45779.998 | 25-JAN-17:30 | 32837.857 | 8089.532 | 709.495 | 0 | 393.16 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 54863700000 | 48981.242 | 14-FEB-15:00 | 32837.857 | 8089.532 | 2090.392 | 0 | 5963.461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 61954500000 | 49150.598 | 02-MAR-15:00 | 32837.857 | 8089.532 | 2135.389 | 0 | 6087.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 59227700000 | 57254.122 | 22-APR-14:39 | 32837.857 | 8089.532 | 3851.02 | 0 | 12475.712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 68254900000 | 63661.67 | 31-MAY-15:00 | 32837.857 | 8089.532 | 5157.338 | 0 | 17576.943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 75316800000 | 77268.415 | 29-JUN-14:00 | 32837.857 | 8089.532 | 7896.327 | 0 | 28444.699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 81721700000 | 82611.532 | 31-JUL-14:00 | 32837.857 | 8089.532 | 8972.766 | 0 | 32711.377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 82678300000 | 80541.992 | 01-AUG-14:00 | 32837.857 | 8089.532 | 8468.727 | 0 | 31145.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 72630300000 | 70199.141 | 02-SEP-15:20 | 32837.857 | 8089.532 | 6599.802 | 0 | 22671.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 62517400000 | 57681.818 | 13-OCT-14:00 | 32837.857 | 8089.532 | 4071.639 | 0 | 12682.789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 58521000000 | 49395.976 | 08-NOV-17:10 | 32837.857 | 8089.532 | 3112.276 | 0 | 1606.356 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 60841000000 | 45718.181 | 09-DEC-16:49 | 32837.857 | 8089.532 | 558.402 | 0 | 482.435 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 799490000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 54863700000 | 45718.181 |  | 32837.857 | 8089.532 | 558.402 | 0 | 393.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 82678300000 | 82611.532 |  | 32837.857 | 8089.532 | 8972.766 | 0 | 32711.377 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 8393.53 | 1769.01 | 0 | 10162.55
Cost per Total Building Area ($/m2) | 4.02 | 0.85 | 0 | 4.86
Cost per Net Conditioned Building Area ($/m2) | 4.02 | 0.85 | 0 | 4.86

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1002.67 | 479.67 | 479.67
Net Site Energy | 1002.67 | 479.67 | 479.67
Total Source Energy | 1566.96 | 749.63 | 749.63
Net Source Energy | 1566.96 | 749.63 | 749.63
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 276.44 | 0 | 0 | 0 | 0
Cooling | 22.48 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.81 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 17.81 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 726.23 | 276.44 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 23.99 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 23.99 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 13.77 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 13.77 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_2 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
LGSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.9 | 3.9 | 3.18 | 0.402 | 0.495 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.9 | 3.9 | 3.18 | 0.402 | 0.495 | No | LGSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW_SOUTH | 3.9 | 3.9 | 3.18 | 0.402 | 0.495 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE4_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.402 | 0.495 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.402 | 0.495 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 3.18 | 0.402 | 0.495
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 23699.7 | 18583.5 | 5116.2 | 0.78 | 3.75
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 11137.62 | 8633.75 | 2503.87 | 0.78 | 3.97
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10194.97 | 7843.38 | 2351.59 | 0.77 | 3.96
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10095.4 | 7760.23 | 2335.16 | 0.77 | 3.95
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10042.97 | 7716.47 | 2326.5 | 0.77 | 3.96
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17833.85 | 13566.04 | 4267.81 | 0.76 | 3.91
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 9276 | 7079.15 | 2196.85 | 0.76 | 3.94
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 9242.97 | 7051.83 | 2191.14 | 0.76 | 3.92
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 9285.78 | 7087.31 | 2198.47 | 0.76 | 3.94
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10221.01 | 7864.21 | 2356.81 | 0.77 | 3.96
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 33089.25 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15146.93 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15084.02 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15081.08 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15094.68 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 29918.47 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15095.01 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15086.49 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15174.28 | 0.8
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 18216.44 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.38 | 1566.52 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.63 | 730.6 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.57 | 657.4 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.56 | 649.73 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.56 | 645.7 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.97 | 1100.57 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.51 | 587.23 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.5 | 584.74 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.51 | 587.98 | 1 | Unitary Fans
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.57 | 659.23 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 5626.6501 | 7.149 | 13.0587 | 0 | 0.0001 | 172431.5781 | 2166.0462
February | 4362.8195 | 5.7841 | 11.6637 | 0 | 0 | 154056.3265 | 1705.321
March | 4775.4213 | 6.391 | 13.149 | 0 | 0.0001 | 173684.027 | 1873.0087
April | 3970.9541 | 5.5233 | 12.2681 | 0 | 0.0001 | 162081.7617 | 1579.8622
May | 3574.8352 | 5.269 | 12.9379 | 0 | 0.0001 | 170972.8591 | 1454.0284
June | 3233.6149 | 4.9582 | 12.9297 | 0 | 0.0001 | 170887.926 | 1335.8185
July | 3222.9881 | 5.097 | 13.8781 | 0 | 0.0001 | 183438.3151 | 1348.0485
August | 3332.8068 | 5.3096 | 14.5993 | 0 | 0.0001 | 192975.6317 | 1398.1477
September | 3342.6269 | 5.1035 | 13.2266 | 0 | 0.0001 | 174809.3187 | 1378.52
October | 3751.1805 | 5.3991 | 12.7479 | 0 | 0.0001 | 168446.1002 | 1511.8618
November | 4556.7982 | 6.091 | 12.4994 | 0 | 0.0001 | 165103.0574 | 1786.4626
December | 5554.3439 | 7.08 | 13.0369 | 0 | 0.0001 | 172148.3882 | 2140.6608
Annual Sum or Average | 49305.0397 | 69.1549 | 155.9953 | 0 | 0.0006 | 2061040 | 19677.7864
Minimum of Months | 3222.9881 | 4.9582 | 11.6637 | 0 | 0 | 154056.3265 | 1335.8185
Maximum of Months | 5626.6501 | 7.149 | 14.5993 | 0 | 0.0001 | 192975.6317 | 2166.0462
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 60758100000 | 45096.918 | 30-JAN-17:00 | 32837.857 | 8089.532 | 419.575 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 54283400000 | 44921.234 | 27-FEB-17:00 | 32837.857 | 8089.532 | 243.891 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 61199400000 | 48296.994 | 29-MAR-14:00 | 32837.857 | 8089.532 | 1787.196 | 0 | 5582.409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 57111300000 | 51433.577 | 29-APR-15:30 | 32837.857 | 8089.532 | 2416.689 | 0 | 8089.498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 60244100000 | 55143.891 | 04-MAY-14:00 | 32837.857 | 8089.532 | 3237.736 | 0 | 10978.766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 60214200000 | 58482.58 | 17-JUN-15:00 | 32837.857 | 8089.532 | 3896.334 | 0 | 13658.857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 64636500000 | 66396.274 | 24-JUL-14:00 | 32837.857 | 8089.532 | 5359.808 | 0 | 20109.076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 67997100000 | 64016.62 | 07-AUG-14:00 | 32837.857 | 8089.532 | 4990.467 | 0 | 18098.763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 61596000000 | 77902.202 | 02-SEP-15:00 | 32837.857 | 8089.532 | 7278.536 | 0 | 29696.276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 59353800000 | 49851.674 | 17-OCT-14:00 | 32837.857 | 8089.532 | 2110.104 | 0 | 6814.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 58175800000 | 48994.243 | 04-NOV-16:49 | 32837.857 | 8089.532 | 1714.291 | 0 | 2602.607 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 60658300000 | 45285.746 | 13-DEC-17:00 | 32837.857 | 8089.532 | 608.402 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 726228000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 54283400000 | 44921.234 |  | 32837.857 | 8089.532 | 243.891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 67997100000 | 77902.202 |  | 32837.857 | 8089.532 | 7278.536 | 0 | 29696.276 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 14593.55 | 2325.73 | 0 | 16919.28
Cost per Total Building Area ($/m2) | 6.98 | 1.11 | 0 | 8.09
Cost per Net Conditioned Building Area ($/m2) | 6.98 | 1.11 | 0 | 8.09

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1204.54 | 576.25 | 576.25
Net Site Energy | 1204.54 | 576.25 | 576.25
Total Source Energy | 3260.56 | 1559.84 | 1559.84
Net Source Energy | 3260.56 | 1559.84 | 1559.84
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 411.87 | 0 | 0 | 0 | 0
Cooling | 80.46 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.91 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 26.17 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 792.67 | 411.87 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 23.99 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 23.99 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 13.77 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 13.77 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_2 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 78.94 | 0 | 90 | N
LGSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 78.94 | 180 | 90 | S
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
LGSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 78.94 | 0 | 90 | N
LGSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 78.94 | 180 | 90 | S
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.9 | 3.9 | 3.18 | 0.501 | 0.622 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.9 | 3.9 | 3.18 | 0.501 | 0.622 | No | LGSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW_SOUTH | 3.9 | 3.9 | 3.18 | 0.501 | 0.622 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.622 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.622 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.622 | No | SMSTORE4_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.622 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.622 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.622 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.622 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.622 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.622 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 3.18 | 0.501 | 0.622
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 3.18 | 0.501 | 0.622
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 36863.36 | 24924.28 | 11939.08 | 0.68 | 3.43
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17923.1 | 12117.51 | 5805.59 | 0.68 | 3.65
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15756.64 | 10652.8 | 5103.84 | 0.68 | 3.66
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15481.93 | 10467.07 | 5014.86 | 0.68 | 3.66
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15405.23 | 10415.22 | 4990.01 | 0.68 | 3.66
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 28366.65 | 19178.22 | 9188.44 | 0.68 | 3.45
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14816.46 | 10017.16 | 4799.3 | 0.68 | 3.67
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14753.87 | 9974.85 | 4779.03 | 0.68 | 3.66
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14826.55 | 10023.98 | 4802.57 | 0.68 | 3.67
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16940.36 | 11453.09 | 5487.27 | 0.68 | 3.66
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 51779.81 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23915.79 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23843.71 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23840.67 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23858.55 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 47373.48 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23858.87 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23846.17 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23940.94 | 0.8
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 28198.94 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.48 | 1623.76 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.72 | 822.23 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.63 | 735.98 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.62 | 723.15 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.62 | 719.57 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.14 | 1301.33 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.6 | 692.07 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.59 | 689.15 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.6 | 692.54 | 1 | Unitary Fans
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.68 | 791.27 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 26864.0843 | 43.6254 | 115.4548 | 0 | 0.0004 | 26572.1475 | 11137.3247
February | 22519.7891 | 37.5774 | 102.8201 | 0 | 0.0003 | 23665.8948 | 9432.5316
March | 23528.2947 | 40.4396 | 114.4946 | 0 | 0.0004 | 26354.8336 | 9967.7085
April | 20923.2851 | 36.9112 | 107.5068 | 0 | 0.0003 | 24747.7463 | 8954.8345
May | 22210.6745 | 40.0341 | 119.2279 | 0 | 0.0004 | 27447.0736 | 9587.257
June | 25904.8551 | 47.1582 | 141.8488 | 0 | 0.0004 | 32655.1848 | 11226.3579
July | 29116.6003 | 53.0182 | 159.5145 | 0 | 0.0005 | 36722.0458 | 12619.4876
August | 28830.4166 | 52.4962 | 157.9414 | 0 | 0.0005 | 36359.8951 | 12495.3681
September | 23490.2699 | 42.7028 | 128.2684 | 0 | 0.0004 | 29528.749 | 10174.2309
October | 21584.2922 | 38.5682 | 113.8457 | 0 | 0.0003 | 26207.6231 | 9284.6663
November | 21768.4801 | 37.8708 | 108.6636 | 0 | 0.0003 | 25013.2962 | 9265.7513
December | 25571.8025 | 42.2766 | 114.3958 | 0 | 0.0004 | 26329.6375 | 10673.2582
Annual Sum or Average | 292312.8443 | 512.6788 | 1483.9823 | 0 | 0.0045 | 341604.1274 | 124818.7765
Minimum of Months | 20923.2851 | 36.9112 | 102.8201 | 0 | 0.0003 | 23665.8948 | 8954.8345
Maximum of Months | 29116.6003 | 53.0182 | 159.5145 | 0 | 0.0005 | 36722.0458 | 12619.4876
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 61658700000 | 46258.739 | 26-JAN-17:00 | 32837.857 | 8089.532 | 1581.395 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 54914900000 | 45338.518 | 03-FEB-17:00 | 32837.857 | 8089.532 | 661.174 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 61154400000 | 47084.005 | 31-MAR-14:00 | 32837.857 | 8089.532 | 1019.091 | 0 | 5137.525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 57425300000 | 51924.965 | 07-APR-14:00 | 32837.857 | 8089.532 | 1821.624 | 0 | 9175.952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 63688900000 | 62116.005 | 30-MAY-15:00 | 32837.857 | 8089.532 | 3162.012 | 0 | 18026.604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 75773900000 | 87485.657 | 08-JUN-12:00 | 32837.857 | 8089.532 | 6672.997 | 0 | 39885.271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 85210700000 | 92418.775 | 13-JUL-14:00 | 32837.857 | 8089.532 | 7281.377 | 0 | 44210.008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 84370400000 | 92774.512 | 04-AUG-14:00 | 32837.857 | 8089.532 | 7615.752 | 0 | 44231.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 68519200000 | 72589.924 | 05-SEP-14:00 | 32837.857 | 8089.532 | 4736.506 | 0 | 26926.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 60812800000 | 55085.72 | 05-OCT-14:09 | 32837.857 | 8089.532 | 2267.96 | 0 | 11890.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 58041500000 | 53257.532 | 02-NOV-16:49 | 32837.857 | 8089.532 | 1370.407 | 0 | 7209.781 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 61095900000 | 45541.039 | 14-DEC-17:00 | 32837.857 | 8089.532 | 863.695 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 792667000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 54914900000 | 45338.518 |  | 32837.857 | 8089.532 | 661.174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 85210700000 | 92774.512 |  | 32837.857 | 8089.532 | 7615.752 | 0 | 44231.371 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 11796.17 | 3412.72 | 0 | 15208.89
Cost per Total Building Area ($/m2) | 5.64 | 1.63 | 0 | 7.28
Cost per Net Conditioned Building Area ($/m2) | 5.64 | 1.63 | 0 | 7.28

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1118.79 | 535.23 | 535.23
Net Site Energy | 1118.79 | 535.23 | 535.23
Total Source Energy | 2915.28 | 1394.66 | 1394.66
Net Source Energy | 2915.28 | 1394.66 | 1394.66
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 357.98 | 0 | 0 | 0 | 0
Cooling | 45.84 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.88 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 28.96 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 760.81 | 357.98 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 23.99 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 23.99 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 13.77 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 13.77 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_2 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 78.94 | 0 | 90 | N
LGSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 78.94 | 180 | 90 | S
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
LGSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 78.94 | 0 | 90 | N
LGSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 78.94 | 180 | 90 | S
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.9 | 3.9 | 3.18 | 0.501 | 0.622 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.9 | 3.9 | 3.18 | 0.501 | 0.622 | No | LGSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW_SOUTH | 3.9 | 3.9 | 3.18 | 0.501 | 0.622 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.622 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.622 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.622 | No | SMSTORE4_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.622 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.622 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.622 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.622 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.622 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.622 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 3.18 | 0.501 | 0.622
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 3.18 | 0.501 | 0.622
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 26312.9 | 21014.94 | 5297.96 | 0.8 | 3.74
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12664.25 | 10114.37 | 2549.88 | 0.8 | 4.04
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 11429.96 | 9128.6 | 2301.36 | 0.8 | 4.05
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 11298.55 | 9023.65 | 2274.9 | 0.8 | 4.05
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 11230.07 | 8968.96 | 2261.12 | 0.8 | 4.06
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19618.3 | 15668.26 | 3950.04 | 0.8 | 3.79
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10226.23 | 8167.23 | 2059 | 0.8 | 4.06
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10182.27 | 8132.13 | 2050.15 | 0.8 | 4.07
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10231.3 | 8171.28 | 2060.02 | 0.8 | 4.06
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12003.51 | 9586.67 | 2416.84 | 0.8 | 4.04
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 43891.12 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20264.83 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20194.99 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20192.09 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20210.25 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 40070.51 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20210.55 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20197.34 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20287.91 | 0.8
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23967.6 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.59 | 1738.39 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.77 | 871.54 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.69 | 800.9 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.68 | 791.69 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.68 | 786.89 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.19 | 1350.11 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.62 | 716.55 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.62 | 713.47 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.62 | 716.91 | 1 | Unitary Fans
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.73 | 826.07 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 20175.6101 | 32.0197 | 74.2707 | 0 | 0.0003 | 77208.7631 | 8327.2373
February | 17380.7839 | 28.0688 | 66.6052 | 0 | 0.0003 | 69243.7901 | 7221.2392
March | 18486.6023 | 30.5728 | 74.7303 | 0 | 0.0003 | 77696.1836 | 7751.1278
April | 16615.0402 | 28.0996 | 70.5311 | 0 | 0.0003 | 73334.844 | 7027.4221
May | 16994.9306 | 29.1799 | 74.5133 | 0 | 0.0003 | 77478.2752 | 7231.0407
June | 17440.4545 | 30.4551 | 79.2286 | 0 | 0.0003 | 82384.6371 | 7470.6579
July | 20015.0357 | 35.117 | 91.8229 | 0 | 0.0004 | 95481.6555 | 8589.768
August | 20445.0136 | 35.8698 | 93.7869 | 0 | 0.0004 | 97523.9204 | 8774.1441
September | 17363.3192 | 30.2132 | 78.2976 | 0 | 0.0003 | 81415.801 | 7427.0938
October | 17258.0882 | 29.381 | 74.3098 | 0 | 0.0003 | 77265.0436 | 7318.4121
November | 17497.4546 | 28.9386 | 70.7406 | 0 | 0.0003 | 73548.1655 | 7336.5548
December | 20136.3726 | 31.9562 | 74.1194 | 0 | 0.0003 | 77051.4528 | 8310.918
Annual Sum or Average | 219808.7056 | 369.8716 | 922.9563 | 0 | 0.0036 | 959632.5319 | 92785.6157
Minimum of Months | 16615.0402 | 28.0688 | 66.6052 | 0 | 0.0003 | 69243.7901 | 7027.4221
Maximum of Months | 20445.0136 | 35.8698 | 93.7869 | 0 | 0.0004 | 97523.9204 | 8774.1441
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 61212000000 | 45610.653 | 05-JAN-17:00 | 32837.857 | 8089.532 | 933.309 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 54897300000 | 46033.888 | 15-FEB-17:00 | 32837.857 | 8089.532 | 1356.544 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 61598500000 | 49973.502 | 30-MAR-14:00 | 32837.857 | 8089.532 | 2332.097 | 0 | 6714.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 58140700000 | 53387.256 | 25-APR-14:00 | 32837.857 | 8089.532 | 3045.182 | 0 | 9414.684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 61425700000 | 57387.901 | 23-MAY-15:00 | 32837.857 | 8089.532 | 3846.692 | 0 | 12613.819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 65315500000 | 67970.198 | 27-JUN-15:00 | 32837.857 | 8089.532 | 6040.115 | 0 | 21002.694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 75699000000 | 77114.583 | 17-JUL-14:00 | 32837.857 | 8089.532 | 7930.344 | 0 | 28256.849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 77318100000 | 78356.405 | 30-AUG-13:00 | 32837.857 | 8089.532 | 8033.909 | 0 | 29395.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 64547400000 | 68958.025 | 02-SEP-15:09 | 32837.857 | 8089.532 | 6377.411 | 0 | 21653.224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 61256700000 | 58391.524 | 05-OCT-14:00 | 32837.857 | 8089.532 | 4155.247 | 0 | 13308.888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 58309900000 | 49375.106 | 04-NOV-16:00 | 32837.857 | 8089.532 | 2792.315 | 0 | 1905.447 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 61087300000 | 46388.766 | 01-DEC-17:00 | 32837.857 | 8089.532 | 1711.422 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 760808000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 54897300000 | 45610.653 |  | 32837.857 | 8089.532 | 933.309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 77318100000 | 78356.405 |  | 32837.857 | 8089.532 | 8033.909 | 0 | 29395.107 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 7996.75 | 2470.24 | 0 | 10466.98
Cost per Total Building Area ($/m2) | 3.83 | 1.18 | 0 | 5.01
Cost per Net Conditioned Building Area ($/m2) | 3.83 | 1.18 | 0 | 5.01

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1428.29 | 683.29 | 683.29
Net Site Energy | 1428.29 | 683.29 | 683.29
Total Source Energy | 3405.21 | 1629.04 | 1629.04
Net Source Energy | 3405.21 | 1629.04 | 1629.04
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 641.29 | 0 | 0 | 0 | 0
Cooling | 71.26 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.87 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 29.74 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 787 | 641.29 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 23.99 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 23.99 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 13.77 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 13.77 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_2 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 78.94 | 0 | 90 | N
LGSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 78.94 | 180 | 90 | S
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
LGSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 78.94 | 0 | 90 | N
LGSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 78.94 | 180 | 90 | S
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.9 | 3.9 | 3.18 | 0.501 | 0.622 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.9 | 3.9 | 3.18 | 0.501 | 0.622 | No | LGSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW_SOUTH | 3.9 | 3.9 | 3.18 | 0.501 | 0.622 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.622 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.622 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.622 | No | SMSTORE4_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.622 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.622 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.622 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.622 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.622 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.622 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 3.18 | 0.501 | 0.622
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 3.18 | 0.501 | 0.622
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 34602.19 | 23868.38 | 10733.81 | 0.69 | 3.46
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17097.74 | 11732.01 | 5365.73 | 0.69 | 3.68
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15578.36 | 10544.05 | 5034.31 | 0.68 | 3.67
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15394.65 | 10408.06 | 4986.59 | 0.68 | 3.66
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15318.1 | 10356.31 | 4961.79 | 0.68 | 3.67
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 28222.92 | 19081.04 | 9141.88 | 0.68 | 3.45
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14755.54 | 9975.97 | 4779.57 | 0.68 | 3.66
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14692.55 | 9933.38 | 4759.16 | 0.68 | 3.66
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14766.07 | 9983.09 | 4782.98 | 0.68 | 3.66
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19300.48 | 13089.97 | 6210.52 | 0.68 | 3.45
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 58564.14 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 27023.49 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 26943.86 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 26940.58 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 26960.41 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 53542.47 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 26960.74 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 26946.51 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 27051.26 | 0.8
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 31910.04 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.47 | 1609.14 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.72 | 816.66 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.63 | 729.9 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.62 | 719.08 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.62 | 715.5 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.14 | 1294.74 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.59 | 689.22 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.59 | 686.28 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.59 | 689.71 | 1 | Unitary Fans
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.78 | 893.13 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 23719.2175 | 34.2633 | 41.5707 | 0 | 0.0003 | 27293.0596 | 9426.3865
February | 18575.0254 | 28.1229 | 36.7574 | 0 | 0.0003 | 24141.0284 | 7505.3714
March | 16865.0508 | 27.6658 | 40.3152 | 0 | 0.0003 | 26489.5135 | 7018.2173
April | 13879.9257 | 24.1064 | 37.5344 | 0 | 0.0003 | 24668.5795 | 5903.8345
May | 14620.4804 | 26.3279 | 42.5826 | 0 | 0.0003 | 27990.1839 | 6308.2339
June | 16467.2232 | 30.035 | 49.2036 | 0 | 0.0004 | 32343.7231 | 7141.5091
July | 17819.9232 | 32.5169 | 53.2934 | 0 | 0.0004 | 35032.1454 | 7729.5547
August | 18292.6293 | 33.3806 | 54.7106 | 0 | 0.0004 | 35963.7314 | 7934.6976
September | 14080.7587 | 25.4837 | 41.4264 | 0 | 0.0003 | 27230.6984 | 6087.5682
October | 14435.5352 | 25.1582 | 39.3196 | 0 | 0.0003 | 25842.1897 | 6148.4614
November | 16018.3151 | 26.333 | 38.4742 | 0 | 0.0003 | 25280.1502 | 6671.2327
December | 21147.9049 | 31.7398 | 40.9418 | 0 | 0.0003 | 26887.6265 | 8518.3359
Annual Sum or Average | 205921.9894 | 345.1336 | 516.1299 | 0 | 0.0038 | 339162.6297 | 86393.4032
Minimum of Months | 13879.9257 | 24.1064 | 36.7574 | 0 | 0.0003 | 24141.0284 | 5903.8345
Maximum of Months | 23719.2175 | 34.2633 | 54.7106 | 0 | 0.0004 | 35963.7314 | 9426.3865
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 63331500000 | 47085.653 | 04-JAN-17:00 | 32837.857 | 8089.532 | 2408.309 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 56017400000 | 46271.416 | 01-FEB-17:00 | 32837.857 | 8089.532 | 1594.072 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 61466900000 | 45519.722 | 01-MAR-17:00 | 32837.857 | 8089.532 | 842.378 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 57241600000 | 49582.296 | 26-APR-14:00 | 32837.857 | 8089.532 | 1483.429 | 0 | 7171.478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 64949100000 | 81830.414 | 27-MAY-14:00 | 32837.857 | 8089.532 | 5794.56 | 0 | 35108.464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 75051200000 | 86488.17 | 29-JUN-14:00 | 32837.857 | 8089.532 | 6618.37 | 0 | 38942.411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 81289500000 | 95231.433 | 15-JUL-14:00 | 32837.857 | 8089.532 | 7953.517 | 0 | 46350.526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 83451100000 | 88143.361 | 25-AUG-15:00 | 32837.857 | 8089.532 | 6986.884 | 0 | 40229.088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 63186800000 | 68439.677 | 14-SEP-14:00 | 32837.857 | 8089.532 | 4203.773 | 0 | 23308.515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 59964900000 | 57929.499 | 07-OCT-15:09 | 32837.857 | 8089.532 | 2708.743 | 0 | 14293.367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 58660700000 | 48436.724 | 02-NOV-16:00 | 32837.857 | 8089.532 | 657.148 | 0 | 3102.233 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 62390700000 | 46465.286 | 30-DEC-17:00 | 32837.857 | 8089.532 | 1787.942 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 787001000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 56017400000 | 45519.722 |  | 32837.857 | 8089.532 | 657.148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 83451100000 | 95231.433 |  | 32837.857 | 8089.532 | 7953.517 | 0 | 46350.526 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 14205.17 | 5068.52 | 0 | 19273.68
Cost per Total Building Area ($/m2) | 6.8 | 2.42 | 0 | 9.22
Cost per Net Conditioned Building Area ($/m2) | 6.8 | 2.42 | 0 | 9.22

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1315.59 | 629.37 | 629.37
Net Site Energy | 1315.59 | 629.37 | 629.37
Total Source Energy | 3207.97 | 1534.68 | 1534.68
Net Source Energy | 3207.97 | 1534.68 | 1534.68
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 572.57 | 0 | 0 | 0 | 0
Cooling | 28.68 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.86 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 28.35 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 743.02 | 572.57 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 23.99 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 23.99 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 13.77 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 13.77 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_2 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 78.94 | 0 | 90 | N
LGSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 78.94 | 180 | 90 | S
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
LGSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 78.94 | 0 | 90 | N
LGSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 78.94 | 180 | 90 | S
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.9 | 3.9 | 3.18 | 0.501 | 0.622 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.9 | 3.9 | 3.18 | 0.501 | 0.622 | No | LGSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW_SOUTH | 3.9 | 3.9 | 3.18 | 0.501 | 0.622 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.622 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.622 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.622 | No | SMSTORE4_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.622 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.622 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.622 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.622 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.622 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.622 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.622 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 3.18 | 0.501 | 0.622
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 3.18 | 0.501 | 0.622
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 25026.75 | 19987.75 | 5039 | 0.8 | 3.74
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12155.49 | 9708.05 | 2447.44 | 0.8 | 4.02
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10984.71 | 8772.99 | 2211.71 | 0.8 | 4.05
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10860.48 | 8673.78 | 2186.7 | 0.8 | 4.06
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10796.52 | 8622.7 | 2173.82 | 0.8 | 4.05
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20355.62 | 16257.12 | 4098.5 | 0.8 | 3.79
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10342.89 | 8260.4 | 2082.49 | 0.8 | 4.05
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10330.24 | 8250.3 | 2079.94 | 0.8 | 4.05
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10418.7 | 8320.95 | 2097.75 | 0.8 | 4.06
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14327.34 | 11442.61 | 2884.74 | 0.8 | 4.04
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 55870.76 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 25760.96 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 25679.4 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 25676.11 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 25696.98 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 50997.06 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 25697.31 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 25682.07 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 25788.62 | 0.8
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 30497.72 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.51 | 1653.42 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.73 | 836.53 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.66 | 769.7 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.66 | 760.99 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.65 | 756.51 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.23 | 1400.85 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.62 | 724.73 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.62 | 723.84 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.63 | 730.04 | 1 | Unitary Fans
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.87 | 985.99 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 22201.4871 | 33.0343 | 46.6883 | 0 | 0.0003 | 1106710 | 8929.1787
February | 18276.6417 | 28.0371 | 41.4824 | 0 | 0.0003 | 983482.0002 | 7432.1154
March | 17601.7859 | 28.6242 | 45.8179 | 0 | 0.0003 | 1086590 | 7314.51
April | 15240.5179 | 25.5242 | 42.3475 | 0 | 0.0003 | 1004410 | 6404.7983
May | 15100.0875 | 25.9365 | 44.2988 | 0 | 0.0003 | 1050790 | 6408.3684
June | 15240.09 | 26.7458 | 46.7666 | 0 | 0.0003 | 1109420 | 6522.7678
July | 16746.1317 | 29.7082 | 52.5432 | 0 | 0.0004 | 1246500 | 7198.2282
August | 16672.1588 | 29.525 | 52.1232 | 0 | 0.0004 | 1236530 | 7161.4089
September | 14894.8604 | 25.9299 | 44.9476 | 0 | 0.0003 | 1066240 | 6354.706
October | 15645.0463 | 26.4621 | 44.4131 | 0 | 0.0003 | 1053440 | 6599.9697
November | 16682.0904 | 27.1603 | 43.5386 | 0 | 0.0003 | 1032540 | 6935.3915
December | 20956.3516 | 31.7932 | 46.2818 | 0 | 0.0003 | 1097200 | 8487.5215
Annual Sum or Average | 205257.2492 | 338.481 | 551.2492 | 0 | 0.0039 | 13073800 | 85748.9644
Minimum of Months | 14894.8604 | 25.5242 | 41.4824 | 0 | 0.0003 | 983482.0002 | 6354.706
Maximum of Months | 22201.4871 | 33.0343 | 52.5432 | 0 | 0.0004 | 1246500 | 8929.1787
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 62896700000 | 46898.473 | 06-JAN-17:00 | 32837.857 | 8089.532 | 2221.129 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 55893600000 | 46012.896 | 22-FEB-17:00 | 32837.857 | 8089.532 | 1335.552 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 61753200000 | 46612.358 | 30-MAR-15:00 | 32837.857 | 8089.532 | 1473.193 | 0 | 4211.775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 57082900000 | 45364.617 | 14-APR-15:00 | 32837.857 | 8089.532 | 2354.694 | 0 | 2082.534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 59719100000 | 52622.154 | 16-MAY-15:00 | 32837.857 | 8089.532 | 2848.274 | 0 | 8846.491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 63050800000 | 71138.768 | 30-JUN-14:00 | 32837.857 | 8089.532 | 6492.27 | 0 | 23719.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 70841500000 | 73901.705 | 21-JUL-15:00 | 32837.857 | 8089.532 | 7237.566 | 0 | 25736.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 70274800000 | 67077.426 | 09-AUG-15:00 | 32837.857 | 8089.532 | 5813.354 | 0 | 20336.683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 60596700000 | 60426.721 | 02-SEP-15:50 | 32837.857 | 8089.532 | 4460.086 | 0 | 15039.246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 59869700000 | 50782.15 | 06-OCT-15:00 | 32837.857 | 8089.532 | 2458.674 | 0 | 7396.087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 58681500000 | 45127.097 | 27-NOV-17:00 | 32837.857 | 8089.532 | 449.753 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 62356400000 | 46824.044 | 11-DEC-17:00 | 32837.857 | 8089.532 | 2146.7 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 743017000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 55893600000 | 45127.097 |  | 32837.857 | 8089.532 | 449.753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 70841500000 | 73901.705 |  | 32837.857 | 8089.532 | 7237.566 | 0 | 25736.75 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 15991.3 | 4616.23 | 0 | 20607.54
Cost per Total Building Area ($/m2) | 7.65 | 2.21 | 0 | 9.86
Cost per Net Conditioned Building Area ($/m2) | 7.65 | 2.21 | 0 | 9.86

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1574.83 | 753.39 | 753.39
Net Site Energy | 1574.83 | 753.39 | 753.39
Total Source Energy | 3443.71 | 1647.46 | 1647.46
Net Source Energy | 3443.71 | 1647.46 | 1647.46
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 839.65 | 0 | 0 | 0 | 0
Cooling | 22.92 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.83 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 26.31 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 735.18 | 839.65 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 23.99 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 23.99 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 13.77 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 13.77 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_2 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 78.94 | 0 | 90 | N
LGSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 78.94 | 180 | 90 | S
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
LGSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 78.94 | 0 | 90 | N
LGSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 78.94 | 180 | 90 | S
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.49 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.49 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.49 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.49 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.9 | 3.9 | 3.18 | 0.501 | 0.49 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.9 | 3.9 | 3.18 | 0.501 | 0.49 | No | LGSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.49 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.49 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW_SOUTH | 3.9 | 3.9 | 3.18 | 0.501 | 0.49 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.49 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.49 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.49 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.49 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.49 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.49 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.49 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.49 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.49 | No | SMSTORE4_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.49 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.49 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.49 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.49 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.49 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.49 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.49 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.49 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.49 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.49 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.49 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.49 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.49 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.49 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.49 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.49 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 3.18 | 0.501 | 0.49 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 3.18 | 0.501 | 0.49 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 3.18 | 0.501 | 0.49
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 3.18 | 0.501 | 0.49
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 29717.98 | 21266.75 | 8451.22 | 0.72 | 3.55
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12902.17 | 9239.73 | 3662.43 | 0.72 | 3.78
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13102.27 | 9261.34 | 3840.93 | 0.71 | 3.75
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13150.51 | 9281.36 | 3869.15 | 0.71 | 3.75
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13199.28 | 9307.99 | 3891.29 | 0.71 | 3.74
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27210.93 | 18859.59 | 8351.33 | 0.69 | 3.49
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13624.04 | 9491.14 | 4132.9 | 0.7 | 3.72
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13627.3 | 9488.23 | 4139.07 | 0.7 | 3.72
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13702.63 | 9544.92 | 4157.71 | 0.7 | 3.73
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18123.63 | 12737.02 | 5386.61 | 0.7 | 3.73
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 60392.48 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 28059.37 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 27988.56 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 27985.8 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 28005.94 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 55629.65 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 28006.21 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 27990.71 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 28077.68 | 0.8
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 32697.18 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.39 | 1583.25 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.6 | 701.15 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.59 | 688.83 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.59 | 688.68 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.59 | 689.75 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.17 | 1334.93 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.59 | 689.76 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.59 | 688.94 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.6 | 693.56 | 1 | Unitary Fans
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.81 | 922.01 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 24311.7482 | 34.8674 | 41.7894 | 0 | 0.0003 | 27435.0286 | 9637.8008
February | 20629.5468 | 30.147 | 37.2853 | 0 | 0.0003 | 24481.6778 | 8231.6634
March | 18830.5882 | 29.5951 | 40.797 | 0 | 0.0003 | 26800.1679 | 7712.3733
April | 14807.0025 | 24.9188 | 37.4436 | 0 | 0.0003 | 24605.6562 | 6221.9067
May | 14142.9201 | 24.7171 | 38.7467 | 0 | 0.0003 | 25465.9254 | 6030.408
June | 13601.0998 | 24.5008 | 39.6413 | 0 | 0.0003 | 26056.8535 | 5869.2187
July | 15053.5958 | 27.4028 | 44.8043 | 0 | 0.0003 | 29451.6377 | 6523.2958
August | 15005.362 | 27.1853 | 44.2384 | 0 | 0.0003 | 29079.1863 | 6489.997
September | 13445.5662 | 23.8961 | 38.1314 | 0 | 0.0003 | 25063.1292 | 5771.0846
October | 14827.6546 | 25.4333 | 39.0581 | 0 | 0.0003 | 25668.671 | 6276.4451
November | 17486.7457 | 27.7809 | 38.8554 | 0 | 0.0003 | 25526.2128 | 7190.4518
December | 22755.2889 | 33.3425 | 41.417 | 0 | 0.0003 | 27195.0983 | 9088.3868
Annual Sum or Average | 204897.1187 | 333.787 | 482.208 | 0 | 0.0036 | 316829.2446 | 85043.032
Minimum of Months | 13445.5662 | 23.8961 | 37.2853 | 0 | 0.0003 | 24481.6778 | 5771.0846
Maximum of Months | 24311.7482 | 34.8674 | 44.8043 | 0 | 0.0003 | 29451.6377 | 9637.8008
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 63660900000 | 47015.776 | 09-JAN-17:00 | 32837.857 | 8089.532 | 2338.432 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 56807900000 | 46912.841 | 01-FEB-17:00 | 32837.857 | 8089.532 | 2235.498 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 62187800000 | 45723.106 | 08-MAR-17:00 | 32837.857 | 8089.532 | 1045.763 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 57095600000 | 43786.203 | 04-APR-15:00 | 32837.857 | 8089.532 | 564.425 | 0 | 2294.389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 59091800000 | 50929.351 | 31-MAY-15:00 | 32837.857 | 8089.532 | 1865.992 | 0 | 8135.969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 60463000000 | 63661.822 | 14-JUN-14:00 | 32837.857 | 8089.532 | 3883.697 | 0 | 18850.736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 68340300000 | 76058.088 | 08-JUL-15:30 | 32837.857 | 8089.532 | 5925.117 | 0 | 29205.582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 67476100000 | 75567.352 | 12-AUG-14:00 | 32837.857 | 8089.532 | 5744.295 | 0 | 28895.668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 58157100000 | 58960.878 | 07-SEP-14:00 | 32837.857 | 8089.532 | 3177.812 | 0 | 14855.677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 59562200000 | 53412.205 | 07-OCT-14:00 | 32837.857 | 8089.532 | 2231.718 | 0 | 10253.098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 59231700000 | 46233.885 | 24-NOV-17:00 | 32837.857 | 8089.532 | 1556.541 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 63104200000 | 46631.336 | 30-DEC-17:00 | 32837.857 | 8089.532 | 1953.992 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 735178000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 56807900000 | 43786.203 |  | 32837.857 | 8089.532 | 564.425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 68340300000 | 76058.088 |  | 32837.857 | 8089.532 | 5925.117 | 0 | 29205.582 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 12780.8 | 6627.67 | 0 | 19408.47
Cost per Total Building Area ($/m2) | 6.11 | 3.17 | 0 | 9.28
Cost per Net Conditioned Building Area ($/m2) | 6.11 | 3.17 | 0 | 9.28

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2350.04 | 1124.25 | 1124.25
Net Site Energy | 2350.04 | 1124.25 | 1124.25
Total Source Energy | 4377.56 | 2094.21 | 2094.21
Net Source Energy | 4377.56 | 2094.21 | 2094.21
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1619.67 | 0 | 0 | 0 | 0
Cooling | 5.76 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.47 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 39.01 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 730.37 | 1619.67 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 23.99 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 23.99 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 13.77 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 13.77 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_2 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 78.94 | 0 | 90 | N
LGSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 78.94 | 180 | 90 | S
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOFS | 0.3 | 0.273 | 0.29 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOFS | 0.3 | 0.273 | 0.29 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOFS | 0.3 | 0.273 | 0.29 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOFS | 0.3 | 0.273 | 0.29 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOFS | 0.3 | 0.273 | 0.29 | 174.19 | 270 | 0
LGSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 78.94 | 0 | 90 | N
LGSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 78.94 | 180 | 90 | S
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOFS | 0.3 | 0.273 | 0.29 | 348.39 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOFS | 0.3 | 0.273 | 0.29 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOFS | 0.3 | 0.273 | 0.29 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOFS | 0.3 | 0.273 | 0.29 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOFS | 0.3 | 0.273 | 0.29 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 2.58 | 0.504 | 0.49 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 2.58 | 0.504 | 0.49 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 2.58 | 0.504 | 0.49 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 2.58 | 0.504 | 0.49 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.9 | 3.9 | 2.58 | 0.504 | 0.49 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.9 | 3.9 | 2.58 | 0.504 | 0.49 | No | LGSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 2.58 | 0.504 | 0.49 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 2.58 | 0.504 | 0.49 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW_SOUTH | 3.9 | 3.9 | 2.58 | 0.504 | 0.49 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 2.58 | 0.504 | 0.49 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 2.58 | 0.504 | 0.49 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 2.58 | 0.504 | 0.49 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 2.58 | 0.504 | 0.49 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 2.58 | 0.504 | 0.49 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 2.58 | 0.504 | 0.49 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 2.58 | 0.504 | 0.49 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 2.58 | 0.504 | 0.49 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 2.58 | 0.504 | 0.49 | No | SMSTORE4_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 2.58 | 0.504 | 0.49 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 2.58 | 0.504 | 0.49 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 2.58 | 0.504 | 0.49 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 2.58 | 0.504 | 0.49 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.88 | 3.88 | 2.58 | 0.504 | 0.49 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.88 | 3.88 | 2.58 | 0.504 | 0.49 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 2.58 | 0.504 | 0.49 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 2.58 | 0.504 | 0.49 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 2.58 | 0.504 | 0.49 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 2.58 | 0.504 | 0.49 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 2.58 | 0.504 | 0.49 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 2.58 | 0.504 | 0.49 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 2.58 | 0.504 | 0.49 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 2.58 | 0.504 | 0.49 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 2.58 | 0.504 | 0.49 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 2.58 | 0.504 | 0.49 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 2.58 | 0.504 | 0.49 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.88 | 2.58 | 0.504 | 0.49 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 2.58 | 0.504 | 0.49
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 2.58 | 0.504 | 0.49
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 28441.2 | 22714.71 | 5726.49 | 0.8 | 3.74
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12086.15 | 9652.67 | 2433.48 | 0.8 | 4.03
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12024.18 | 9603.17 | 2421.01 | 0.8 | 4.04
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12021.78 | 9601.26 | 2420.52 | 0.8 | 4.04
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12038.59 | 9614.68 | 2423.91 | 0.8 | 4.04
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 23764.07 | 18979.3 | 4784.77 | 0.8 | 3.75
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12038.82 | 9614.87 | 2423.95 | 0.8 | 4.04
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12026.09 | 9604.7 | 2421.39 | 0.8 | 4.04
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12104.31 | 9667.17 | 2437.14 | 0.8 | 4.03
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16654.44 | 13301.16 | 3353.28 | 0.8 | 4.04
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 78377.54 | 0.78
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 36270.44 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 36185.74 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 36182.46 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 36205.43 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 71983.1 | 0.78
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 36205.75 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 36188.34 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 36295.25 | 0.8
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 42516.36 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.72 | 1879 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.73 | 831.75 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.73 | 827.49 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.73 | 827.32 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.73 | 828.48 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.44 | 1570 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.73 | 828.5 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.73 | 827.62 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.73 | 833 | 1 | Unitary Fans
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.01 | 1146.14 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 32692.1597 | 34.3065 | 96.9546 | 0 | 0.0004 | 19439.5879 | 12027.2435
February | 27041.2351 | 28.615 | 85.1845 | 0 | 0.0003 | 17081.3874 | 9984.998
March | 21956.2451 | 24.2562 | 90.5514 | 0 | 0.0003 | 18164.5807 | 8264.6634
April | 15001.943 | 17.4757 | 80.7462 | 0 | 0.0003 | 16202.3954 | 5785.7992
May | 12313.2895 | 15.027 | 80.5696 | 0 | 0.0003 | 16169.7034 | 4854.0122
June | 11415.3507 | 14.1653 | 79.5925 | 0 | 0.0003 | 15974.3864 | 4536.0671
July | 11652.744 | 14.5194 | 82.4932 | 0 | 0.0003 | 16556.7484 | 4639.5603
August | 12207.3595 | 15.0952 | 84.0088 | 0 | 0.0003 | 16860.5712 | 4842.649
September | 12690.2253 | 15.3646 | 80.4759 | 0 | 0.0003 | 16150.4974 | 4983.7729
October | 16816.6763 | 19.4001 | 86.5474 | 0 | 0.0003 | 17365.6866 | 6456.5121
November | 24352.7627 | 26.4026 | 89.9503 | 0 | 0.0003 | 18041.3913 | 9089.6283
December | 29250.9355 | 31.1423 | 96.1 | 0 | 0.0004 | 19271.4819 | 10830.0196
Annual Sum or Average | 227390.9263 | 255.7697 | 1033.1743 | 0 | 0.0037 | 207278.4181 | 86294.9255
Minimum of Months | 11415.3507 | 14.1653 | 79.5925 | 0 | 0.0003 | 15974.3864 | 4536.0671
Maximum of Months | 32692.1597 | 34.3065 | 96.9546 | 0 | 0.0004 | 19439.5879 | 12027.2435
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 68497500000 | 50790.878 | 13-JAN-09:09 | 32837.857 | 8089.532 | 6113.534 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 60188100000 | 50506.977 | 03-FEB-09:09 | 32837.857 | 8089.532 | 5829.634 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 64004900000 | 45691.564 | 02-MAR-17:00 | 32837.857 | 8089.532 | 1014.22 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 57090900000 | 43889.049 | 10-APR-08:09 | 32837.857 | 8089.532 | 2961.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 56975700000 | 46289.569 | 24-MAY-14:00 | 32837.857 | 8089.532 | 1363.582 | 0 | 3998.597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 56287500000 | 51859.118 | 21-JUN-15:00 | 32837.857 | 8089.532 | 2526.955 | 0 | 8404.774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 58339500000 | 57229.739 | 29-JUL-15:00 | 32837.857 | 8089.532 | 3650.04 | 0 | 12652.309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 59410000000 | 51912.109 | 15-AUG-14:00 | 32837.857 | 8089.532 | 2543.533 | 0 | 8441.186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 56908000000 | 43184.42 | 02-SEP-15:00 | 32837.857 | 8089.532 | 552.616 | 0 | 1704.415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 61189900000 | 47840.804 | 27-OCT-08:09 | 32837.857 | 8089.532 | 3163.46 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 63570800000 | 48552.395 | 09-NOV-09:09 | 32837.857 | 8089.532 | 3875.051 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 67905200000 | 50175.643 | 29-DEC-09:09 | 32837.857 | 8089.532 | 5498.3 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 730368000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 56287500000 | 43184.42 |  | 32837.857 | 8089.532 | 552.616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 68497500000 | 57229.739 |  | 32837.857 | 8089.532 | 6113.534 | 0 | 12652.309 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 20246.99 | 6656.63 | 0 | 26903.61
Cost per Total Building Area ($/m2) | 9.69 | 3.18 | 0 | 12.87
Cost per Net Conditioned Building Area ($/m2) | 9.69 | 3.18 | 0 | 12.87

## Picture
DOE Commercial Building Benchmark - Strip Mall

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | 11.15 | 70.85 | 3694.32
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | 9.85
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 5.25
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | 7.2 | 46.3 | 2414.21
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | 7.5
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 2.8
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | 13.7 | 89.4 | 4661.57
|  |  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15 | 12.15
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 8.75
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.22 | 0.64 | 0.74 | 0.68 | 0.68 | 0.71 | 0.72 | 0.72 | 0.73 | 0.68 | 0.68 | 0.58 | 0.54 | 0 | 0 | 0 | 8.44 | 52.69 | 2747.41
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.21 | 0.56 | 0.66 | 0.68 | 0.68 | 0.69 | 0.7 | 0.69 | 0.66 | 0.58 | 0.47 | 0.43 | 0.43 | 0.08 | 0 | 0 | 7.61
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.13 | 0.35 | 0.37 | 0.37 | 0.39 | 0.41 | 0.38 | 0.34 | 0.03 | 0 | 0 | 0 | 0 | 0 | 2.88
INFIL_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 9 | 68 | 3545.71
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 15
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 16.5 | 118 | 6152.86
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19.5
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0.23 | 0.13 | 0.08 | 6.62 | 44.59 | 2325.05
|  |  | Sat, WinterDesign | 0.11 | 0.1 | 0.08 | 0.06 | 0.06 | 0.06 | 0.07 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0.16 | 0.13 | 6.9
|  |  | Sun, Hol, Other | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07 | 0.1 | 0.12 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.1 | 0.06 | 4.59
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 102 | 5318.57
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 11
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 102 | 5318.57
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 11
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 455.4 | 3171.6 | 165376.29
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8
|  |  | Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 433.8
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 630 | 4428 | 230888.57
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 654
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 102 | 5318.57
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 11
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0