## BuildingSummary
Building Summary Super Market new construction version 1.1_3.1
|  | Value | Data Source
Program
| Building Name | Benchmark Super Market
| Available Fuel Types | gas, electricity
| Principal Building Activity | Food Sales
Form
| Total Floor Area (ft2) | 45001.6 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 1.5
| Number of Floors | 1
| Window Fraction (Window to Wall Ratio) | South: 0.362 East: 0.00 North: 0.00 West: 0.00 Total: 0.109
| Skylight/TDD Percentage | 0.00%
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | Office, DryStorage, Deli, Sales, Produce, Bakery
| Floor to Ceiling Height (ft) | 6.1
| Roof type | Insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Mass wall | 2003 CBECS
| Gross Dimensions - Total Area (ft2) | 17320.85
| Net Dimensions - Total Area (ft2) | 15440.29
| Wall to Skin Ratio | 0.28
Roof
| Construction Type | Insulation entirely above deck | 2003 CBECS
| Gross Dimensions - Total Area (ft2) | 45001.6
| Net Dimensions - Total Area (ft2) | 45001.6
| Roof to Skin Ratio | 0.72
Window
| Dimensions - Total Area (ft2) | South: 1,880.5 East: 0.00 North: 0.00 West: 0.00 Total: 1,880.5
| Operable area (ft2) | 0
Skylights/TDD
| Dimensions - Total Area (ft2) | 0
| Operable area (ft2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab-on-grade
| Dimensions - Total Area (ft2) | 45001.6
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
Internal Mass
| Construction | 6 inch wood
| Dimensions - Total Area (ft2) | 90003
| Thermal Properties (lb/ft2 ) | 16.6
Air Barrier System
| Infiltration (ACH) | 0.25 | See Benchmark Technical Report
HVAC
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | Unitary DX | 2003 CBECS
| Fan Control | Constant volume | 2003 CBECS
Service Water Heating
| SWH Type | N/A
| Fuel | N/A
| Thermal Efficiency (%) | N/A
| Temperature Setpoint (ºF ) | N/A
| Water Consumption (gal ) | N/A

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Office | Yes | 1 | 88.84 | 541.72 | 6.0977 | 115.08 | 0 | 18.5806 | 4.7813 | 11.836 | 8.07 | 0 | 0 | 2.5 | 0.3 | 38.6053 | 0 | 0.40969
DryStorage | Yes | 1 | 621.89 | 3792.03 | 6.0976 | 477.24 | 0 | 27.8709 | 22.3132 | 8.608 | 8.07 | 0 | 0 | 3.8 | 0.6 | 457.9242 | 0 | 0.31547
Deli | Yes | 1 | 224.72 | 1370.24 | 6.0975 | 138.43 | 0 | 11.6129 | 19.3509 | 18.292 | 53.8 | 26.9 | 18.927 | 3.8 | 0.6 | 208.3655 | 0 | 0.28845
Sales | Yes | 1 | 2324.94 | 14176.6 | 6.0976 | 323.52 | 174.7 | 11.6129 | 200.2034 | 18.292 | 5.38 | 0 | 0 | 3.8 | 0.6 | 2155.7368 | 0 | 0.20333
Produce | Yes | 1 | 711.36 | 4337.61 | 6.0976 | 366.18 | 0 | 11.6129 | 61.2561 | 18.292 | 5.38 | 0 | 0 | 3.8 | 0.6 | 659.589 | 0 | 0.27037
Bakery | Yes | 1 | 209.04 | 1274.65 | 6.0976 | 189.13 | 0 | 11.6129 | 18.0007 | 18.292 | 53.8 | 26.9 | 18.927 | 3.8 | 0.6 | 193.8266 | 1179.8675 | 0.33998
Total Conditioned Zones |  |  | 4180.79 | 25492.85 |  | 1609.58 | 174.7 |  | 325.9056 | [6 empty] | 3714.0474 | 1179.8675
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7A | 8A
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fabric
Exterior walls
| Construction Type | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall
| R-value (m2·K / W) | 0.38314 | 0.38314 | 0.38314 | 1.1682 | 1.1682 | 1.1682 | 1.1682 | 1.1682 | 1.1682 | 1.1682 | 1.4327 | 1.4327 | 1.692 | 1.692 | 1.9531 | 2.2026
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 3.663
Window
| U-Factor (W / m2·K) | 6.49 | 6.49 | 6.49 | 3.18 | 3.18 | 3.18 | 6.49 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 2.58
| SHGC | 0.25 | 0.25 | 0.25 | 0.262 | 0.262 | 0.262 | 0.34 | 0.402 | 0.402 | 0.402 | 0.402 | 0.402 | 0.402 | 0.402 | 0.501 | 0.504
| Visible transmittance | 0.25 | 0.25 | 0.25 | 0.318 | 0.318 | 0.318 | 0.34 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.49 | 0.49
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade
| R-value (m2·K / W) | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC:1_COOLC DXCOIL | 11.3055 | 10.8724 | 11.9357 | 9.2542 | 5.8691 | 7.9082 | 6.2998 | 10.4513 | 9.5484 | 7.4223 | 12.8292 | 11.02 | 13.175 | 11.9298 | 11.1956 | 12.8697
| PSZ-AC:2_COOLC DXCOIL | 66.2022 | 69.5011 | 52.967 | 65.6646 | 28.5949 | 42.1944 | 35.2635 | 70.0356 | 51.4625 | 46.0926 | 81.6451 | 59.3084 | 88.2804 | 64.9744 | 92.0284 | 70.5645
| PSZ-AC:3_COOLC DXCOIL | 47.7668 | 45.6555 | 45.2606 | 43.2833 | 39.7046 | 42.1689 | 27.5689 | 42.0518 | 43.4397 | 28.9698 | 40.2726 | 35.912 | 39.0472 | 33.2593 | 29.9592 | 28.429
| PSZ-AC:4_COOLC DXCOIL | 136.4712 | 206.3424 | 149.1267 | 218.8193 | 117.8973 | 219.2231 | 130.259 | 227.2258 | 172.9815 | 170.0675 | 257.8551 | 192.6483 | 274.8934 | 205.5666 | 291.3793 | 214.0713
| PSZ-AC:5_COOLC DXCOIL | 71.3495 | 72.8124 | 54.1402 | 70.15 | 33.2032 | 45.8529 | 39.0997 | 74.2951 | 55.0173 | 44.3465 | 85.093 | 61.9653 | 91.6036 | 67.6013 | 82.2411 | 72.8034
| PSZ-AC:6_COOLC DXCOIL | 42.0724 | 41.8204 | 44.9162 | 41.2225 | 38.6342 | 41.5058 | 27.056 | 39.6067 | 42.4089 | 28.7464 | 38.0872 | 35.3336 | 38.1422 | 32.9198 | 29.2537 | 27.8344
Heating (kW)
| PSZ-AC:1_HEATC | 4.1433 | 4.243 | 4.9815 | 3.42 | 2.5776 | 3.2292 | 2.7948 | 3.8222 | 3.4708 | 3.2576 | 4.4278 | 4.0254 | 4.7145 | 4.6075 | 4.7864 | 5.7065
| PSZ-AC:2_HEATC | 30.9646 | 42.9144 | 40.8389 | 43.7382 | 20.867 | 35.6464 | 28.4439 | 51.9294 | 45.4817 | 39.6697 | 68.1128 | 57.0287 | 75.314 | 70.829 | 77.9612 | 99.5863
| PSZ-AC:3_HEATC | 23.4948 | 27.7531 | 25.4817 | 28.4677 | 22.5601 | 25.023 | 18.8521 | 30.0477 | 25.1355 | 22.2623 | 32.6717 | 25.6751 | 34.5699 | 29.1886 | 31.3076 | 37.2074
| PSZ-AC:4_HEATC | 63.8313 | 127.409 | 105.9288 | 145.7522 | 86.0349 | 123.4581 | 105.0682 | 168.4815 | 152.8781 | 134.0837 | 223.352 | 203.0866 | 257.3274 | 251.0883 | 277.324 | 351.5875
| PSZ-AC:5_HEATC | 33.3721 | 44.959 | 42.3101 | 46.7258 | 24.2298 | 38.7372 | 31.5382 | 55.0877 | 48.6234 | 42.6581 | 73.7069 | 63.1944 | 83.5834 | 78.5472 | 86.6378 | 110.6089
| PSZ-AC:6_HEATC | 19.9932 | 22.0789 | 21.6522 | 21.9985 | 19.096 | 20.2893 | 14.8459 | 22.7245 | 19.4655 | 16.7941 | 23.4393 | 18.4131 | 24.279 | 19.9948 | 20.7332 | 23.4067
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC:1_COOLC DXCOIL | 3.87 | 3.93 | 4.03 | 3.88 | 4.04 | 4.06 | 4.05 | 3.84 | 4.06 | 4.06 | 3.79 | 4.06 | 3.83 | 4.03 | 4.06 | 4.04
| PSZ-AC:2_COOLC DXCOIL | 3.19 | 3.19 | 3.47 | 3.19 | 3.75 | 3.47 | 3.74 | 3.19 | 3.47 | 3.37 | 3.12 | 4.37 | 3.53 | 4.37 | 3.53 | 4.18
| PSZ-AC:3_COOLC DXCOIL | 3.38 | 3.42 | 3.47 | 3.45 | 3.47 | 3.47 | 3.75 | 3.44 | 3.47 | 3.74 | 3.44 | 3.74 | 3.74 | 3.74 | 3.74 | 3.75
| PSZ-AC:4_COOLC DXCOIL | 3.51 | 3.49 | 3.94 | 3.49 | 4.18 | 3.49 | 4.14 | 3.35 | 3.95 | 3.76 | 3.27 | 3.95 | 3.27 | 3.95 | 3.27 | 3.94
| PSZ-AC:5_COOLC DXCOIL | 3.12 | 3.12 | 3.47 | 3.19 | 3.75 | 3.47 | 3.74 | 3.12 | 3.47 | 3.47 | 3.12 | 4.36 | 3.53 | 4.32 | 3.72 | 4.18
| PSZ-AC:6_COOLC DXCOIL | 3.45 | 3.47 | 3.47 | 3.47 | 3.74 | 3.47 | 3.74 | 3.47 | 3.47 | 3.75 | 3.74 | 3.74 | 3.74 | 3.74 | 3.75 | 3.74
Heating Efficiency (%)
| PSZ-AC:1_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC:2_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78 | 0.8 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:3_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC:4_HEATC | 0.8 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:5_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78 | 0.8 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:6_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
HVAC Control - Economizer
| PSZ-AC:1_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC:2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC:3_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ-AC:4_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC:5_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC:6_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
Fan Max Flow Rate (m3/s )
| BAKERY EXHAUST FAN | 1.18 | 1.18 | 1.18 | 1.18 | 1.18 | 1.18 | 1.18 | 1.18 | 1.18 | 1.18 | 1.18 | 1.18 | 1.18 | 1.18 | 1.18 | 1.18
| PSZ-AC:1_FAN | 0.58 | 0.59 | 0.72 | 0.48 | 0.35 | 0.48 | 0.38 | 0.52 | 0.58 | 0.45 | 0.61 | 0.67 | 0.65 | 0.72 | 0.68 | 0.78
| PSZ-AC:2_FAN | 2.67 | 2.8 | 3.2 | 2.64 | 1.73 | 2.55 | 2.13 | 2.82 | 3.11 | 2.49 | 3.29 | 3.58 | 3.56 | 3.93 | 3.71 | 4.26
| PSZ-AC:3_FAN | 2.6 | 2.62 | 2.73 | 2.57 | 2.4 | 2.55 | 1.67 | 2.46 | 2.62 | 1.75 | 2.36 | 2.17 | 2.36 | 2.01 | 1.81 | 1.72
| PSZ-AC:4_FAN | 5.5 | 8.31 | 8.19 | 8.81 | 7.12 | 8.83 | 7.87 | 9.15 | 10.45 | 8.42 | 10.38 | 11.64 | 11.07 | 12.42 | 11.73 | 12.93
| PSZ-AC:5_FAN | 2.87 | 2.93 | 3.27 | 2.82 | 2.01 | 2.77 | 2.36 | 2.99 | 3.32 | 2.68 | 3.43 | 3.74 | 3.69 | 4.08 | 3.86 | 4.4
| PSZ-AC:6_FAN | 2.5 | 2.53 | 2.71 | 2.49 | 2.33 | 2.51 | 1.63 | 2.39 | 2.56 | 1.74 | 2.3 | 2.13 | 2.3 | 1.99 | 1.77 | 1.68
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.079738 | 0.10859 | 0.077009 | 0.098987 | 0.12276 | 0.095213 | 0.14452 | 0.070086 | 0.037051 | 0.071205 | 0.096077 | 0.037051 | 0.054097 | 0.070359 | 0.053955 | 0.089076
| Total Cost ($/m2) | 38.2 | 49.23 | 32.56 | 40.67 | 48.19 | 36.92 | 53.28 | 27.6 | 13.83 | 25.75 | 36.76 | 13.88 | 21.14 | 26.09 | 20.12 | 32.9
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011447 | 0.0080851 | 0.0083045 | 0.0098404 | 0.008513 | 0.0077955 | 0.0084681 | 0.0097458 | 0.0069655 | 0.0083595 | 0.0084422 | 0.0069908 | 0.0078631 | 0.0082976 | 0.0078772 | 0.0041481
| Total Cost ($/m2) | 1.13 | 2.53 | 2.58 | 4.98 | 2.91 | 3.46 | 5.19 | 7.3 | 4.36 | 6.74 | 8.11 | 5.5 | 8.93 | 8.66 | 10.93 | 8.44
Total Utility Costs
| Cost Intensity ($/m2) | 39.33 | 51.75 | 35.14 | 45.65 | 51.11 | 40.38 | 58.47 | 34.89 | 18.2 | 32.49 | 44.87 | 19.38 | 30.06 | 34.75 | 31.05 | 41.35
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 162113.8889 | 125694.4444 | 122658.3333 | 61922.2222 | 13380.5556 | 72613.8889 | 4011.1111 | 49122.2222 | 31861.1111 | 5636.1111 | 30077.7778 | 18933.3333 | 29947.2222 | 11508.3333 | 10911.1111 | 4727.7778
| Interior Lighting | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778
| Exterior Lighting | 18927.7778 | 18919.4444 | 18916.6667 | 18913.8889 | 18900 | 18894.4444 | 18905.5556 | 18894.4444 | 18900 | 18863.8889 | 18897.2222 | 18886.1111 | 18883.3333 | 18880.5556 | 18869.4444 | 18752.7778
| Interior Equipment | 188483.3333 | 188483.3333 | 188483.3333 | 188483.3333 | 188483.3333 | 188483.3333 | 188483.3333 | 188483.3333 | 188483.3333 | 188483.3333 | 188483.3333 | 188483.3333 | 188483.3333 | 188483.3333 | 188483.3333 | 188483.3333
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 134525 | 166033.3333 | 172177.7778 | 169219.4444 | 136961.1111 | 168677.7778 | 139777.7778 | 176763.8889 | 187980.5556 | 152358.3333 | 189930.5556 | 240452.7778 | 242472.2222 | 258233.3333 | 251105.5556 | 288444.4444
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 1239316.6667 | 1136658.3333 | 1006083.3333 | 1019961.1111 | 1024094.4444 | 913294.4444 | 930822.2222 | 953505.5556 | 874472.2222 | 887038.8889 | 912769.4444 | 840613.8889 | 894441.6667 | 813833.3333 | 830263.8889 | 784536.1111
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 2002747.2222 | 1895169.4444 | 1767697.2222 | 1717880.5556 | 1641194.4444 | 1621341.6667 | 1541380.5556 | 1646147.2222 | 1561075 | 1511761.1111 | 1599538.8889 | 1566750 | 1633608.3333 | 1550316.6667 | 1559013.8889 | 1544325
Gas (MJ)
| Heating | 101550 | 995150 | 986290 | 1800010 | 1116780 | 1540430 | 2246770 | 2813310 | 2303150 | 3054860 | 3700540 | 2970800 | 4427360 | 4043250 | 5481400 | 8185990
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 294920 | 294920 | 294920 | 294920 | 294920 | 294920 | 294920 | 294920 | 294920 | 294920 | 294920 | 294920 | 294920 | 294920 | 294920 | 294920
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 15870 | 17830 | 16700 | 19730 | 19360 | 18060 | 20980 | 21220 | 20930 | 21990 | 22520 | 22460 | 23650 | 23860 | 25520 | 27770
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 412330 | 1307900 | 1297910 | 2114660 | 1431050 | 1853410 | 2562660 | 3129450 | 2618990 | 3371770 | 4017980 | 3288180 | 4745930 | 4362020 | 5801830 | 8508680
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 7622220 | 8130510 | 7661620 | 8299020 | 7339360 | 7690250 | 8111630 | 9055570 | 8238870 | 8814110 | 9776320 | 8928470 | 10626920 | 9943160 | 11414280 | 14068250
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 139.5932 | 108.2331 | 105.6188 | 53.3201 | 11.5217 | 62.5265 | 3.4539 | 42.2982 | 27.435 | 4.8531 | 25.8994 | 16.3031 | 25.787 | 9.9096 | 9.3954 | 4.071
| Interior Lighting (elec) | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453
| Exterior Lighting (elec) | 16.2984 | 16.2912 | 16.2888 | 16.2864 | 16.2744 | 16.2697 | 16.2792 | 16.2697 | 16.2744 | 16.2433 | 16.272 | 16.2625 | 16.2601 | 16.2577 | 16.2481 | 16.1477
| Interior Equipment (elec) | 162.2995 | 162.2995 | 162.2995 | 162.2995 | 162.2995 | 162.2995 | 162.2995 | 162.2995 | 162.2995 | 162.2995 | 162.2995 | 162.2995 | 162.2995 | 162.2995 | 162.2995 | 162.2995
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 115.837 | 142.9682 | 148.2591 | 145.7117 | 117.9346 | 145.2453 | 120.36 | 152.2081 | 161.8665 | 131.1929 | 163.5456 | 207.0494 | 208.7883 | 222.3599 | 216.2223 | 248.3741
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 1067.1524 | 978.7552 | 866.3195 | 878.2694 | 881.8286 | 786.4207 | 801.5136 | 821.0458 | 752.9917 | 763.8126 | 785.9687 | 723.8369 | 770.187 | 700.7766 | 714.9247 | 675.5494
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1724.5281 | 1631.8949 | 1522.131 | 1479.2348 | 1413.2018 | 1396.107 | 1327.2539 | 1417.4666 | 1344.2125 | 1301.7492 | 1377.333 | 1349.0991 | 1406.6696 | 1334.9487 | 1342.4377 | 1329.7893
Gas (MJ/m2)
| Heating (gas) | 24.2897 | 238.0292 | 235.91 | 430.543 | 267.1218 | 368.4543 | 537.4032 | 672.9135 | 550.8887 | 730.6897 | 885.1294 | 710.5834 | 1058.9769 | 967.1019 | 1311.0919 | 1958.0008
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 70.5417 | 70.5417 | 70.5417 | 70.5417 | 70.5417 | 70.5417 | 70.5417 | 70.5417 | 70.5417 | 70.5417 | 70.5417 | 70.5417 | 70.5417 | 70.5417 | 70.5417 | 70.5417
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 3.7959 | 4.2647 | 3.9945 | 4.7192 | 4.6307 | 4.3198 | 5.0182 | 5.0756 | 5.0062 | 5.2598 | 5.3865 | 5.3722 | 5.6568 | 5.7071 | 6.1041 | 6.6423
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 98.6249 | 312.8356 | 310.4461 | 505.8039 | 342.2918 | 443.3157 | 612.9607 | 748.5308 | 626.4342 | 806.4911 | 961.0576 | 786.4973 | 1135.1754 | 1043.3483 | 1387.7353 | 2035.1847
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 1823.153 | 1944.7305 | 1832.5771 | 1985.0363 | 1755.496 | 1839.4251 | 1940.2146 | 2165.9949 | 1970.6491 | 2108.2403 | 2338.3906 | 2135.594 | 2541.845 | 2378.2969 | 2730.173 | 3364.9741
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 361.1523 | 353.3842 | 304.6628 | 328.6586 | 306.1255 | 295.6714 | 307.4702 | 308.1635 | 290.7809 | 300.3805 | 292.7577 | 301.6177 | 296.2664 | 299.8601 | 293.4396 | 300.8461
| Feb | 362.818 | 341.3489 | 313.4079 | 316.5509 | 314.3978 | 307.7263 | 314.044 | 298.2451 | 293.3899 | 291.5894 | 293.046 | 297.737 | 295.7081 | 308.318 | 298.5331 | 296.9084
| Mar | 377.4616 | 352.9068 | 342.7345 | 330.9132 | 312.4093 | 304.5732 | 300.3136 | 338.2238 | 297.6044 | 300.8577 | 316.7307 | 312.9832 | 309.3465 | 310.1022 | 299.8423 | 300.2644
| Apr | 389.7042 | 377.4025 | 347.9722 | 351.5498 | 315.8587 | 345.3454 | 310.6046 | 336.4281 | 318.6498 | 306.0863 | 318.2335 | 320.1479 | 333.4294 | 307.7808 | 307.1268 | 299.6265
| May | 400.1055 | 421.0558 | 384.2789 | 386.7903 | 335.4247 | 358.0595 | 321.3191 | 363.4957 | 336.7606 | 329.1335 | 363.0662 | 339.6592 | 390.0533 | 329.5218 | 322.5923 | 320.3791
| Jun | 422.1291 | 424.9868 | 429.9611 | 401.0579 | 333.67 | 394.6767 | 326.0296 | 425.9452 | 358.7444 | 327.1875 | 393.0126 | 355.354 | 415.6365 | 361.7623 | 371.366 | 346.2166
| Jul | 412.7081 | 434.8202 | 438.5733 | 427.0062 | 344.5211 | 400.8779 | 340.759 | 432.2698 | 372.0518 | 346.5534 | 421.0721 | 371.5273 | 415.4628 | 368.9451 | 398.3478 | 346.1776
| Aug | 415.2136 | 433.5842 | 432.08 | 406.6778 | 353.2137 | 412.6344 | 337.067 | 428.5621 | 381.9522 | 343.5403 | 415.5429 | 372.586 | 416.3052 | 364.5548 | 379.0257 | 344.5342
| Sep | 402.1428 | 415.0233 | 415.9116 | 382.9802 | 348.3727 | 381.3943 | 344.2885 | 375.467 | 343.4392 | 346.6428 | 366.2472 | 346.7498 | 363.2358 | 348.0663 | 349.1271 | 314.7479
| Oct | 401.4227 | 385.9496 | 368.4512 | 351.1409 | 335.5966 | 346.2305 | 321.4896 | 351.0025 | 329.7485 | 310.1248 | 340.9955 | 322.8224 | 325.1125 | 323.2337 | 317.8955 | 306.3988
| Nov | 380.29 | 367.2344 | 329.4328 | 326.5664 | 322.8619 | 304.3581 | 315.2743 | 341.7257 | 298.175 | 314.718 | 342.8028 | 300.7052 | 310.4139 | 301.1034 | 317.1613 | 297.4704
| Dec | 364.552 | 353.4637 | 321.2618 | 326.2862 | 313.4564 | 294.1893 | 307.3362 | 309.2039 | 289.503 | 294.4455 | 299.9914 | 296.1991 | 299.9422 | 298.0961 | 297.4937 | 301.6529
Time of Peak Electrical Demand
| Jan | 23-JAN-18:10 | 20-JAN-18:10 | 27-JAN-18:10 | 24-JAN-18:10 | 10-JAN-18:10 | 23-JAN-18:10 | 05-JAN-18:10 | 09-JAN-11:20 | 02-JAN-11:20 | 14-JAN-11:20 | 17-JAN-18:10 | 23-JAN-11:20 | 30-JAN-11:20 | 23-JAN-11:20 | 13-JAN-11:20 | 03-JAN-11:09
| Feb | 23-FEB-11:00 | 15-FEB-18:10 | 28-FEB-18:10 | 21-FEB-18:10 | 13-FEB-11:39 | 10-FEB-18:10 | 15-FEB-18:10 | 13-FEB-11:20 | 14-FEB-18:10 | 24-FEB-18:10 | 28-FEB-11:20 | 11-FEB-11:20 | 21-FEB-11:20 | 02-FEB-18:10 | 21-FEB-11:20 | 27-FEB-11:20
| Mar | 13-MAR-17:10 | 28-MAR-17:10 | 17-MAR-17:10 | 29-MAR-17:10 | 04-MAR-11:39 | 31-MAR-17:10 | 27-MAR-17:10 | 09-MAR-18:10 | 08-MAR-18:10 | 30-MAR-17:10 | 14-MAR-17:10 | 30-MAR-17:10 | 23-MAR-17:10 | 30-MAR-17:10 | 30-MAR-10:20 | 09-MAR-11:20
| Apr | 03-APR-17:10 | 29-APR-17:10 | 25-APR-17:10 | 14-APR-17:10 | 10-APR-10:50 | 21-APR-17:10 | 29-APR-10:39 | 04-APR-17:10 | 21-APR-17:10 | 29-APR-17:10 | 10-APR-10:09 | 25-APR-17:10 | 01-APR-17:10 | 24-APR-10:20 | 14-APR-10:20 | 14-APR-10:20
| May | 15-MAY-17:10 | 26-MAY-17:10 | 30-MAY-17:10 | 31-MAY-17:10 | 30-MAY-10:50 | 31-MAY-17:10 | 24-MAY-17:10 | 15-MAY-17:10 | 31-MAY-17:10 | 05-MAY-17:10 | 30-MAY-17:10 | 24-MAY-10:39 | 27-MAY-17:10 | 25-MAY-17:10 | 31-MAY-17:10 | 30-MAY-17:10
| Jun | 27-JUN-17:10 | 13-JUN-17:10 | 28-JUN-17:10 | 19-JUN-17:10 | 28-JUN-17:10 | 27-JUN-17:10 | 16-JUN-10:39 | 30-JUN-17:10 | 29-JUN-17:10 | 28-JUN-10:39 | 20-JUN-17:10 | 30-JUN-10:50 | 29-JUN-17:10 | 30-JUN-10:50 | 14-JUN-17:10 | 21-JUN-17:10
| Jul | 13-JUL-17:10 | 05-JUL-17:10 | 11-JUL-17:10 | 03-JUL-17:10 | 29-JUL-10:50 | 25-JUL-17:10 | 03-JUL-10:50 | 25-JUL-10:00 | 20-JUL-17:10 | 31-JUL-17:10 | 14-JUL-10:00 | 19-JUL-10:50 | 13-JUL-17:10 | 21-JUL-17:10 | 06-JUL-17:10 | 11-JUL-17:10
| Aug | 21-AUG-17:10 | 31-AUG-17:10 | 01-AUG-17:10 | 14-AUG-17:10 | 08-AUG-17:10 | 05-AUG-10:50 | 15-AUG-10:50 | 17-AUG-17:10 | 01-AUG-17:10 | 18-AUG-17:10 | 04-AUG-17:10 | 30-AUG-10:50 | 25-AUG-17:10 | 11-AUG-17:10 | 11-AUG-17:10 | 15-AUG-17:10
| Sep | 13-SEP-17:10 | 15-SEP-17:10 | 08-SEP-17:10 | 06-SEP-17:10 | 09-SEP-10:50 | 01-SEP-17:10 | 29-SEP-10:50 | 08-SEP-17:10 | 01-SEP-17:10 | 02-SEP-17:10 | 06-SEP-10:50 | 01-SEP-17:10 | 14-SEP-17:10 | 01-SEP-17:10 | 08-SEP-17:10 | 01-SEP-17:10
| Oct | 06-OCT-17:10 | 06-OCT-17:10 | 13-OCT-17:10 | 20-OCT-17:10 | 05-OCT-10:50 | 06-OCT-10:50 | 16-OCT-17:10 | 20-OCT-17:10 | 11-OCT-17:10 | 05-OCT-17:10 | 31-OCT-18:10 | 05-OCT-17:10 | 14-OCT-10:20 | 06-OCT-17:10 | 07-OCT-17:10 | 02-OCT-10:20
| Nov | 01-NOV-18:10 | 27-NOV-18:10 | 13-NOV-18:10 | 28-NOV-18:10 | 20-NOV-11:39 | 21-NOV-18:10 | 16-NOV-18:10 | 04-NOV-11:50 | 10-NOV-11:20 | 03-NOV-18:10 | 02-NOV-18:10 | 16-NOV-11:20 | 02-NOV-18:10 | 07-NOV-18:10 | 09-NOV-11:20 | 14-NOV-18:10
| Dec | 15-DEC-18:10 | 02-DEC-11:00 | 13-DEC-18:10 | 04-DEC-18:10 | 04-DEC-18:10 | 05-DEC-18:10 | 14-DEC-18:10 | 23-DEC-11:20 | 22-DEC-11:20 | 05-DEC-11:20 | 12-DEC-18:10 | 30-DEC-11:20 | 02-DEC-11:20 | 29-DEC-18:10 | 02-DEC-11:20 | 18-DEC-11:09
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12
| Total Building | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12
Emissions
| Carbon Equivalent (kg) | 556688.4586 | 655739.6714 | 557029.4969 | 567303.0745 | 217605.3548 | 580260.4901 | 226346.2883 | 500653.9058 | 684923.7867 | 170909.8718 | 925248.034 | 699308.6374 | 644754.6558 | 645202.8148 | 638262.2394 | 587987.9854
| CO2 (kg) | 1293310 | 1654400 | 1322550 | 1311180 | 586630.4171 | 1391760 | 614443.5174 | 1159230 | 1622340 | 437227.9253 | 2176960 | 1662610 | 1536380 | 1544970 | 1532520 | 1531870
| NOX (kg) | 2262.5005 | 2146.8539 | 2182.4167 | 2419.1615 | 505.9076 | 2211.6904 | 532.7807 | 2139.7938 | 2730.937 | 579.742 | 3772.8895 | 2772.0645 | 2576.8787 | 2545.3791 | 2519.4065 | 1766.2229
| SO2 (kg) | 8572.6716 | 9040.3111 | 7108.6155 | 6030.3262 | 4776.0635 | 8919.1797 | 4485.9163 | 6009.9307 | 6817.6065 | 1169.3738 | 10780.6889 | 6842.5614 | 3856.8496 | 4140.6999 | 3681.0768 | 7863.5118
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0391 | 0.0255 | 0.0194 | 0.0222 | 0.0023 | 0.0169 | 0.0023 | 0.0245 | 0.0268 | 0.0049 | 0.0329 | 0.027 | 0.0286 | 0.0292 | 0.0275 | 0.0275
| Water for Electricity (m3) | 1060.97 | 3083.66 | 52508.4 | 10725.8 | 28815.7 | 44479.9 | 27063.2 | 373.7371 | 7088.53 | 15445.4 | 2481.59 | 7114.29 | 2534.45 | 98203.5 | 2418.72 | 1577.81

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 7622.22 | 1823.15 | 1823.15
Net Site Energy | 7622.22 | 1823.15 | 1823.15
Total Source Energy | 24365.48 | 5827.95 | 5827.95
Net Source Energy | 24365.48 | 5827.95 | 5827.95
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 101.55 | 0 | 0 | 0 | 0
Cooling | 583.61 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 68.14 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 678.54 | 294.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 484.29 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 15.87 | 0 | 0 | 0 | 87.12
Refrigeration | 4461.54 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7209.89 | 412.33 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 11.84 | 18.59 | 8.07
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 8.61 | 27.86 | 8.07
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 18.29 | 11.61 | 80.7
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 18.29 | 11.61 | 5.38
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 18.29 | 11.61 | 5.38
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 18.29 | 11.61 | 80.7
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.6518
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.6518
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
OFFICE_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 60.34 | 0 | 90 | N
OFFICE_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 54.71 | 90 | 90 | E
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 88.84 | 0 | 180
OFFICE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 88.84 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 621.89 | 180 | 0
DELI_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 224.72 | 0 | 180
DELI_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 224.72 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 2324.94 | 0 | 180
SALES_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 2324.94 | 180 | 0
PRODUCE_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 267.12 | 270 | 90 | W
PRODUCE_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 98.96 | 180 | 90 | S
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 711.36 | 180 | 0
BAKERY_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS | 0.08 | 2.61 | 4.28 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 209.04 | 0 | 180
BAKERY_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 209.04 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 174.7 | 174.7 | 6.49 | 0.25 | 0.25 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 6.49 | 0.25 | 0.25
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 6.49 | 0.25 | 0.25
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11305.45 | 8383.85 | 2921.6 | 0.74 | 3.87
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 66202.18 | 44758.19 | 21444 | 0.68 | 3.19
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 47766.8 | 36430.6 | 11336.21 | 0.76 | 3.38
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 136471.25 | 92265.93 | 44205.33 | 0.68 | 3.51
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 71349.53 | 48238.22 | 23111.31 | 0.68 | 3.12
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 42072.37 | 33326.03 | 8746.33 | 0.79 | 3.45
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 4143.26 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 30964.57 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 23494.83 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 63831.32 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 33372.12 | 0.8
PSZ-AC:6_HEATC | Coil:Heating:Gas | 19993.16 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.35 | 125 | 1.18 | 421.39 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.58 | 669.19 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.67 | 2915.57 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.6 | 2846.93 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.5 | 10309.87 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.87 | 3142.26 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.5 | 2730.08 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.71 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 100708.032 | 174.8006 | 656.7025 | 0 | 0.003 | 81273.8209 | 43210.5566
February | 91336.0434 | 159.0579 | 599.7169 | 0 | 0.0027 | 74221.6536 | 39241.8891
March | 102867.8229 | 179.4022 | 677.4991 | 0 | 0.0031 | 83848.2773 | 44222.7141
April | 104164.7982 | 182.4071 | 691.8882 | 0 | 0.0032 | 85629.6605 | 44854.7198
May | 113832.1505 | 199.5516 | 757.7987 | 0 | 0.0035 | 93787.0513 | 49039.2186
June | 114193.2803 | 200.2421 | 760.6542 | 0 | 0.0035 | 94140.4982 | 49200.541
July | 119565.1883 | 209.7041 | 796.7693 | 0 | 0.0036 | 98610.2307 | 51519.2747
August | 120265.7817 | 210.9119 | 801.2732 | 0 | 0.0037 | 99167.6287 | 51819.0546
September | 113223.3454 | 198.5461 | 754.2319 | 0 | 0.0034 | 93345.6598 | 48783.132
October | 111747.4338 | 195.8693 | 743.7019 | 0 | 0.0034 | 92042.3709 | 48138.3343
November | 102090.8556 | 178.7083 | 677.5855 | 0 | 0.0031 | 83859.4743 | 43954.9431
December | 99312.5966 | 173.2992 | 654.8501 | 0 | 0.003 | 81045.2729 | 42704.0807
Annual Sum or Average | 1293310 | 2262.5005 | 8572.6716 | 0 | 0.0391 | 1060970 | 556688.4586
Minimum of Months | 91336.0434 | 159.0579 | 599.7169 | 0 | 0.0027 | 74221.6536 | 39241.8891
Maximum of Months | 120265.7817 | 210.9119 | 801.2732 | 0 | 0.0037 | 99167.6287 | 51819.0546
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 552301000000 | 361152.27 | 23-JAN-18:10 | 41924.28 | 31827.177 | 23035.293 | 0 | 26565.907 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 233469.466 | 0 | 0
February | 504377000000 | 362817.98 | 23-FEB-11:00 | 62886.42 | 35805.575 | 23035.293 | 0 | 31995.797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209094.896 | 0 | 0
March | 569796000000 | 377461.644 | 13-MAR-17:10 | 41924.28 | 31827.177 | 23035.293 | 0 | 41548.635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239126.258 | 0 | 0
April | 581901000000 | 389704.238 | 03-APR-17:10 | 41924.28 | 31827.177 | 23035.293 | 0 | 53650.383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239267.105 | 0 | 0
May | 637335000000 | 400105.487 | 15-MAY-17:10 | 41924.28 | 31827.177 | 23035.293 | 0 | 61559.979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241758.759 | 0 | 0
June | 639737000000 | 422129.136 | 27-JUN-17:10 | 41924.28 | 31827.177 | 23035.293 | 0 | 79205.891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246136.494 | 0 | 0
July | 670111000000 | 412708.082 | 13-JUL-17:10 | 41924.28 | 31827.177 | 23035.293 | 0 | 71818.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244103.298 | 0 | 0
August | 673899000000 | 415213.569 | 21-AUG-17:10 | 41924.28 | 31827.177 | 23035.293 | 0 | 73208.848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245217.971 | 0 | 0
September | 634336000000 | 402142.776 | 13-SEP-17:10 | 41924.28 | 31827.177 | 23035.293 | 0 | 63498.982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241857.044 | 0 | 0
October | 625479000000 | 401422.714 | 06-OCT-17:10 | 41924.28 | 31827.177 | 23035.293 | 0 | 62894.983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241740.982 | 0 | 0
November | 569872000000 | 380289.97 | 01-NOV-18:10 | 41924.28 | 31827.177 | 23035.293 | 0 | 39516.859 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 239656.213 | 0 | 0
December | 550748000000 | 364551.981 | 15-DEC-18:10 | 41924.28 | 31827.177 | 23035.293 | 0 | 27674.14 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 235760.944 | 0 | 0
Annual Sum or Average | 7209890000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 504377000000 | 361152.27 |  | 41924.28 | 31827.177 | 23035.293 | 0 | 26565.907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209094.896 | 0 | 0
Maximum of Months | 673899000000 | 422129.136 |  | 62886.42 | 35805.575 | 23035.293 | 0 | 79205.891 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 246136.494 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 159695.17 | 4720.14 | 0 | 164415.32
Cost per Total Building Area ($/m2) | 38.2 | 1.13 | 0 | 39.33
Cost per Net Conditioned Building Area ($/m2) | 38.2 | 1.13 | 0 | 39.33

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 8130.51 | 1944.73 | 1944.73
Net Site Energy | 8130.51 | 1944.73 | 1944.73
Total Source Energy | 1428.23 | 341.62 | 341.62
Net Source Energy | 1428.23 | 341.62 | 341.62
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 995.15 | 0 | 0 | 0 | 0
Cooling | 452.5 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 68.11 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 678.54 | 294.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 597.72 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 17.83 | 0 | 0 | 0 | 87.12
Refrigeration | 4091.97 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6822.61 | 1307.9 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 11.84 | 18.59 | 8.07
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 8.61 | 27.86 | 8.07
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 18.29 | 11.61 | 80.7
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 18.29 | 11.61 | 5.38
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 18.29 | 11.61 | 5.38
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 18.29 | 11.61 | 80.7
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.6518
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.6518
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
OFFICE_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 60.34 | 0 | 90 | N
OFFICE_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 54.71 | 90 | 90 | E
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 88.84 | 0 | 180
OFFICE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 88.84 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 621.89 | 180 | 0
DELI_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 224.72 | 0 | 180
DELI_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 224.72 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 2324.94 | 0 | 180
SALES_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 2324.94 | 180 | 0
PRODUCE_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 267.12 | 270 | 90 | W
PRODUCE_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 98.96 | 180 | 90 | S
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 711.36 | 180 | 0
BAKERY_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS | 0.08 | 2.61 | 4.28 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 209.04 | 0 | 180
BAKERY_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 209.04 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 174.7 | 174.7 | 6.49 | 0.25 | 0.25 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 6.49 | 0.25 | 0.25
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 6.49 | 0.25 | 0.25
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10872.4 | 8264.1 | 2608.3 | 0.76 | 3.93
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 69501.09 | 46988.52 | 22512.57 | 0.68 | 3.19
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 45655.54 | 35599 | 10056.54 | 0.78 | 3.42
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 206342.43 | 139504.66 | 66837.78 | 0.68 | 3.49
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 72812.38 | 49227.23 | 23585.15 | 0.68 | 3.12
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 41820.38 | 33400.07 | 8420.31 | 0.8 | 3.47
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 4242.98 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 42914.43 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 27753.13 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 127409.04 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 44959.03 | 0.8
PSZ-AC:6_HEATC | Coil:Heating:Gas | 22078.9 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.35 | 125 | 1.18 | 421.39 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.59 | 681.94 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.8 | 3060.85 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.62 | 2861.01 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1109.65 | 8.31 | 15352.18 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.93 | 3206.68 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.53 | 2762.9 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.71 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 127351.6809 | 161.697 | 646.0037 | 0 | 0.0018 | 220336.7996 | 50018.0455
February | 114082.4923 | 144.3917 | 572.2868 | 0 | 0.0016 | 195191.461 | 44747.5291
March | 127411.5977 | 164.3286 | 682.0992 | 0 | 0.0019 | 232660.5036 | 50370.9825
April | 130498.9736 | 170.3721 | 727.5008 | 0 | 0.002 | 248156.2279 | 51857.2808
May | 145857.545 | 191.0298 | 821.6146 | 0 | 0.0023 | 280261.8733 | 58038.5915
June | 152496.1478 | 199.8915 | 861.3499 | 0 | 0.0024 | 293816.7454 | 60701.7135
July | 161514.6115 | 211.7419 | 912.6965 | 0 | 0.0026 | 311331.8092 | 64295.2979
August | 160382.3142 | 210.2305 | 905.9201 | 0 | 0.0025 | 309020.1772 | 63841.0776
September | 145332.1988 | 190.467 | 820.4098 | 0 | 0.0023 | 279851.4283 | 57845.6961
October | 138317.1857 | 180.8077 | 774.2869 | 0 | 0.0022 | 264116.357 | 54993.5224
November | 124554.7783 | 161.374 | 677.0287 | 0 | 0.0019 | 230934.3333 | 49335.6568
December | 126599.3444 | 160.5223 | 639.1143 | 0 | 0.0018 | 217985.896 | 49694.2777
Annual Sum or Average | 1654400 | 2146.8539 | 9040.3111 | 0 | 0.0255 | 3083660 | 655739.6714
Minimum of Months | 114082.4923 | 144.3917 | 572.2868 | 0 | 0.0016 | 195191.461 | 44747.5291
Maximum of Months | 161514.6115 | 211.7419 | 912.6965 | 0 | 0.0026 | 311331.8092 | 64295.2979
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 487496000000 | 353384.158 | 20-JAN-18:10 | 41924.28 | 31827.177 | 28346.961 | 0 | 14976.096 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 231979.496 | 0 | 0
February | 431861000000 | 341348.856 | 15-FEB-18:10 | 41924.28 | 31827.177 | 28346.961 | 0 | 8453.198 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 226467.092 | 0 | 0
March | 514762000000 | 352906.781 | 28-MAR-17:10 | 41924.28 | 31827.177 | 28346.961 | 0 | 18054.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232753.902 | 0 | 0
April | 549046000000 | 377402.525 | 29-APR-17:10 | 34936.9 | 27848.78 | 28346.961 | 0 | 48827.816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 237442.067 | 0 | 0
May | 620080000000 | 421055.82 | 26-MAY-17:10 | 41924.28 | 31827.177 | 28346.961 | 0 | 74779.653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244177.748 | 0 | 0
June | 650070000000 | 424986.774 | 13-JUN-17:10 | 41924.28 | 31827.177 | 28346.961 | 0 | 78592.845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244295.511 | 0 | 0
July | 688822000000 | 434820.197 | 05-JUL-17:10 | 41924.28 | 31827.177 | 28346.961 | 0 | 86461.252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246260.526 | 0 | 0
August | 683708000000 | 433584.235 | 31-AUG-17:10 | 41924.28 | 31827.177 | 28346.961 | 0 | 85646.907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245838.909 | 0 | 0
September | 619172000000 | 415023.329 | 15-SEP-17:10 | 41924.28 | 31827.177 | 28346.961 | 0 | 68398.166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244526.744 | 0 | 0
October | 584358000000 | 385949.557 | 06-OCT-17:10 | 41924.28 | 31827.177 | 28346.961 | 0 | 46509.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 237341.297 | 0 | 0
November | 510943000000 | 367234.412 | 27-NOV-18:10 | 41924.28 | 31827.177 | 28346.961 | 0 | 22358.339 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 238447.507 | 0 | 0
December | 482294000000 | 353463.747 | 02-DEC-11:00 | 62886.42 | 35805.575 | 28346.961 | 0 | 18133.526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208291.265 | 0 | 0
Annual Sum or Average | 6822610000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 431861000000 | 341348.856 |  | 34936.9 | 27848.78 | 28346.961 | 0 | 8453.198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208291.265 | 0 | 0
Maximum of Months | 688822000000 | 434820.197 |  | 62886.42 | 35805.575 | 28346.961 | 0 | 86461.252 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 246260.526 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 205801.05 | 10574.51 | 0 | 216375.57
Cost per Total Building Area ($/m2) | 49.23 | 2.53 | 0 | 51.75
Cost per Net Conditioned Building Area ($/m2) | 49.23 | 2.53 | 0 | 51.75

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 7661.62 | 1832.58 | 1832.58
Net Site Energy | 7661.62 | 1832.58 | 1832.58
Total Source Energy | 21545.74 | 5153.5 | 5153.5
Net Source Energy | 21545.74 | 5153.5 | 5153.5
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 986.29 | 0 | 0 | 0 | 0
Cooling | 441.57 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 68.1 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 678.54 | 294.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 619.84 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 16.7 | 0 | 0 | 0 | 87.12
Refrigeration | 3621.9 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6363.71 | 1297.91 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 11.84 | 18.59 | 8.07
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 8.61 | 27.86 | 8.07
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 18.29 | 11.61 | 80.7
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 18.29 | 11.61 | 5.38
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 18.29 | 11.61 | 5.38
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 18.29 | 11.61 | 80.7
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.6518
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.6518
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
OFFICE_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 60.34 | 0 | 90 | N
OFFICE_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 54.71 | 90 | 90 | E
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 88.84 | 0 | 180
OFFICE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 88.84 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 621.89 | 180 | 0
DELI_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 224.72 | 0 | 180
DELI_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 224.72 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 2324.94 | 0 | 180
SALES_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 2324.94 | 180 | 0
PRODUCE_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 267.12 | 270 | 90 | W
PRODUCE_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 98.96 | 180 | 90 | S
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 711.36 | 180 | 0
BAKERY_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS | 0.08 | 2.61 | 4.28 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 209.04 | 0 | 180
BAKERY_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 209.04 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 174.7 | 174.7 | 6.49 | 0.25 | 0.25 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 6.49 | 0.25 | 0.25
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 6.49 | 0.25 | 0.25
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11935.7 | 9532.51 | 2403.19 | 0.8 | 4.03
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 52967.01 | 42302.38 | 10664.63 | 0.8 | 3.47
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 45260.6 | 36147.62 | 9112.98 | 0.8 | 3.47
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 149126.71 | 114108.15 | 35018.56 | 0.77 | 3.94
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 54140.15 | 43239.32 | 10900.83 | 0.8 | 3.47
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 44916.18 | 35872.55 | 9043.64 | 0.8 | 3.47
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 4981.48 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 40838.95 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 25481.72 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 105928.81 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 42310.09 | 0.8
PSZ-AC:6_HEATC | Coil:Heating:Gas | 21652.16 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.35 | 125 | 1.18 | 421.39 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.72 | 821.4 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.2 | 3499.32 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.73 | 2990.19 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1109.65 | 8.19 | 15128.59 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.27 | 3576.82 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.71 | 2967.43 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.71 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 101762.3868 | 161.0775 | 497.4354 | 0 | 0.0014 | 3674000 | 42167.8773
February | 90716.8053 | 144.3384 | 448.8294 | 0 | 0.0012 | 3315040 | 37666.1582
March | 102441.8905 | 168.2015 | 544.5114 | 0 | 0.0015 | 4022040 | 43061.0735
April | 99774.2157 | 165.9007 | 545.3738 | 0 | 0.0015 | 4028520 | 42149.9918
May | 109516.2029 | 183.3231 | 607.4776 | 0 | 0.0017 | 4487320 | 46389.2886
June | 119553.4055 | 200.8721 | 668.5597 | 0 | 0.0018 | 4938560 | 50716.4604
July | 135053.1883 | 227.1805 | 757.1599 | 0 | 0.0021 | 5593050 | 57318.6003
August | 133490.781 | 224.5341 | 748.2689 | 0 | 0.002 | 5527370 | 56653.6518
September | 121569.513 | 204.3352 | 680.3808 | 0 | 0.0018 | 5025880 | 51579.3683
October | 107567.5043 | 179.4795 | 592.4608 | 0 | 0.0016 | 4376360 | 45505.0354
November | 98646.7573 | 161.7853 | 523.0016 | 0 | 0.0014 | 3863150 | 41447.1076
December | 102452.6563 | 161.3887 | 495.1564 | 0 | 0.0014 | 3657120 | 42374.8836
Annual Sum or Average | 1322550 | 2182.4167 | 7108.6155 | 0 | 0.0194 | 52508400 | 557029.4969
Minimum of Months | 90716.8053 | 144.3384 | 448.8294 | 0 | 0.0012 | 3315040 | 37666.1582
Maximum of Months | 135053.1883 | 227.1805 | 757.1599 | 0 | 0.0021 | 5593050 | 57318.6003
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 445267000000 | 304662.841 | 27-JAN-18:10 | 41924.28 | 31827.177 | 29405.135 | 0 | 5174.199 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 192001.902 | 0 | 0
February | 401764000000 | 313407.934 | 28-FEB-18:10 | 41924.28 | 31827.177 | 29405.135 | 0 | 12653.488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197597.853 | 0 | 0
March | 487448000000 | 342734.52 | 17-MAR-17:10 | 41924.28 | 31827.177 | 29405.135 | 0 | 29836.793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209741.134 | 0 | 0
April | 488233000000 | 347972.17 | 25-APR-17:10 | 41924.28 | 31827.177 | 29405.135 | 0 | 36105.134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208710.443 | 0 | 0
May | 543837000000 | 384278.881 | 30-MAY-17:10 | 41924.28 | 31827.177 | 29405.135 | 0 | 65644.997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215477.292 | 0 | 0
June | 598524000000 | 429961.083 | 28-JUN-17:10 | 41924.28 | 31827.177 | 29405.135 | 0 | 104256.225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222548.266 | 0 | 0
July | 677845000000 | 438573.256 | 11-JUL-17:10 | 41924.28 | 31827.177 | 29405.135 | 0 | 97718.526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 237698.137 | 0 | 0
August | 669885000000 | 432079.96 | 01-AUG-17:10 | 41924.28 | 31827.177 | 29405.135 | 0 | 102520.827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226402.54 | 0 | 0
September | 609108000000 | 415911.561 | 08-SEP-17:10 | 41924.28 | 31827.177 | 29405.135 | 0 | 77529.195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 235225.773 | 0 | 0
October | 530390000000 | 368451.224 | 13-OCT-17:10 | 41924.28 | 31827.177 | 29405.135 | 0 | 41566.906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223727.726 | 0 | 0
November | 468191000000 | 329432.787 | 13-NOV-18:10 | 41924.28 | 31827.177 | 29405.135 | 0 | 16146.946 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 205799.101 | 0 | 0
December | 443222000000 | 321261.798 | 13-DEC-18:10 | 41924.28 | 31827.177 | 29405.135 | 0 | 2322.507 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 211452.551 | 0 | 0
Annual Sum or Average | 6363710000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 401764000000 | 304662.841 |  | 41924.28 | 31827.177 | 29405.135 | 0 | 2322.507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192001.902 | 0 | 0
Maximum of Months | 677845000000 | 438573.256 |  | 41924.28 | 31827.177 | 29405.135 | 0 | 104256.225 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 237698.137 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 136128.49 | 10778.46 | 0 | 146906.95
Cost per Total Building Area ($/m2) | 32.56 | 2.58 | 0 | 35.14
Cost per Net Conditioned Building Area ($/m2) | 32.56 | 2.58 | 0 | 35.14

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 8299.02 | 1985.04 | 1985.04
Net Site Energy | 8299.02 | 1985.04 | 1985.04
Total Source Energy | 23113.42 | 5528.48 | 5528.48
Net Source Energy | 23113.42 | 5528.48 | 5528.48
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1800.01 | 0 | 0 | 0 | 0
Cooling | 222.92 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 68.09 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 678.54 | 294.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 609.19 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 19.73 | 0 | 0 | 0 | 87.12
Refrigeration | 3671.86 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6184.37 | 2114.66 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 11.84 | 18.59 | 8.07
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 8.61 | 27.86 | 8.07
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 18.29 | 11.61 | 80.7
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 18.29 | 11.61 | 5.38
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 18.29 | 11.61 | 5.38
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 18.29 | 11.61 | 80.7
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.6518
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.6518
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
OFFICE_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 60.34 | 0 | 90 | N
OFFICE_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 54.71 | 90 | 90 | E
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 88.84 | 0 | 180
OFFICE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 88.84 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 621.89 | 180 | 0
DELI_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 224.72 | 0 | 180
DELI_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 224.72 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 2324.94 | 0 | 180
SALES_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 2324.94 | 180 | 0
PRODUCE_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 267.12 | 270 | 90 | W
PRODUCE_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 98.96 | 180 | 90 | S
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 711.36 | 180 | 0
BAKERY_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS | 0.08 | 0.856 | 0.98 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 209.04 | 0 | 180
BAKERY_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 209.04 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 174.7 | 174.7 | 3.18 | 0.262 | 0.318 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 3.18 | 0.262 | 0.318
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 3.18 | 0.262 | 0.318
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9254.21 | 6914.41 | 2339.8 | 0.75 | 3.88
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 65664.61 | 44394.74 | 21269.87 | 0.68 | 3.19
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 43283.26 | 34311.96 | 8971.29 | 0.79 | 3.45
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 218819.33 | 147940.07 | 70879.25 | 0.68 | 3.49
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 70149.99 | 47427.23 | 22722.76 | 0.68 | 3.19
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 41222.5 | 32922.56 | 8299.93 | 0.8 | 3.47
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 3420.04 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 43738.19 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 28467.68 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 145752.2 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 46725.83 | 0.8
PSZ-AC:6_HEATC | Coil:Heating:Gas | 21998.53 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.35 | 125 | 1.18 | 421.39 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.48 | 557.63 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.64 | 2891.89 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.57 | 2813.47 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1109.65 | 8.81 | 16280.48 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.82 | 3089.43 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.49 | 2723.4 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.71 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 107180.8296 | 183.6095 | 423.6164 | 0 | 0.0016 | 753321.2503 | 45067.5042
February | 95984.767 | 166.932 | 391.6315 | 0 | 0.0015 | 696470.6633 | 40590.8568
March | 103767.7605 | 186.7031 | 453.9536 | 0 | 0.0017 | 807371.7382 | 44458.0515
April | 101891.0758 | 189.2859 | 474.9566 | 0 | 0.0017 | 844787.5207 | 44204.368
May | 111454.1631 | 212.4607 | 546.0505 | 0 | 0.002 | 971291.7085 | 48852.7696
June | 115593.163 | 221.6082 | 572.4933 | 0 | 0.0021 | 1018340 | 50783.1182
July | 123895.5778 | 237.7799 | 614.8613 | 0 | 0.0022 | 1093700 | 54454.1173
August | 123764.0698 | 237.48 | 613.976 | 0 | 0.0022 | 1092130 | 54391.9342
September | 114617.569 | 219.715 | 567.5493 | 0 | 0.0021 | 1009540 | 50352.3994
October | 106051.9432 | 198.4217 | 501.2448 | 0 | 0.0018 | 891558.8019 | 46139.3702
November | 100819.0315 | 180.7396 | 437.8279 | 0 | 0.0016 | 778684.978 | 43133.9309
December | 106158.0463 | 184.426 | 432.1651 | 0 | 0.0016 | 768552.6924 | 44874.6542
Annual Sum or Average | 1311180 | 2419.1615 | 6030.3262 | 0 | 0.0222 | 10725800 | 567303.0745
Minimum of Months | 95984.767 | 166.932 | 391.6315 | 0 | 0.0015 | 696470.6633 | 40590.8568
Maximum of Months | 123895.5778 | 237.7799 | 614.8613 | 0 | 0.0022 | 1093700 | 54454.1173
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 434358000000 | 328658.631 | 24-JAN-18:10 | 41924.28 | 31827.177 | 28777.693 | 0 | 2937.944 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 218861.389 | 0 | 0
February | 401578000000 | 316550.934 | 21-FEB-18:10 | 41924.28 | 31827.177 | 28777.693 | 0 | 2512.992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211508.791 | 0 | 0
March | 465523000000 | 330913.198 | 29-MAR-17:10 | 41924.28 | 31827.177 | 28777.693 | 0 | 6718.008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221666.04 | 0 | 0
April | 487096000000 | 351549.849 | 14-APR-17:10 | 41924.28 | 31827.177 | 28777.693 | 0 | 18212.175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230808.523 | 0 | 0
May | 560038000000 | 386790.28 | 31-MAY-17:10 | 41924.28 | 31827.177 | 28777.693 | 0 | 43388.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240872.971 | 0 | 0
June | 587164000000 | 401057.911 | 19-JUN-17:10 | 41924.28 | 31827.177 | 28777.693 | 0 | 59857.644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 238671.116 | 0 | 0
July | 630619000000 | 427006.206 | 03-JUL-17:10 | 41924.28 | 31827.177 | 28777.693 | 0 | 79562.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244914.889 | 0 | 0
August | 629711000000 | 406677.839 | 14-AUG-17:10 | 41924.28 | 31827.177 | 28777.693 | 0 | 61179.599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242969.089 | 0 | 0
September | 582094000000 | 382980.246 | 06-SEP-17:10 | 41924.28 | 31827.177 | 28777.693 | 0 | 42452.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 237998.745 | 0 | 0
October | 514064000000 | 351140.854 | 20-OCT-17:10 | 41924.28 | 31827.177 | 28777.693 | 0 | 15971.461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232640.242 | 0 | 0
November | 448982000000 | 326566.433 | 28-NOV-18:10 | 41924.28 | 31827.177 | 28777.693 | 0 | 2937.632 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 216769.503 | 0 | 0
December | 443140000000 | 326286.185 | 04-DEC-18:10 | 41924.28 | 31827.177 | 28777.693 | 0 | 3608.612 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 215818.275 | 0 | 0
Annual Sum or Average | 6184370000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 401578000000 | 316550.934 |  | 41924.28 | 31827.177 | 28777.693 | 0 | 2512.992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211508.791 | 0 | 0
Maximum of Months | 630619000000 | 427006.206 |  | 41924.28 | 31827.177 | 28777.693 | 0 | 79562.167 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 244914.889 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 170047.66 | 20809.12 | 0 | 190856.78
Cost per Total Building Area ($/m2) | 40.67 | 4.98 | 0 | 45.65
Cost per Net Conditioned Building Area ($/m2) | 40.67 | 4.98 | 0 | 45.65

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 7339.36 | 1755.49 | 1755.49
Net Site Energy | 7339.36 | 1755.49 | 1755.49
Total Source Energy | 19848.9 | 4747.64 | 4747.64
Net Source Energy | 19848.9 | 4747.64 | 4747.64
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1116.78 | 0 | 0 | 0 | 0
Cooling | 48.17 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 68.04 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 678.54 | 294.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 493.06 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 19.36 | 0 | 0 | 0 | 87.12
Refrigeration | 3686.74 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5908.3 | 1431.05 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 11.84 | 18.59 | 8.07
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 8.61 | 27.86 | 8.07
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 18.29 | 11.61 | 80.7
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 18.29 | 11.61 | 5.38
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 18.29 | 11.61 | 5.38
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 18.29 | 11.61 | 80.7
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.6518
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.6518
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
OFFICE_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 60.34 | 0 | 90 | N
OFFICE_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 54.71 | 90 | 90 | E
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 88.84 | 0 | 180
OFFICE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 88.84 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 621.89 | 180 | 0
DELI_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 224.72 | 0 | 180
DELI_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 224.72 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 2324.94 | 0 | 180
SALES_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 2324.94 | 180 | 0
PRODUCE_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 267.12 | 270 | 90 | W
PRODUCE_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 98.96 | 180 | 90 | S
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 711.36 | 180 | 0
BAKERY_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS | 0.08 | 0.856 | 0.98 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 209.04 | 0 | 180
BAKERY_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 209.04 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 174.7 | 174.7 | 3.18 | 0.262 | 0.318 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 3.18 | 0.262 | 0.318
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 3.18 | 0.262 | 0.318
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5869.06 | 4687.36 | 1181.7 | 0.8 | 4.04
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 28594.86 | 22837.43 | 5757.42 | 0.8 | 3.75
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 39704.56 | 31710.25 | 7994.3 | 0.8 | 3.47
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 117897.27 | 94159.28 | 23738 | 0.8 | 4.18
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 33203.17 | 26517.89 | 6685.28 | 0.8 | 3.75
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 38634.23 | 30855.43 | 7778.8 | 0.8 | 3.74
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 2577.59 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 20866.95 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 22560.08 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 86034.93 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 24229.84 | 0.8
PSZ-AC:6_HEATC | Coil:Heating:Gas | 19096.05 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.35 | 125 | 1.18 | 421.39 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.35 | 411.24 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.73 | 1889.15 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.4 | 2623.12 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.12 | 13361.13 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.01 | 2193.6 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.33 | 2552.41 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.71 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 50726.7497 | 44.0065 | 366.4779 | 0 | 0.0002 | 2210920 | 18674.7231
February | 46127.7375 | 39.991 | 337.8695 | 0 | 0.0002 | 2038340 | 16995.714
March | 50612.0543 | 43.8006 | 384.6843 | 0 | 0.0002 | 2320830 | 18690.5736
April | 48414.8417 | 41.8357 | 379.3381 | 0 | 0.0002 | 2288630 | 17913.8037
May | 49546.4514 | 42.6818 | 411.7665 | 0 | 0.0002 | 2484370 | 18404.3936
June | 48044.6065 | 41.3277 | 410.0768 | 0 | 0.0002 | 2474210 | 17879.4473
July | 49193.2881 | 42.2108 | 438.6767 | 0 | 0.0002 | 2646840 | 18364.265
August | 50271.3427 | 43.1225 | 450.6751 | 0 | 0.0002 | 2719240 | 18773.9881
September | 47408.957 | 40.6764 | 423.3568 | 0 | 0.0002 | 2554410 | 17699.9645
October | 48235.7859 | 41.4616 | 417.1706 | 0 | 0.0002 | 2517030 | 17967.2575
November | 48034.9586 | 41.4756 | 382.0446 | 0 | 0.0002 | 2304980 | 17790.583
December | 50013.6437 | 43.3174 | 373.9265 | 0 | 0.0002 | 2255910 | 18450.6412
Annual Sum or Average | 586630.4171 | 505.9076 | 4776.0635 | 0 | 0.0023 | 28815700 | 217605.3548
Minimum of Months | 46127.7375 | 39.991 | 337.8695 | 0 | 0.0002 | 2038340 | 16995.714
Maximum of Months | 50726.7497 | 44.0065 | 450.6751 | 0 | 0.0002 | 2719240 | 18773.9881
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 453321000000 | 306125.519 | 10-JAN-18:10 | 41924.28 | 31827.177 | 23452.039 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 204591.875 | 0 | 0
February | 417937000000 | 314397.754 | 13-FEB-11:39 | 62886.42 | 35805.575 | 23452.039 | 0 | 8258.612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183995.108 | 0 | 0
March | 475858000000 | 312409.284 | 04-MAR-11:39 | 62886.42 | 35805.575 | 23452.039 | 0 | 8236.492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182028.759 | 0 | 0
April | 469254000000 | 315858.665 | 10-APR-10:50 | 62886.42 | 35805.575 | 23452.039 | 0 | 3736.668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189977.964 | 0 | 0
May | 509389000000 | 335424.677 | 30-MAY-10:50 | 62886.42 | 35805.575 | 23452.039 | 0 | 12568.667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200711.976 | 0 | 0
June | 507307000000 | 333670.038 | 28-JUN-17:10 | 41924.28 | 31827.177 | 23452.039 | 0 | 9870.438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226596.104 | 0 | 0
July | 542702000000 | 344521.1 | 29-JUL-10:50 | 62886.42 | 35805.575 | 23452.039 | 0 | 15953.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206423.097 | 0 | 0
August | 557547000000 | 353213.722 | 08-AUG-17:10 | 41924.28 | 31827.177 | 23452.039 | 0 | 21667.714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234342.511 | 0 | 0
September | 523749000000 | 348372.663 | 09-SEP-10:50 | 62886.42 | 35805.575 | 23452.039 | 0 | 17584.784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208643.846 | 0 | 0
October | 516086000000 | 335596.622 | 05-OCT-10:50 | 62886.42 | 35805.575 | 23452.039 | 0 | 12230.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201222.486 | 0 | 0
November | 472607000000 | 322861.933 | 20-NOV-11:39 | 62886.42 | 35805.575 | 23452.039 | 0 | 8728.677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191989.222 | 0 | 0
December | 462545000000 | 313456.407 | 04-DEC-18:10 | 41924.28 | 31827.177 | 23452.039 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 211922.763 | 0 | 0
Annual Sum or Average | 5908300000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 417937000000 | 306125.519 |  | 41924.28 | 31827.177 | 23452.039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182028.759 | 0 | 0
Maximum of Months | 557547000000 | 353213.722 |  | 62886.42 | 35805.575 | 23452.039 | 0 | 21667.714 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 234342.511 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 201478 | 12182.59 | 0 | 213660.58
Cost per Total Building Area ($/m2) | 48.19 | 2.91 | 0 | 51.11
Cost per Net Conditioned Building Area ($/m2) | 48.19 | 2.91 | 0 | 51.11

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 7690.25 | 1839.42 | 1839.42
Net Site Energy | 7690.25 | 1839.42 | 1839.42
Total Source Energy | 22902.28 | 5477.97 | 5477.97
Net Source Energy | 22902.28 | 5477.97 | 5477.97
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1540.43 | 0 | 0 | 0 | 0
Cooling | 261.41 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 68.02 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 678.54 | 294.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 607.24 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 18.06 | 0 | 0 | 0 | 87.12
Refrigeration | 3287.86 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5836.83 | 1853.41 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 11.84 | 18.59 | 8.07
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 8.61 | 27.86 | 8.07
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 18.29 | 11.61 | 80.7
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 18.29 | 11.61 | 5.38
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 18.29 | 11.61 | 5.38
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 18.29 | 11.61 | 80.7
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.6518
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.6518
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
OFFICE_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 60.34 | 0 | 90 | N
OFFICE_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 54.71 | 90 | 90 | E
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 88.84 | 0 | 180
OFFICE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 88.84 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 621.89 | 180 | 0
DELI_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 224.72 | 0 | 180
DELI_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 224.72 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 2324.94 | 0 | 180
SALES_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 2324.94 | 180 | 0
PRODUCE_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 267.12 | 270 | 90 | W
PRODUCE_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 98.96 | 180 | 90 | S
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 711.36 | 180 | 0
BAKERY_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS | 0.08 | 0.856 | 0.98 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 209.04 | 0 | 180
BAKERY_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 209.04 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 174.7 | 174.7 | 3.18 | 0.262 | 0.318 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 3.18 | 0.262 | 0.318
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 3.18 | 0.262 | 0.318
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7908.25 | 6315.97 | 1592.28 | 0.8 | 4.06
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 42194.37 | 33698.76 | 8495.61 | 0.8 | 3.47
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 42168.88 | 33678.4 | 8490.48 | 0.8 | 3.47
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 219223.05 | 148213.02 | 71010.02 | 0.68 | 3.49
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 45852.94 | 36620.69 | 9232.25 | 0.8 | 3.47
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 41505.81 | 33148.83 | 8356.98 | 0.8 | 3.47
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 3229.16 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 35646.36 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 25023.02 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 123458.13 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 38737.17 | 0.8
PSZ-AC:6_HEATC | Coil:Heating:Gas | 20289.29 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.35 | 125 | 1.18 | 421.39 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.48 | 554.13 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.55 | 2787.61 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.55 | 2785.93 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1109.65 | 8.83 | 16310.52 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.77 | 3029.32 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.51 | 2742.12 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.71 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 113921.8797 | 172.2836 | 647.7981 | 0 | 0.0013 | 3230240 | 46587.2375
February | 100457.7839 | 155.3995 | 603.9231 | 0 | 0.0012 | 3011600 | 41442.6745
March | 111204.6133 | 172.5581 | 673.551 | 0 | 0.0013 | 3358840 | 45931.6762
April | 106479.5838 | 170.8586 | 697.873 | 0 | 0.0013 | 3480350 | 44565.4834
May | 114228.5613 | 184.6733 | 761.637 | 0 | 0.0014 | 3798400 | 47952.2026
June | 122441.9952 | 199.57 | 831.6098 | 0 | 0.0016 | 4147420 | 51568.3095
July | 135545.9692 | 221.2207 | 923.358 | 0 | 0.0017 | 4605000 | 57117.6324
August | 136808.0724 | 223.2193 | 931.3799 | 0 | 0.0017 | 4645010 | 57643.1027
September | 119640.1593 | 194.8119 | 810.7813 | 0 | 0.0015 | 4043540 | 50368.3832
October | 111905.4224 | 180.0002 | 737.525 | 0 | 0.0014 | 3678120 | 46881.625
November | 106629.458 | 166.0306 | 651.2155 | 0 | 0.0012 | 3247480 | 44101.4082
December | 112492.7765 | 171.0646 | 648.5282 | 0 | 0.0013 | 3233920 | 46100.7548
Annual Sum or Average | 1391760 | 2211.6904 | 8919.1797 | 0 | 0.0169 | 44479900 | 580260.4901
Minimum of Months | 100457.7839 | 155.3995 | 603.9231 | 0 | 0.0012 | 3011600 | 41442.6745
Maximum of Months | 136808.0724 | 223.2193 | 931.3799 | 0 | 0.0017 | 4645010 | 57643.1027
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 423885000000 | 295671.416 | 23-JAN-18:10 | 41924.28 | 31827.177 | 28631.022 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 188958.788 | 0 | 0
February | 395195000000 | 307726.343 | 10-FEB-18:10 | 41924.28 | 31827.177 | 28631.022 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 201013.716 | 0 | 0
March | 440761000000 | 304573.228 | 31-MAR-17:10 | 41924.28 | 31827.177 | 28631.022 | 0 | 6809.986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195380.762 | 0 | 0
April | 456706000000 | 345345.4 | 21-APR-17:10 | 41924.28 | 31827.177 | 28631.022 | 0 | 28682.385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214280.535 | 0 | 0
May | 498441000000 | 358059.498 | 31-MAY-17:10 | 41924.28 | 31827.177 | 28631.022 | 0 | 44413.437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211263.581 | 0 | 0
June | 544242000000 | 394676.715 | 27-JUN-17:10 | 41924.28 | 31827.177 | 28631.022 | 0 | 79610.396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212683.839 | 0 | 0
July | 604287000000 | 400877.919 | 25-JUL-17:10 | 41924.28 | 31827.177 | 28631.022 | 0 | 75319.611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223175.828 | 0 | 0
August | 609537000000 | 412634.442 | 05-AUG-10:50 | 62886.42 | 35805.575 | 28631.022 | 0 | 60670.317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224641.108 | 0 | 0
September | 530610000000 | 381394.271 | 01-SEP-17:10 | 41924.28 | 31827.177 | 28631.022 | 0 | 59636.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219374.881 | 0 | 0
October | 482657000000 | 346230.531 | 06-OCT-10:50 | 62886.42 | 35805.575 | 28631.022 | 0 | 19989.605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198917.909 | 0 | 0
November | 426148000000 | 304358.084 | 21-NOV-18:10 | 41924.28 | 31827.177 | 28631.022 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 197645.457 | 0 | 0
December | 424368000000 | 294189.315 | 05-DEC-18:10 | 41924.28 | 31827.177 | 28631.022 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 187476.687 | 0 | 0
Annual Sum or Average | 5836830000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 395195000000 | 294189.315 |  | 41924.28 | 31827.177 | 28631.022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187476.687 | 0 | 0
Maximum of Months | 609537000000 | 412634.442 |  | 62886.42 | 35805.575 | 28631.022 | 0 | 79610.396 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 224641.108 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 154373.04 | 14448.34 | 0 | 168821.39
Cost per Total Building Area ($/m2) | 36.92 | 3.46 | 0 | 40.38
Cost per Net Conditioned Building Area ($/m2) | 36.92 | 3.46 | 0 | 40.38

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 8111.63 | 1940.21 | 1940.21
Net Site Energy | 8111.63 | 1940.21 | 1940.21
Total Source Energy | 19972.48 | 4777.2 | 4777.2
Net Source Energy | 19972.48 | 4777.2 | 4777.2
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2246.77 | 0 | 0 | 0 | 0
Cooling | 14.44 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 68.06 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 678.54 | 294.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 503.2 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 20.98 | 0 | 0 | 0 | 87.12
Refrigeration | 3350.96 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5548.97 | 2562.66 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 11.84 | 18.59 | 8.07
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 8.61 | 27.86 | 8.07
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 18.29 | 11.61 | 80.7
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 18.29 | 11.61 | 5.38
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 18.29 | 11.61 | 5.38
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 18.29 | 11.61 | 80.7
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.6518
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.6518
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
OFFICE_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 60.34 | 0 | 90 | N
OFFICE_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 54.71 | 90 | 90 | E
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 88.84 | 0 | 180
OFFICE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 88.84 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 621.89 | 180 | 0
DELI_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 224.72 | 0 | 180
DELI_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 224.72 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 2324.94 | 0 | 180
SALES_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 2324.94 | 180 | 0
PRODUCE_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 267.12 | 270 | 90 | W
PRODUCE_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 98.96 | 180 | 90 | S
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 711.36 | 180 | 0
BAKERY_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS | 0.08 | 0.856 | 0.98 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 209.04 | 0 | 180
BAKERY_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 209.04 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 174.7 | 174.7 | 6.49 | 0.34 | 0.34 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 6.49 | 0.34 | 0.34
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 6.49 | 0.34 | 0.34
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6299.81 | 5031.38 | 1268.43 | 0.8 | 4.05
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 35263.49 | 28163.38 | 7100.12 | 0.8 | 3.74
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 27568.9 | 22018.05 | 5550.85 | 0.8 | 3.75
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 130259.04 | 104032.07 | 26226.97 | 0.8 | 4.14
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 39099.69 | 31227.17 | 7872.52 | 0.8 | 3.74
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 27055.95 | 21608.37 | 5447.57 | 0.8 | 3.74
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 2794.75 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 28443.86 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 18852.07 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 105068.15 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 31538.17 | 0.8
PSZ-AC:6_HEATC | Coil:Heating:Gas | 14845.92 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.35 | 125 | 1.18 | 421.39 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.38 | 441.43 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.13 | 2329.72 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.67 | 1821.37 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1109.65 | 7.87 | 14538.4 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.36 | 2583.16 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.63 | 1787.48 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.71 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 55700.3967 | 48.5854 | 355.1539 | 0 | 0.0002 | 2142400 | 20361.5615
February | 48434.1604 | 42.1141 | 332.6554 | 0 | 0.0002 | 2006790 | 17778.0629
March | 53759.8064 | 46.773 | 364.1859 | 0 | 0.0002 | 2196980 | 19717.4762
April | 50369.2633 | 43.728 | 358.2379 | 0 | 0.0002 | 2161180 | 18525.8566
May | 51058.0677 | 44.2083 | 384.1854 | 0 | 0.0002 | 2317810 | 18843.4174
June | 49050.7785 | 42.4091 | 380.0349 | 0 | 0.0002 | 2292810 | 18136.0285
July | 49454.5373 | 42.6762 | 397.8358 | 0 | 0.0002 | 2400270 | 18330.0799
August | 50410.6382 | 43.4934 | 406.9357 | 0 | 0.0002 | 2455180 | 18688.7513
September | 48268.3829 | 41.6247 | 393.2975 | 0 | 0.0002 | 2372910 | 17905.7037
October | 50826.0287 | 43.9543 | 391.9376 | 0 | 0.0002 | 2364620 | 18786.76
November | 51275.8036 | 44.5273 | 362.4904 | 0 | 0.0002 | 2186820 | 18852.5858
December | 55835.6537 | 48.6869 | 358.9659 | 0 | 0.0002 | 2165410 | 20420.0045
Annual Sum or Average | 614443.5174 | 532.7807 | 4485.9163 | 0 | 0.0023 | 27063200 | 226346.2883
Minimum of Months | 48268.3829 | 41.6247 | 332.6554 | 0 | 0.0002 | 2006790 | 17778.0629
Maximum of Months | 55835.6537 | 48.6869 | 406.9357 | 0 | 0.0002 | 2455180 | 20420.0045
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 439272000000 | 307470.245 | 05-JAN-18:10 | 41924.28 | 31827.177 | 23922.94 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 205465.7 | 0 | 0
February | 411468000000 | 314043.995 | 15-FEB-18:10 | 41924.28 | 31827.177 | 23922.94 | 0 | 1300.475 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 210738.975 | 0 | 0
March | 450464000000 | 300313.641 | 27-MAR-17:10 | 41924.28 | 31827.177 | 23922.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202639.244 | 0 | 0
April | 443123000000 | 310604.592 | 29-APR-10:39 | 62886.42 | 35805.575 | 23922.94 | 0 | 4078.585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183911.072 | 0 | 0
May | 475238000000 | 321319.109 | 24-MAY-17:10 | 41924.28 | 31827.177 | 23922.94 | 0 | 4424.684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219220.028 | 0 | 0
June | 470113000000 | 326029.56 | 16-JUN-10:39 | 62886.42 | 35805.575 | 23922.94 | 0 | 8052.424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195362.202 | 0 | 0
July | 492145000000 | 340758.997 | 03-JUL-10:50 | 62886.42 | 35805.575 | 23922.94 | 0 | 12953.785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205190.278 | 0 | 0
August | 503403000000 | 337067.004 | 15-AUG-10:50 | 62886.42 | 35805.575 | 23922.94 | 0 | 9666.256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204785.814 | 0 | 0
September | 486535000000 | 344288.54 | 29-SEP-10:50 | 62886.42 | 35805.575 | 23922.94 | 0 | 12465.992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209207.614 | 0 | 0
October | 484835000000 | 321489.603 | 16-OCT-17:10 | 41924.28 | 31827.177 | 23922.94 | 0 | 6483.053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 217332.152 | 0 | 0
November | 448381000000 | 315274.331 | 16-NOV-18:10 | 41924.28 | 31827.177 | 23922.94 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 213269.786 | 0 | 0
December | 443989000000 | 307336.198 | 14-DEC-18:10 | 41924.28 | 31827.177 | 23922.94 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 205331.654 | 0 | 0
Annual Sum or Average | 5548970000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 411468000000 | 300313.641 |  | 41924.28 | 31827.177 | 23922.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183911.072 | 0 | 0
Maximum of Months | 503403000000 | 344288.54 |  | 62886.42 | 35805.575 | 23922.94 | 0 | 12953.785 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 219220.028 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 222753.96 | 21700.91 | 0 | 244454.87
Cost per Total Building Area ($/m2) | 53.28 | 5.19 | 0 | 58.47
Cost per Net Conditioned Building Area ($/m2) | 53.28 | 5.19 | 0 | 58.47

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 9055.57 | 2165.99 | 2165.99
Net Site Energy | 9055.57 | 2165.99 | 2165.99
Total Source Energy | 24609.18 | 5886.25 | 5886.25
Net Source Energy | 24609.18 | 5886.25 | 5886.25
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2813.31 | 0 | 0 | 0 | 0
Cooling | 176.84 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 68.02 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 678.54 | 294.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 636.35 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 21.22 | 0 | 0 | 0 | 87.12
Refrigeration | 3432.62 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5926.13 | 3129.45 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 11.84 | 18.59 | 8.07
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 8.61 | 27.86 | 8.07
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 18.29 | 11.61 | 80.7
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 18.29 | 11.61 | 5.38
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 18.29 | 11.61 | 5.38
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 18.29 | 11.61 | 80.7
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.6518
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.6518
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
OFFICE_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 60.34 | 0 | 90 | N
OFFICE_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 54.71 | 90 | 90 | E
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 88.84 | 0 | 180
OFFICE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 88.84 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 621.89 | 180 | 0
DELI_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 224.72 | 0 | 180
DELI_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 224.72 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 2324.94 | 0 | 180
SALES_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 2324.94 | 180 | 0
PRODUCE_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 267.12 | 270 | 90 | W
PRODUCE_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 98.96 | 180 | 90 | S
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 711.36 | 180 | 0
BAKERY_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS | 0.08 | 0.856 | 0.98 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 209.04 | 0 | 180
BAKERY_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 209.04 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 174.7 | 174.7 | 3.18 | 0.402 | 0.495 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 3.18 | 0.402 | 0.495
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10451.33 | 7679.26 | 2772.07 | 0.73 | 3.84
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 70035.6 | 47349.89 | 22685.71 | 0.68 | 3.19
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 42051.84 | 33092.93 | 8958.91 | 0.79 | 3.44
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 227225.81 | 153623.55 | 73602.25 | 0.68 | 3.35
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 74295.13 | 50229.69 | 24065.44 | 0.68 | 3.12
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 39606.65 | 31632.06 | 7974.59 | 0.8 | 3.47
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 3822.17 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 51929.41 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 30047.66 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 168481.48 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 55087.73 | 0.8
PSZ-AC:6_HEATC | Coil:Heating:Gas | 22724.49 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.35 | 125 | 1.18 | 421.39 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.52 | 605.06 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.82 | 3084.39 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.46 | 2689.79 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1109.65 | 9.15 | 16905.93 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.99 | 3271.98 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.39 | 2616.65 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.71 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 103687.4835 | 172.2014 | 431.5833 | 0 | 0.0018 | 26832.1487 | 43026.225
February | 91269.9319 | 153.2177 | 388.9473 | 0 | 0.0016 | 24182.1027 | 38023.3
March | 95008.3572 | 167.8464 | 450.9995 | 0 | 0.0019 | 28043.5548 | 40344.5001
April | 87979.7055 | 160.9104 | 447.8995 | 0 | 0.0018 | 27852.8349 | 37861.0242
May | 92840.7369 | 178.9247 | 523.0237 | 0 | 0.0021 | 32527.633 | 40787.1531
June | 98963.0011 | 195.6801 | 584.8814 | 0 | 0.0024 | 36376.2108 | 43930.0164
July | 105834.5322 | 209.9221 | 629.1088 | 0 | 0.0025 | 39127.0961 | 47040.1936
August | 106625.7833 | 211.4059 | 633.3393 | 0 | 0.0026 | 39390.1814 | 47384.0482
September | 93427.8535 | 183.6173 | 545.9943 | 0 | 0.0022 | 33957.331 | 41370.7084
October | 91854.4402 | 173.1058 | 495.8336 | 0 | 0.002 | 30835.4133 | 39995.5957
November | 91592.6259 | 164.3582 | 448.8441 | 0 | 0.0018 | 27910.4748 | 39126.8528
December | 100141.4638 | 168.6037 | 429.4759 | 0 | 0.0018 | 26702.0972 | 41764.2882
Annual Sum or Average | 1159230 | 2139.7938 | 6009.9307 | 0 | 0.0245 | 373737.0789 | 500653.9058
Minimum of Months | 87979.7055 | 153.2177 | 388.9473 | 0 | 0.0016 | 24182.1027 | 37861.0242
Maximum of Months | 106625.7833 | 211.4059 | 633.3393 | 0 | 0.0026 | 39390.1814 | 47384.0482
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 425461000000 | 308163.483 | 09-JAN-11:20 | 62886.42 | 35805.575 | 29595.2 | 0 | 2173.996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177702.293 | 0 | 0
February | 383441000000 | 298245.074 | 13-FEB-11:20 | 62886.42 | 35805.575 | 29595.2 | 0 | 356.283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169601.596 | 0 | 0
March | 444670000000 | 338223.765 | 09-MAR-18:10 | 41924.28 | 31827.177 | 29595.2 | 0 | 7392.756 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 223154.203 | 0 | 0
April | 441646000000 | 336428.128 | 04-APR-17:10 | 41924.28 | 31827.177 | 29595.2 | 0 | 9809.192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223272.278 | 0 | 0
May | 515771000000 | 363495.734 | 15-MAY-17:10 | 41924.28 | 31827.177 | 29595.2 | 0 | 21368.983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 238780.094 | 0 | 0
June | 576796000000 | 425945.16 | 30-JUN-17:10 | 41924.28 | 31827.177 | 29595.2 | 0 | 75668.573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246929.929 | 0 | 0
July | 620415000000 | 432269.845 | 25-JUL-10:00 | 62886.42 | 35805.575 | 29595.2 | 0 | 79968.526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224014.124 | 0 | 0
August | 624587000000 | 428562.149 | 17-AUG-17:10 | 41924.28 | 31827.177 | 29595.2 | 0 | 78620.345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246595.146 | 0 | 0
September | 538441000000 | 375466.994 | 08-SEP-17:10 | 41924.28 | 31827.177 | 29595.2 | 0 | 42118.664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230001.673 | 0 | 0
October | 488939000000 | 351002.54 | 20-OCT-17:10 | 41924.28 | 31827.177 | 29595.2 | 0 | 16533.904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231121.978 | 0 | 0
November | 442560000000 | 341725.738 | 04-NOV-11:50 | 62886.42 | 35805.575 | 29595.2 | 0 | 11292.359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202146.184 | 0 | 0
December | 423399000000 | 309203.945 | 23-DEC-11:20 | 62886.42 | 35805.575 | 29595.2 | 0 | 1793.206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179123.544 | 0 | 0
Annual Sum or Average | 5926130000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 383441000000 | 298245.074 |  | 41924.28 | 31827.177 | 29595.2 | 0 | 356.283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169601.596 | 0 | 0
Maximum of Months | 624587000000 | 432269.845 |  | 62886.42 | 35805.575 | 29595.2 | 0 | 79968.526 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 246929.929 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 115371.36 | 30499.04 | 0 | 145870.4
Cost per Total Building Area ($/m2) | 27.6 | 7.3 | 0 | 34.89
Cost per Net Conditioned Building Area ($/m2) | 27.6 | 7.3 | 0 | 34.89

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 8238.87 | 1970.65 | 1970.65
Net Site Energy | 8238.87 | 1970.65 | 1970.65
Total Source Energy | 21506.68 | 5144.16 | 5144.16
Net Source Energy | 21506.68 | 5144.16 | 5144.16
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2303.15 | 0 | 0 | 0 | 0
Cooling | 114.7 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 68.04 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 678.54 | 294.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 676.73 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 20.93 | 0 | 0 | 0 | 87.12
Refrigeration | 3148.1 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5619.87 | 2618.99 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 11.84 | 18.59 | 8.07
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 8.61 | 27.86 | 8.07
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 18.29 | 11.61 | 80.7
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 18.29 | 11.61 | 5.38
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 18.29 | 11.61 | 5.38
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 18.29 | 11.61 | 80.7
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.6518
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.6518
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
OFFICE_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 60.34 | 0 | 90 | N
OFFICE_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 54.71 | 90 | 90 | E
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 88.84 | 0 | 180
OFFICE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 88.84 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 621.89 | 180 | 0
DELI_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 224.72 | 0 | 180
DELI_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 224.72 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 2324.94 | 0 | 180
SALES_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 2324.94 | 180 | 0
PRODUCE_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 267.12 | 270 | 90 | W
PRODUCE_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 98.96 | 180 | 90 | S
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 711.36 | 180 | 0
BAKERY_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS | 0.08 | 0.856 | 0.98 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 209.04 | 0 | 180
BAKERY_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 209.04 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 174.7 | 174.7 | 3.18 | 0.402 | 0.495 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 3.18 | 0.402 | 0.495
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9548.36 | 7625.85 | 1922.51 | 0.8 | 4.06
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 51462.52 | 41100.81 | 10361.71 | 0.8 | 3.47
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 43439.72 | 34693.36 | 8746.36 | 0.8 | 3.47
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 172981.54 | 138152.61 | 34828.92 | 0.8 | 3.95
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 55017.33 | 43939.88 | 11077.45 | 0.8 | 3.47
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 42408.86 | 33870.06 | 8538.8 | 0.8 | 3.47
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 3470.82 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 45481.7 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 25135.47 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 152878.14 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 48623.38 | 0.8
PSZ-AC:6_HEATC | Coil:Heating:Gas | 19465.54 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.35 | 125 | 1.18 | 421.39 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.58 | 669.05 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.11 | 3399.92 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.62 | 2869.89 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 10.45 | 17705.04 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.32 | 3634.77 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.56 | 2801.78 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.71 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 136174.6705 | 218.6414 | 514.9568 | 0 | 0.0021 | 535347.5987 | 56452.1525
February | 120291.7817 | 195.4116 | 467.1895 | 0 | 0.0019 | 485706.1878 | 50090.6138
March | 131895.8409 | 216.9226 | 526.657 | 0 | 0.0021 | 547550.4785 | 55183.6121
April | 124456.3996 | 209.3193 | 522.0222 | 0 | 0.0021 | 542765.4648 | 52525.391
May | 132312.8995 | 227.7198 | 583.05 | 0 | 0.0023 | 606254.1635 | 56349.921
June | 138652.1948 | 241.1635 | 624.6961 | 0 | 0.0024 | 649574.3656 | 59298.2119
July | 153261.9643 | 267.4361 | 695.1816 | 0 | 0.0027 | 722872.3686 | 65630.9336
August | 152934.8528 | 266.6796 | 692.6927 | 0 | 0.0027 | 720283.1423 | 65472.6394
September | 137282.8171 | 238.5237 | 617.1302 | 0 | 0.0024 | 641705.4212 | 58687.258
October | 131192.2765 | 221.8207 | 556.6216 | 0 | 0.0022 | 578747.8055 | 55483.2027
November | 127457.9261 | 208.6122 | 503.4613 | 0 | 0.002 | 523427.2221 | 53227.6169
December | 136430.0574 | 218.6866 | 513.9477 | 0 | 0.0021 | 534295.6947 | 56522.234
Annual Sum or Average | 1622340 | 2730.937 | 6817.6065 | 0 | 0.0268 | 7088530 | 684923.7867
Minimum of Months | 120291.7817 | 195.4116 | 467.1895 | 0 | 0.0019 | 485706.1878 | 50090.6138
Maximum of Months | 153261.9643 | 267.4361 | 695.1816 | 0 | 0.0027 | 722872.3686 | 65630.9336
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 424430000000 | 290780.892 | 02-JAN-11:20 | 62886.42 | 35805.575 | 31501.851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160587.046 | 0 | 0
February | 385074000000 | 293389.92 | 14-FEB-18:10 | 41924.28 | 31827.177 | 31501.851 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 183806.464 | 0 | 0
March | 434105000000 | 297604.443 | 08-MAR-18:10 | 41924.28 | 31827.177 | 31501.851 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 188020.987 | 0 | 0
April | 430311000000 | 318649.818 | 21-APR-17:10 | 41924.28 | 31827.177 | 31501.851 | 0 | 13781.302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199615.208 | 0 | 0
May | 480646000000 | 336760.598 | 31-MAY-17:10 | 41924.28 | 31827.177 | 31501.851 | 0 | 22161.583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209345.706 | 0 | 0
June | 514990000000 | 358744.411 | 29-JUN-17:10 | 41924.28 | 31827.177 | 31501.851 | 0 | 36512.356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216978.746 | 0 | 0
July | 573102000000 | 372051.782 | 20-JUL-17:10 | 41924.28 | 31827.177 | 31501.851 | 0 | 39377.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227421.464 | 0 | 0
August | 571049000000 | 381952.238 | 01-AUG-17:10 | 41924.28 | 31827.177 | 31501.851 | 0 | 45144.718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231554.212 | 0 | 0
September | 508752000000 | 343439.224 | 01-SEP-17:10 | 41924.28 | 31827.177 | 31501.851 | 0 | 18850.313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219335.603 | 0 | 0
October | 458838000000 | 329748.517 | 11-OCT-17:10 | 41924.28 | 31827.177 | 31501.851 | 0 | 12355.251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212139.958 | 0 | 0
November | 414979000000 | 298174.964 | 10-NOV-11:20 | 62886.42 | 35805.575 | 31501.851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167981.118 | 0 | 0
December | 423596000000 | 289503.015 | 22-DEC-11:20 | 62886.42 | 35805.575 | 31501.851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159309.169 | 0 | 0
Annual Sum or Average | 5619870000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 385074000000 | 289503.015 |  | 41924.28 | 31827.177 | 31501.851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159309.169 | 0 | 0
Maximum of Months | 573102000000 | 381952.238 |  | 62886.42 | 35805.575 | 31501.851 | 0 | 45144.718 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 231554.212 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 57839.61 | 18242.56 | 0 | 76082.17
Cost per Total Building Area ($/m2) | 13.83 | 4.36 | 0 | 18.2
Cost per Net Conditioned Building Area ($/m2) | 13.83 | 4.36 | 0 | 18.2

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 8814.11 | 2108.24 | 2108.24
Net Site Energy | 8814.11 | 2108.24 | 2108.24
Total Source Energy | 13162.53 | 3148.33 | 3148.33
Net Source Energy | 13162.53 | 3148.33 | 3148.33
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 3054.86 | 0 | 0 | 0 | 0
Cooling | 20.29 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 67.91 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 678.54 | 294.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 548.49 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 21.99 | 0 | 0 | 0 | 87.12
Refrigeration | 3193.34 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5442.34 | 3371.77 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 11.84 | 18.59 | 8.07
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 8.61 | 27.86 | 8.07
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 18.29 | 11.61 | 80.7
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 18.29 | 11.61 | 5.38
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 18.29 | 11.61 | 5.38
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 18.29 | 11.61 | 80.7
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.6518
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.6518
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
OFFICE_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 60.34 | 0 | 90 | N
OFFICE_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 54.71 | 90 | 90 | E
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 88.84 | 0 | 180
OFFICE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 88.84 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 621.89 | 180 | 0
DELI_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 224.72 | 0 | 180
DELI_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 224.72 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 2324.94 | 0 | 180
SALES_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 2324.94 | 180 | 0
PRODUCE_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 267.12 | 270 | 90 | W
PRODUCE_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 98.96 | 180 | 90 | S
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 711.36 | 180 | 0
BAKERY_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS | 0.08 | 0.856 | 0.98 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 209.04 | 0 | 180
BAKERY_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 209.04 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 174.7 | 174.7 | 3.18 | 0.402 | 0.495 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 3.18 | 0.402 | 0.495
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7422.34 | 5927.89 | 1494.45 | 0.8 | 4.06
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 46092.64 | 35027.96 | 11064.68 | 0.76 | 3.37
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 28969.82 | 23136.9 | 5832.92 | 0.8 | 3.74
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 170067.54 | 124546.8 | 45520.74 | 0.73 | 3.76
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 44346.47 | 35417.54 | 8928.93 | 0.8 | 3.47
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 28746.39 | 22958.46 | 5787.94 | 0.8 | 3.75
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 3257.57 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 39669.72 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 22262.29 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 134083.66 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 42658.1 | 0.8
PSZ-AC:6_HEATC | Coil:Heating:Gas | 16794.09 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.35 | 125 | 1.18 | 421.39 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.45 | 520.08 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.49 | 2724.55 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.75 | 1913.92 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1109.65 | 8.42 | 15557.59 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.68 | 2929.79 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.74 | 1899.16 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.71 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 44935.9511 | 55.076 | 91.4066 | 0 | 0.0004 | 1206590 | 17082.5165
February | 38157.1173 | 47.6307 | 83.1294 | 0 | 0.0004 | 1097510 | 14597.9857
March | 41061.6867 | 51.9458 | 93.8588 | 0 | 0.0004 | 1239300 | 15783.0344
April | 36712.4676 | 47.7527 | 92.2744 | 0 | 0.0004 | 1218630 | 14251.4929
May | 33668.2785 | 46.3455 | 100.9199 | 0 | 0.0004 | 1333250 | 13343.1314
June | 30393.3296 | 43.3978 | 101.0665 | 0 | 0.0004 | 1335410 | 12212.3563
July | 29512.8322 | 43.7585 | 108.4687 | 0 | 0.0004 | 1433430 | 12031.8424
August | 29386.1302 | 44.2145 | 112.1143 | 0 | 0.0004 | 1481680 | 12049.1519
September | 31070.8615 | 44.2588 | 102.6397 | 0 | 0.0004 | 1356190 | 12473.1924
October | 36578.5729 | 48.808 | 99.7878 | 0 | 0.0004 | 1318070 | 14331.1927
November | 40736.2519 | 51.226 | 91.1475 | 0 | 0.0004 | 1203440 | 15624.9447
December | 45014.4459 | 55.3278 | 92.5602 | 0 | 0.0004 | 1221850 | 17129.0304
Annual Sum or Average | 437227.9253 | 579.742 | 1169.3738 | 0 | 0.0049 | 15445400 | 170909.8718
Minimum of Months | 29386.1302 | 43.3978 | 83.1294 | 0 | 0.0004 | 1097510 | 12031.8424
Maximum of Months | 45014.4459 | 55.3278 | 112.1143 | 0 | 0.0004 | 1481680 | 17129.0304
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 425154000000 | 300380.502 | 14-JAN-11:20 | 62886.42 | 35805.575 | 25966.481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175722.026 | 0 | 0
February | 386720000000 | 291589.416 | 24-FEB-18:10 | 41924.28 | 31827.177 | 25966.481 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 187541.33 | 0 | 0
March | 436681000000 | 300857.655 | 30-MAR-17:10 | 41924.28 | 31827.177 | 25966.481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201139.716 | 0 | 0
April | 429398000000 | 306086.289 | 29-APR-17:10 | 34936.9 | 27848.78 | 25966.481 | 0 | 2642.864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214691.264 | 0 | 0
May | 469785000000 | 329133.478 | 05-MAY-17:10 | 41924.28 | 31827.177 | 25966.481 | 0 | 7567.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221848.27 | 0 | 0
June | 470547000000 | 327187.533 | 28-JUN-10:39 | 62886.42 | 35805.575 | 25966.481 | 0 | 8237.281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194291.775 | 0 | 0
July | 505085000000 | 346553.426 | 31-JUL-17:10 | 41924.28 | 31827.177 | 25966.481 | 0 | 17384.276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229451.212 | 0 | 0
August | 522087000000 | 343540.312 | 18-AUG-17:10 | 41924.28 | 31827.177 | 25966.481 | 0 | 15349.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228472.704 | 0 | 0
September | 477867000000 | 346642.803 | 02-SEP-17:10 | 34936.9 | 27848.78 | 25966.481 | 0 | 34542.516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223348.126 | 0 | 0
October | 464436000000 | 310124.785 | 05-OCT-17:10 | 41924.28 | 31827.177 | 25966.481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210406.847 | 0 | 0
November | 424047000000 | 314718.013 | 03-NOV-18:10 | 41924.28 | 31827.177 | 25966.481 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 210669.927 | 0 | 0
December | 430532000000 | 294445.536 | 05-DEC-11:20 | 62886.42 | 35805.575 | 25966.481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169787.06 | 0 | 0
Annual Sum or Average | 5442340000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 386720000000 | 291589.416 |  | 34936.9 | 27848.78 | 25966.481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169787.06 | 0 | 0
Maximum of Months | 522087000000 | 346642.803 |  | 62886.42 | 35805.575 | 25966.481 | 0 | 34542.516 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 229451.212 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 107645.4 | 28186.33 | 0 | 135831.73
Cost per Total Building Area ($/m2) | 25.75 | 6.74 | 0 | 32.49
Cost per Net Conditioned Building Area ($/m2) | 25.75 | 6.74 | 0 | 32.49

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 9776.32 | 2338.39 | 2338.39
Net Site Energy | 9776.32 | 2338.39 | 2338.39
Total Source Energy | 24806.71 | 5933.49 | 5933.49
Net Source Energy | 24806.71 | 5933.49 | 5933.49
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 3700.54 | 0 | 0 | 0 | 0
Cooling | 108.28 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 68.03 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 678.54 | 294.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 683.75 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 22.52 | 0 | 0 | 0 | 87.12
Refrigeration | 3285.97 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5758.34 | 4017.98 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 11.84 | 18.59 | 8.07
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 8.61 | 27.86 | 8.07
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 18.29 | 11.61 | 80.7
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 18.29 | 11.61 | 5.38
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 18.29 | 11.61 | 5.38
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 18.29 | 11.61 | 80.7
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.6518
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.6518
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
OFFICE_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 60.34 | 0 | 90 | N
OFFICE_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 54.71 | 90 | 90 | E
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 88.84 | 0 | 180
OFFICE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 88.84 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 621.89 | 180 | 0
DELI_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 224.72 | 0 | 180
DELI_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 224.72 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 2324.94 | 0 | 180
SALES_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 2324.94 | 180 | 0
PRODUCE_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 267.12 | 270 | 90 | W
PRODUCE_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 98.96 | 180 | 90 | S
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 711.36 | 180 | 0
BAKERY_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS | 0.08 | 0.698 | 0.78 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 209.04 | 0 | 180
BAKERY_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 209.04 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 174.7 | 174.7 | 3.18 | 0.402 | 0.495 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 3.18 | 0.402 | 0.495
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12829.15 | 9247.42 | 3581.73 | 0.72 | 3.79
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 81645.14 | 55198.91 | 26446.23 | 0.68 | 3.12
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 40272.58 | 31707.62 | 8564.97 | 0.79 | 3.44
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 257855.09 | 174331.5 | 83523.59 | 0.68 | 3.27
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 85093.01 | 57529.95 | 27563.05 | 0.68 | 3.12
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 38087.19 | 30418.53 | 7668.65 | 0.8 | 3.74
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 4427.75 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 68112.75 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 32671.74 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 223351.97 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 73706.87 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 23439.25 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.35 | 125 | 1.18 | 421.39 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.61 | 708.61 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.29 | 3595.68 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.36 | 2578.65 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 10.38 | 17593.23 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.43 | 3747.52 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.3 | 2516.27 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.71 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 186119.869 | 302.3571 | 800.5621 | 0 | 0.0025 | 184251.0632 | 77172.3079
February | 163674.5849 | 268.8697 | 721.8554 | 0 | 0.0022 | 166141.4556 | 68150.1436
March | 176127.4027 | 294.7886 | 809.523 | 0 | 0.0025 | 186327.7382 | 73857.4792
April | 164555.4454 | 284.024 | 807.9121 | 0 | 0.0025 | 185970.2716 | 69827.4815
May | 177247.2834 | 315.4189 | 927.1065 | 0 | 0.0028 | 213420.903 | 76120.35
June | 189887.6235 | 343.3151 | 1025.6079 | 0 | 0.0031 | 236103.3725 | 82065.3645
July | 207623.725 | 376.4727 | 1127.9422 | 0 | 0.0034 | 259663.0093 | 89834.824
August | 204455.6818 | 370.5197 | 1109.4815 | 0 | 0.0033 | 255412.8982 | 88444.1366
September | 182464.11 | 328.5318 | 977.3496 | 0 | 0.003 | 224992.1212 | 78726.8892
October | 173399.016 | 303.7086 | 877.8311 | 0 | 0.0027 | 202071.0448 | 74002.8143
November | 169027.2277 | 285.9317 | 795.0336 | 0 | 0.0024 | 182997.4022 | 71169.4751
December | 182379.5186 | 298.9515 | 800.484 | 0 | 0.0025 | 184237.4881 | 75876.768
Annual Sum or Average | 2176960 | 3772.8895 | 10780.6889 | 0 | 0.0329 | 2481590 | 925248.034
Minimum of Months | 163674.5849 | 268.8697 | 721.8554 | 0 | 0.0022 | 166141.4556 | 68150.1436
Maximum of Months | 207623.725 | 376.4727 | 1127.9422 | 0 | 0.0034 | 259663.0093 | 89834.824
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 427541000000 | 292757.704 | 17-JAN-18:10 | 41924.28 | 31827.177 | 31161.36 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 183514.738 | 0 | 0
February | 385519000000 | 293046.033 | 28-FEB-11:20 | 62886.42 | 35805.575 | 31161.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163192.678 | 0 | 0
March | 432359000000 | 316730.655 | 14-MAR-17:10 | 41924.28 | 31827.177 | 31161.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211817.837 | 0 | 0
April | 431530000000 | 318233.533 | 10-APR-10:09 | 62886.42 | 35805.575 | 31161.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188380.178 | 0 | 0
May | 495227000000 | 363066.205 | 30-MAY-17:10 | 41924.28 | 31827.177 | 31161.36 | 0 | 19307.619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 238845.769 | 0 | 0
June | 547860000000 | 393012.572 | 20-JUN-17:10 | 41924.28 | 31827.177 | 31161.36 | 0 | 47040.978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241058.776 | 0 | 0
July | 602528000000 | 421072.067 | 14-JUL-10:00 | 62886.42 | 35805.575 | 31161.36 | 0 | 68933.555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222285.156 | 0 | 0
August | 592666000000 | 415542.861 | 04-AUG-17:10 | 41924.28 | 31827.177 | 31161.36 | 0 | 65193.137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245436.906 | 0 | 0
September | 522077000000 | 366247.24 | 06-SEP-10:50 | 62886.42 | 35805.575 | 31161.36 | 0 | 23050.926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 213342.959 | 0 | 0
October | 468891000000 | 340995.54 | 31-OCT-18:10 | 41924.28 | 31827.177 | 31161.36 | 0 | 7719.905 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 224032.669 | 0 | 0
November | 424632000000 | 342802.759 | 02-NOV-18:10 | 41924.28 | 31827.177 | 31161.36 | 0 | 7463.564 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 226096.229 | 0 | 0
December | 427509000000 | 299991.411 | 12-DEC-18:10 | 41924.28 | 31827.177 | 31161.36 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 190748.446 | 0 | 0
Annual Sum or Average | 5758340000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 385519000000 | 292757.704 |  | 41924.28 | 31827.177 | 31161.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163192.678 | 0 | 0
Maximum of Months | 602528000000 | 421072.067 |  | 62886.42 | 35805.575 | 31161.36 | 0 | 68933.555 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 245436.906 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 153678.96 | 33920.69 | 0 | 187599.65
Cost per Total Building Area ($/m2) | 36.76 | 8.11 | 0 | 44.87
Cost per Net Conditioned Building Area ($/m2) | 36.76 | 8.11 | 0 | 44.87

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 8928.47 | 2135.59 | 2135.59
Net Site Energy | 8928.47 | 2135.59 | 2135.59
Total Source Energy | 22305.19 | 5335.16 | 5335.16
Net Source Energy | 22305.19 | 5335.16 | 5335.16
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2970.8 | 0 | 0 | 0 | 0
Cooling | 68.16 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 67.99 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 678.54 | 294.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 865.63 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 22.46 | 0 | 0 | 0 | 87.12
Refrigeration | 3026.21 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5640.3 | 3288.18 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 11.84 | 18.59 | 8.07
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 8.61 | 27.86 | 8.07
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 18.29 | 11.61 | 80.7
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 18.29 | 11.61 | 5.38
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 18.29 | 11.61 | 5.38
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 18.29 | 11.61 | 80.7
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.6518
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.6518
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
OFFICE_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 60.34 | 0 | 90 | N
OFFICE_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 54.71 | 90 | 90 | E
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 88.84 | 0 | 180
OFFICE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 88.84 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 621.89 | 180 | 0
DELI_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 224.72 | 0 | 180
DELI_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 224.72 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 2324.94 | 0 | 180
SALES_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 2324.94 | 180 | 0
PRODUCE_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 267.12 | 270 | 90 | W
PRODUCE_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 98.96 | 180 | 90 | S
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 711.36 | 180 | 0
BAKERY_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS | 0.08 | 0.698 | 0.78 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 209.04 | 0 | 180
BAKERY_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 209.04 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 174.7 | 174.7 | 3.18 | 0.402 | 0.495 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 3.18 | 0.402 | 0.495
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11020.05 | 8801.22 | 2218.83 | 0.8 | 4.06
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 59308.37 | 47366.94 | 11941.43 | 0.8 | 4.37
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 35912.04 | 28681.34 | 7230.7 | 0.8 | 3.74
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 192648.29 | 153859.57 | 38788.72 | 0.8 | 3.95
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 61965.28 | 49488.9 | 12476.38 | 0.8 | 4.36
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 35333.65 | 28219.4 | 7114.24 | 0.8 | 3.74
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 4025.42 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 57028.68 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 25675.07 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 203086.63 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 63194.42 | 0.8
PSZ-AC:6_HEATC | Coil:Heating:Gas | 18413.13 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.35 | 125 | 1.18 | 421.39 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.67 | 772.17 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.58 | 6833.98 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.17 | 2372.56 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 11.64 | 19717.98 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.74 | 7140.13 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.13 | 2334.35 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.71 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 145358.824 | 231.2438 | 538.0849 | 0 | 0.0022 | 559375.0059 | 60049.2348
February | 128413.7489 | 205.8202 | 483.6579 | 0 | 0.0019 | 502806.5734 | 53199.4641
March | 138831.2226 | 226.2258 | 542.9669 | 0 | 0.0022 | 564492.186 | 57879.0022
April | 129504.3496 | 215.7941 | 532.2884 | 0 | 0.0021 | 553425.6478 | 54458.1547
May | 136203.8932 | 231.1047 | 582.2706 | 0 | 0.0023 | 605421.9822 | 57682.1743
June | 137450.4033 | 237.2911 | 609.636 | 0 | 0.0024 | 633903.0093 | 58609.4322
July | 151616.1845 | 264.2391 | 685.9569 | 0 | 0.0027 | 713278.1508 | 64894.2772
August | 149290.1758 | 259.7764 | 673.2201 | 0 | 0.0026 | 700031.4955 | 63858.5975
September | 132711.7797 | 227.8616 | 581.8595 | 0 | 0.0023 | 605012.6898 | 56466.3679
October | 133769.2062 | 224.4899 | 558.4195 | 0 | 0.0022 | 580605.6921 | 56407.4663
November | 133916.0016 | 217.4675 | 519.69 | 0 | 0.0021 | 540286.932 | 55756.3755
December | 145542.7119 | 230.7502 | 534.5107 | 0 | 0.0021 | 555653.2555 | 60048.0906
Annual Sum or Average | 1662610 | 2772.0645 | 6842.5614 | 0 | 0.027 | 7114290 | 699308.6374
Minimum of Months | 128413.7489 | 205.8202 | 483.6579 | 0 | 0.0019 | 502806.5734 | 53199.4641
Maximum of Months | 151616.1845 | 264.2391 | 685.9569 | 0 | 0.0027 | 713278.1508 | 64894.2772
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 443479000000 | 301617.7 | 23-JAN-11:20 | 62886.42 | 35805.575 | 39592.569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163333.137 | 0 | 0
February | 398631000000 | 297736.962 | 11-FEB-11:20 | 62886.42 | 35805.575 | 39592.569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159452.399 | 0 | 0
March | 447536000000 | 312983.233 | 30-MAR-17:10 | 41924.28 | 31827.177 | 39592.569 | 0 | 6868.618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192770.588 | 0 | 0
April | 438763000000 | 320147.946 | 25-APR-17:10 | 41924.28 | 31827.177 | 39592.569 | 0 | 5320.883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201483.037 | 0 | 0
May | 479986000000 | 339659.226 | 24-MAY-10:39 | 62886.42 | 35805.575 | 39592.569 | 0 | 9689.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191684.853 | 0 | 0
June | 502566000000 | 355353.99 | 30-JUN-10:50 | 62886.42 | 35805.575 | 39592.569 | 0 | 14508.035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202561.392 | 0 | 0
July | 565496000000 | 371527.254 | 19-JUL-10:50 | 62886.42 | 35805.575 | 39592.569 | 0 | 25494.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207747.911 | 0 | 0
August | 554993000000 | 372586.021 | 30-AUG-10:50 | 62886.42 | 35805.575 | 39592.569 | 0 | 27122.988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207178.469 | 0 | 0
September | 479661000000 | 346749.825 | 01-SEP-17:10 | 41924.28 | 31827.177 | 39592.569 | 0 | 19054.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214351.028 | 0 | 0
October | 460311000000 | 322822.412 | 05-OCT-17:10 | 41924.28 | 31827.177 | 39592.569 | 0 | 11241.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198237.356 | 0 | 0
November | 428346000000 | 300705.225 | 16-NOV-11:20 | 62886.42 | 35805.575 | 39592.569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162420.661 | 0 | 0
December | 440529000000 | 296199.065 | 30-DEC-11:20 | 62886.42 | 35805.575 | 39592.569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157914.501 | 0 | 0
Annual Sum or Average | 5640300000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 398631000000 | 296199.065 |  | 41924.28 | 31827.177 | 39592.569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157914.501 | 0 | 0
Maximum of Months | 565496000000 | 372586.021 |  | 62886.42 | 35805.575 | 39592.569 | 0 | 27122.988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214351.028 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 58049.12 | 22986.94 | 0 | 81036.06
Cost per Total Building Area ($/m2) | 13.88 | 5.5 | 0 | 19.38
Cost per Net Conditioned Building Area ($/m2) | 13.88 | 5.5 | 0 | 19.38

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 10626.92 | 2541.84 | 2541.84
Net Site Energy | 10626.92 | 2541.84 | 2541.84
Total Source Energy | 25395.52 | 6074.33 | 6074.33
Net Source Energy | 25395.52 | 6074.33 | 6074.33
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 4427.36 | 0 | 0 | 0 | 0
Cooling | 107.81 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 67.98 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 678.54 | 294.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 872.9 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 23.65 | 0 | 0 | 0 | 87.12
Refrigeration | 3219.99 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5880.99 | 4745.93 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 11.84 | 18.59 | 8.07
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 8.61 | 27.86 | 8.07
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 18.29 | 11.61 | 80.7
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 18.29 | 11.61 | 5.38
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 18.29 | 11.61 | 5.38
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 18.29 | 11.61 | 80.7
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.6518
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.6518
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
OFFICE_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 60.34 | 0 | 90 | N
OFFICE_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 54.71 | 90 | 90 | E
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 88.84 | 0 | 180
OFFICE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 88.84 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 621.89 | 180 | 0
DELI_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 224.72 | 0 | 180
DELI_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 224.72 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 2324.94 | 0 | 180
SALES_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 2324.94 | 180 | 0
PRODUCE_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 267.12 | 270 | 90 | W
PRODUCE_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 98.96 | 180 | 90 | S
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 711.36 | 180 | 0
BAKERY_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS | 0.08 | 0.591 | 0.65 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 209.04 | 0 | 180
BAKERY_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 209.04 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 174.7 | 174.7 | 3.18 | 0.402 | 0.495 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 3.18 | 0.402 | 0.495
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13174.97 | 9654.7 | 3520.27 | 0.73 | 3.83
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 88280.4 | 59684.9 | 28595.5 | 0.68 | 3.53
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 39047.16 | 31185.22 | 7861.94 | 0.8 | 3.74
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 274893.41 | 185850.83 | 89042.59 | 0.68 | 3.27
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 91603.64 | 61931.69 | 29671.96 | 0.68 | 3.53
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 38142.22 | 30462.48 | 7679.73 | 0.8 | 3.74
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 4714.5 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 75314.01 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 34569.92 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 257327.37 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 83583.42 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 24278.97 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.35 | 125 | 1.18 | 421.39 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.65 | 757.83 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.56 | 6781.02 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.36 | 2579.69 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 11.07 | 18755.75 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.69 | 7036.28 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.3 | 2519.9 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.71 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 149507.1263 | 225.5217 | 293.1358 | 0 | 0.0022 | 192517.0152 | 60329.6242
February | 128031.8045 | 196.8762 | 263.2355 | 0 | 0.002 | 172901.0873 | 52022.1435
March | 128398.7689 | 207.1054 | 295.4606 | 0 | 0.0022 | 194119.3212 | 53095.0873
April | 114595.9052 | 194.2519 | 294.3402 | 0 | 0.0022 | 193428.3214 | 48286.8707
May | 121221.891 | 214.5138 | 340.7629 | 0 | 0.0025 | 223974.2078 | 51942.007
June | 125522.7808 | 226.6155 | 367.4759 | 0 | 0.0027 | 241549.5348 | 54214.1461
July | 133374.6418 | 241.5104 | 392.805 | 0 | 0.0029 | 258201.6551 | 57674.1805
August | 133866.4919 | 242.3851 | 394.2017 | 0 | 0.0029 | 259119.629 | 57885.3427
September | 118480.4592 | 210.9069 | 337.1082 | 0 | 0.0025 | 221576.9594 | 50886.278
October | 118390.4714 | 200.8288 | 304.5576 | 0 | 0.0023 | 200143.4454 | 49899.6033
November | 122791.7031 | 198.0576 | 282.5463 | 0 | 0.0021 | 185634.5528 | 50776.1245
December | 142193.8832 | 218.3054 | 291.22 | 0 | 0.0022 | 191280.264 | 57743.248
Annual Sum or Average | 1536380 | 2576.8787 | 3856.8496 | 0 | 0.0286 | 2534450 | 644754.6558
Minimum of Months | 114595.9052 | 194.2519 | 263.2355 | 0 | 0.002 | 172901.0873 | 48286.8707
Maximum of Months | 149507.1263 | 242.3851 | 394.2017 | 0 | 0.0029 | 259119.629 | 60329.6242
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 446721000000 | 296266.356 | 30-JAN-11:20 | 62886.42 | 35805.575 | 38851.852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158722.509 | 0 | 0
February | 401204000000 | 295708.115 | 21-FEB-11:20 | 62886.42 | 35805.575 | 38851.852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158164.268 | 0 | 0
March | 450439000000 | 309346.536 | 23-MAR-17:10 | 41924.28 | 31827.177 | 38851.852 | 0 | 2721.085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194022.141 | 0 | 0
April | 448836000000 | 333429.377 | 01-APR-17:10 | 34936.9 | 27848.78 | 38851.852 | 0 | 6604.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225187.595 | 0 | 0
May | 519715000000 | 390053.33 | 27-MAY-17:10 | 34936.9 | 27848.78 | 38851.852 | 0 | 46535.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241879.867 | 0 | 0
June | 560497000000 | 415636.467 | 29-JUN-17:10 | 41924.28 | 31827.177 | 38851.852 | 0 | 59938.141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243095.016 | 0 | 0
July | 599137000000 | 415462.797 | 13-JUL-17:10 | 41924.28 | 31827.177 | 38851.852 | 0 | 57627.921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245231.566 | 0 | 0
August | 601268000000 | 416305.186 | 25-AUG-17:10 | 41924.28 | 31827.177 | 38851.852 | 0 | 60292.985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243408.891 | 0 | 0
September | 514153000000 | 363235.77 | 14-SEP-17:10 | 41924.28 | 31827.177 | 38851.852 | 0 | 18424.958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232207.501 | 0 | 0
October | 464418000000 | 325112.48 | 14-OCT-10:20 | 62886.42 | 35805.575 | 38851.852 | 0 | 2345.566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185223.067 | 0 | 0
November | 430751000000 | 310413.876 | 02-NOV-18:10 | 41924.28 | 31827.177 | 38851.852 | 0 | 1709.805 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 191770.614 | 0 | 0
December | 443851000000 | 299942.2 | 02-DEC-11:20 | 62886.42 | 35805.575 | 38851.852 | 0 | 104.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162293.783 | 0 | 0
Annual Sum or Average | 5880990000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 401204000000 | 295708.115 |  | 34936.9 | 27848.78 | 38851.852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158164.268 | 0 | 0
Maximum of Months | 601268000000 | 416305.186 |  | 62886.42 | 35805.575 | 38851.852 | 0 | 60292.985 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 245231.566 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 88373.54 | 37317.51 | 0 | 125691.04
Cost per Total Building Area ($/m2) | 21.14 | 8.93 | 0 | 30.06
Cost per Net Conditioned Building Area ($/m2) | 21.14 | 8.93 | 0 | 30.06

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 9943.16 | 2378.3 | 2378.3
Net Site Energy | 9943.16 | 2378.3 | 2378.3
Total Source Energy | 24163.37 | 5779.61 | 5779.61
Net Source Energy | 24163.37 | 5779.61 | 5779.61
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 4043.25 | 0 | 0 | 0 | 0
Cooling | 41.43 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 67.97 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 678.54 | 294.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 929.64 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 23.86 | 0 | 0 | 0 | 87.12
Refrigeration | 2929.8 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5581.14 | 4362.02 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 11.84 | 18.59 | 8.07
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 8.61 | 27.86 | 8.07
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 18.29 | 11.61 | 80.7
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 18.29 | 11.61 | 5.38
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 18.29 | 11.61 | 5.38
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 18.29 | 11.61 | 80.7
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.6518
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.6518
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
OFFICE_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 60.34 | 0 | 90 | N
OFFICE_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 54.71 | 90 | 90 | E
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 88.84 | 0 | 180
OFFICE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 88.84 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 621.89 | 180 | 0
DELI_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 224.72 | 0 | 180
DELI_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 224.72 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 2324.94 | 0 | 180
SALES_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 2324.94 | 180 | 0
PRODUCE_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 267.12 | 270 | 90 | W
PRODUCE_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 98.96 | 180 | 90 | S
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 711.36 | 180 | 0
BAKERY_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS | 0.08 | 0.591 | 0.65 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 209.04 | 0 | 180
BAKERY_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 209.04 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 174.7 | 174.7 | 3.18 | 0.402 | 0.495 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 3.18 | 0.402 | 0.495
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11929.78 | 9527.78 | 2402 | 0.8 | 4.03
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 64974.42 | 51892.17 | 13082.26 | 0.8 | 4.37
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 33259.27 | 26562.69 | 6696.58 | 0.8 | 3.74
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 205566.61 | 164176.86 | 41389.76 | 0.8 | 3.95
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 67601.26 | 53990.1 | 13611.16 | 0.8 | 4.32
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 32919.8 | 26291.57 | 6628.23 | 0.8 | 3.74
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 4607.54 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 70829.03 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 29188.57 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 251088.25 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 78547.18 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 19994.82 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.35 | 125 | 1.18 | 421.39 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.72 | 820.99 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.93 | 7486.87 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.01 | 2197.31 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 12.42 | 21040.2 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 4.08 | 7661.15 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.99 | 2174.88 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.71 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 146351.8071 | 225.0544 | 334.1436 | 0 | 0.0024 | 7922110 | 59565.9516
February | 127933.6052 | 199.5324 | 302.2214 | 0 | 0.0022 | 7165820 | 52340.3913
March | 130713.7834 | 211.1177 | 335.0058 | 0 | 0.0024 | 7944510 | 54178.5547
April | 120783.1668 | 198.3843 | 321.5096 | 0 | 0.0023 | 7625030 | 50382.0277
May | 122884.4394 | 207.5548 | 347.7862 | 0 | 0.0024 | 8249160 | 51811.3595
June | 123223.7723 | 213.0339 | 366.4889 | 0 | 0.0026 | 8693540 | 52428.6594
July | 129121.6073 | 226.4356 | 395.6222 | 0 | 0.0027 | 9385090 | 55247.8828
August | 130167.0912 | 227.5217 | 396.123 | 0 | 0.0028 | 9396860 | 55622.9832
September | 120723.7522 | 207.1635 | 353.4541 | 0 | 0.0025 | 8384110 | 51215.3021
October | 123688.8184 | 205.228 | 336.7347 | 0 | 0.0024 | 7986450 | 51794.268
November | 126720.5947 | 203.1716 | 319.3589 | 0 | 0.0023 | 7573200 | 52378.7741
December | 142655.8826 | 221.181 | 332.2514 | 0 | 0.0024 | 7877600 | 58236.6605
Annual Sum or Average | 1544970 | 2545.3791 | 4140.6999 | 0 | 0.0292 | 98203500 | 645202.8148
Minimum of Months | 120723.7522 | 198.3843 | 302.2214 | 0 | 0.0022 | 7165820 | 50382.0277
Maximum of Months | 146351.8071 | 227.5217 | 396.123 | 0 | 0.0028 | 9396860 | 59565.9516
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 450233000000 | 299860.13 | 23-JAN-11:20 | 62886.42 | 35805.575 | 41802.785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159365.351 | 0 | 0
February | 407251000000 | 308317.992 | 02-FEB-18:10 | 41924.28 | 31827.177 | 41802.785 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 188433.603 | 0 | 0
March | 451506000000 | 310102.171 | 30-MAR-17:10 | 41924.28 | 31827.177 | 41802.785 | 0 | 3712.782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190835.147 | 0 | 0
April | 433349000000 | 307780.77 | 24-APR-10:20 | 62886.42 | 35805.575 | 41802.785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167285.99 | 0 | 0
May | 468819000000 | 329521.798 | 25-MAY-17:10 | 41924.28 | 31827.177 | 41802.785 | 0 | 9979.786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203987.77 | 0 | 0
June | 494075000000 | 361762.312 | 30-JUN-10:50 | 62886.42 | 35805.575 | 41802.785 | 0 | 17059.333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204208.2 | 0 | 0
July | 533377000000 | 368945.073 | 21-JUL-17:10 | 41924.28 | 31827.177 | 41802.785 | 0 | 36772.704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216618.127 | 0 | 0
August | 534046000000 | 364554.75 | 11-AUG-17:10 | 41924.28 | 31827.177 | 41802.785 | 0 | 25707.348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223293.16 | 0 | 0
September | 476489000000 | 348066.278 | 01-SEP-17:10 | 41924.28 | 31827.177 | 41802.785 | 0 | 17759.041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214752.995 | 0 | 0
October | 453889000000 | 323233.709 | 06-OCT-17:10 | 41924.28 | 31827.177 | 41802.785 | 0 | 7741.649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199937.818 | 0 | 0
November | 430403000000 | 301103.424 | 07-NOV-18:10 | 41924.28 | 31827.177 | 41802.785 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 181219.034 | 0 | 0
December | 447703000000 | 298096.056 | 29-DEC-18:10 | 41924.28 | 31827.177 | 41802.785 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 178211.666 | 0 | 0
Annual Sum or Average | 5581140000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 407251000000 | 298096.056 |  | 41924.28 | 31827.177 | 41802.785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159365.351 | 0 | 0
Maximum of Months | 534046000000 | 368945.073 |  | 62886.42 | 35805.575 | 41802.785 | 0 | 36772.704 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 223293.16 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 109078.41 | 36194.47 | 0 | 145272.88
Cost per Total Building Area ($/m2) | 26.09 | 8.66 | 0 | 34.75
Cost per Net Conditioned Building Area ($/m2) | 26.09 | 8.66 | 0 | 34.75

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 11414.28 | 2730.17 | 2730.17
Net Site Energy | 11414.28 | 2730.17 | 2730.17
Total Source Energy | 25625.59 | 6129.36 | 6129.36
Net Source Energy | 25625.59 | 6129.36 | 6129.36
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 5481.4 | 0 | 0 | 0 | 0
Cooling | 39.28 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 67.93 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 678.54 | 294.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 903.98 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 25.52 | 0 | 0 | 0 | 87.12
Refrigeration | 2988.95 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5612.45 | 5801.83 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 11.84 | 18.59 | 8.07
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 8.61 | 27.86 | 8.07
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 18.29 | 11.61 | 80.7
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 18.29 | 11.61 | 5.38
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 18.29 | 11.61 | 5.38
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 18.29 | 11.61 | 80.7
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.6518
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.6518
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
OFFICE_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 60.34 | 0 | 90 | N
OFFICE_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 54.71 | 90 | 90 | E
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 88.84 | 0 | 180
OFFICE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 88.84 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 621.89 | 180 | 0
DELI_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 224.72 | 0 | 180
DELI_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 224.72 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 2324.94 | 0 | 180
SALES_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 2324.94 | 180 | 0
PRODUCE_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 267.12 | 270 | 90 | W
PRODUCE_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 98.96 | 180 | 90 | S
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 711.36 | 180 | 0
BAKERY_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS | 0.08 | 0.512 | 0.55 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 209.04 | 0 | 180
BAKERY_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 209.04 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 174.7 | 174.7 | 3.18 | 0.501 | 0.49 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 3.18 | 0.501 | 0.49
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 3.18 | 0.501 | 0.49
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11195.64 | 8941.45 | 2254.18 | 0.8 | 4.06
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 92028.42 | 62218.87 | 29809.55 | 0.68 | 3.53
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 29959.16 | 23927.04 | 6032.12 | 0.8 | 3.74
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 291379.32 | 196996.67 | 94382.65 | 0.68 | 3.27
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 82241.13 | 58917.49 | 23323.64 | 0.72 | 3.72
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 29253.66 | 23363.59 | 5890.07 | 0.8 | 3.75
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 4786.42 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 77961.19 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 31307.59 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 277324.01 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 86637.77 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 20733.22 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.35 | 125 | 1.18 | 421.39 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.68 | 784.48 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.71 | 7068.91 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.81 | 1979.28 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 11.73 | 19880.56 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.86 | 7356.29 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.77 | 1932.67 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.71 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 150675.3952 | 226.9536 | 294.3508 | 0 | 0.0023 | 193313.0846 | 60769.472
February | 132745.0403 | 201.9078 | 265.7103 | 0 | 0.002 | 174514.7282 | 53725.4142
March | 135388.542 | 212.5881 | 292.6862 | 0 | 0.0022 | 192268.7837 | 55431.8704
April | 117833.8707 | 193.1897 | 281.326 | 0 | 0.0021 | 184847.8437 | 49025.0602
May | 116661.2992 | 199.1131 | 304.0741 | 0 | 0.0022 | 199830.8806 | 49287.1722
June | 115870.9123 | 205.3909 | 326.848 | 0 | 0.0024 | 214829.7049 | 49682.2688
July | 126877.5482 | 228.1943 | 368.6188 | 0 | 0.0027 | 242297.5745 | 54716.403
August | 125419.2758 | 223.7712 | 358.5197 | 0 | 0.0026 | 235652.4538 | 53915.4232
September | 116656.6447 | 202.201 | 314.1425 | 0 | 0.0023 | 206460.7547 | 49581.1279
October | 119754.6222 | 199.5969 | 296.5208 | 0 | 0.0022 | 194846.729 | 50135.6264
November | 127917.5653 | 203.3168 | 284.5444 | 0 | 0.0021 | 186932.8752 | 52608.1551
December | 146723.6897 | 223.1832 | 293.7352 | 0 | 0.0022 | 192921.1674 | 59384.2459
Annual Sum or Average | 1532520 | 2519.4065 | 3681.0768 | 0 | 0.0275 | 2418720 | 638262.2394
Minimum of Months | 115870.9123 | 193.1897 | 265.7103 | 0 | 0.002 | 174514.7282 | 49025.0602
Maximum of Months | 150675.3952 | 228.1943 | 368.6188 | 0 | 0.0027 | 242297.5745 | 60769.472
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 448568000000 | 293439.633 | 13-JAN-11:20 | 62886.42 | 35805.575 | 39423.588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155324.05 | 0 | 0
February | 404948000000 | 298533.109 | 21-FEB-11:20 | 62886.42 | 35805.575 | 39423.588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160417.526 | 0 | 0
March | 446145000000 | 299842.334 | 30-MAR-10:20 | 62886.42 | 35805.575 | 39423.588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161726.751 | 0 | 0
April | 428925000000 | 307126.773 | 14-APR-10:20 | 62886.42 | 35805.575 | 39423.588 | 0 | 365.924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168645.267 | 0 | 0
May | 463693000000 | 322592.306 | 31-MAY-17:10 | 41924.28 | 31827.177 | 39423.588 | 0 | 9118.414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200298.847 | 0 | 0
June | 498496000000 | 371365.958 | 14-JUN-17:10 | 41924.28 | 31827.177 | 39423.588 | 0 | 20188.732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 238002.18 | 0 | 0
July | 562233000000 | 398347.814 | 06-JUL-17:10 | 41924.28 | 31827.177 | 39423.588 | 0 | 44798.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240374.529 | 0 | 0
August | 546814000000 | 379025.724 | 11-AUG-17:10 | 41924.28 | 31827.177 | 39423.588 | 0 | 27433.543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 238417.135 | 0 | 0
September | 479077000000 | 349127.141 | 08-SEP-17:10 | 41924.28 | 31827.177 | 39423.588 | 0 | 8785.067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227167.029 | 0 | 0
October | 452127000000 | 317895.534 | 07-OCT-17:10 | 34936.9 | 27848.78 | 39423.588 | 0 | 5676.196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210010.069 | 0 | 0
November | 433764000000 | 317161.329 | 09-NOV-11:20 | 62886.42 | 35805.575 | 39423.588 | 0 | 1387.252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177658.494 | 0 | 0
December | 447659000000 | 297493.665 | 02-DEC-11:20 | 62886.42 | 35805.575 | 39423.588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159378.082 | 0 | 0
Annual Sum or Average | 5612450000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 404948000000 | 293439.633 |  | 34936.9 | 27848.78 | 39423.588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155324.05 | 0 | 0
Maximum of Months | 562233000000 | 398347.814 |  | 62886.42 | 35805.575 | 39423.588 | 0 | 44798.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240374.529 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 84116.37 | 45701.97 | 0 | 129818.34
Cost per Total Building Area ($/m2) | 20.12 | 10.93 | 0 | 31.05
Cost per Net Conditioned Building Area ($/m2) | 20.12 | 10.93 | 0 | 31.05

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 14068.25 | 3364.97 | 3364.97
Net Site Energy | 14068.25 | 3364.97 | 3364.97
Total Source Energy | 29150.26 | 6972.42 | 6972.42
Net Source Energy | 29150.26 | 6972.42 | 6972.42
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 8185.99 | 0 | 0 | 0 | 0
Cooling | 17.02 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 67.51 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 678.54 | 294.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1038.4 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 27.77 | 0 | 0 | 0 | 87.12
Refrigeration | 2824.33 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5559.57 | 8508.68 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 11.84 | 18.59 | 8.07
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 8.61 | 27.86 | 8.07
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 18.29 | 11.61 | 80.7
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 18.29 | 11.61 | 5.38
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 18.29 | 11.61 | 5.38
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 18.29 | 11.61 | 80.7
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.6518
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 16.713 | 12.83 | 13.6518
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
OFFICE_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 60.34 | 0 | 90 | N
OFFICE_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 54.71 | 90 | 90 | E
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 88.84 | 0 | 180
OFFICE_CEILING | ROOFS | 0.3 | 0.273 | 0.29 | 88.84 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOFS | 0.3 | 0.273 | 0.29 | 621.89 | 180 | 0
DELI_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 224.72 | 0 | 180
DELI_CEILING | ROOFS | 0.3 | 0.273 | 0.29 | 224.72 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 2324.94 | 0 | 180
SALES_CEILING | ROOFS | 0.3 | 0.273 | 0.29 | 2324.94 | 180 | 0
PRODUCE_WALL_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 267.12 | 270 | 90 | W
PRODUCE_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 98.96 | 180 | 90 | S
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOFS | 0.3 | 0.273 | 0.29 | 711.36 | 180 | 0
BAKERY_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS | 0.08 | 0.454 | 0.49 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 209.04 | 0 | 180
BAKERY_CEILING | ROOFS | 0.3 | 0.273 | 0.29 | 209.04 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 174.7 | 174.7 | 2.58 | 0.504 | 0.49 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 2.58 | 0.504 | 0.49
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 2.58 | 0.504 | 0.49
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12869.73 | 10278.48 | 2591.25 | 0.8 | 4.04
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 70564.52 | 56356.73 | 14207.8 | 0.8 | 4.18
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 28428.96 | 22704.94 | 5724.02 | 0.8 | 3.75
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 214071.29 | 170969.16 | 43102.13 | 0.8 | 3.94
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 72803.45 | 58144.86 | 14658.59 | 0.8 | 4.18
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 27834.35 | 22230.05 | 5604.3 | 0.8 | 3.74
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 5706.45 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 99586.26 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 37207.37 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 351587.53 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 110608.86 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 23406.7 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.35 | 125 | 1.18 | 421.39 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.78 | 885.68 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 4.26 | 7996.97 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.72 | 1878.19 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 12.93 | 21769.31 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 4.4 | 8250.71 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.68 | 1838.9 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.8 | 1.71 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 163875.8659 | 179.9709 | 653.4346 | 0 | 0.0024 | 131073.2147 | 61520.4636
February | 145091.8299 | 159.9015 | 590.2408 | 0 | 0.0021 | 118400.1304 | 54554.8671
March | 142809.7436 | 160.7847 | 652.0521 | 0 | 0.0023 | 130817.3089 | 54219.7407
April | 116871.2591 | 135.2195 | 609.7317 | 0 | 0.0021 | 122344.0382 | 44931.6713
May | 104973.5793 | 126.0036 | 642.8436 | 0 | 0.0022 | 129006.856 | 41057.684
June | 103741.3254 | 127.1302 | 689.8135 | 0 | 0.0023 | 138442.0594 | 40976.7166
July | 109487.2158 | 135.0088 | 745.5354 | 0 | 0.0025 | 149627.8644 | 43375.1169
August | 109667.8538 | 133.9442 | 719.8326 | 0 | 0.0025 | 144465.2778 | 43248.574
September | 106808.3351 | 127.3096 | 635.3287 | 0 | 0.0022 | 127495.5919 | 41637.3791
October | 124604.5985 | 143.6358 | 638.9657 | 0 | 0.0022 | 128207.7089 | 47823.0545
November | 145137.0636 | 161.8853 | 630.8863 | 0 | 0.0023 | 126563.7438 | 54869.4921
December | 158797.1942 | 175.4289 | 654.8466 | 0 | 0.0024 | 131362.0679 | 59773.2255
Annual Sum or Average | 1531870 | 1766.2229 | 7863.5118 | 0 | 0.0275 | 1577810 | 587987.9854
Minimum of Months | 103741.3254 | 126.0036 | 590.2408 | 0 | 0.0021 | 118400.1304 | 40976.7166
Maximum of Months | 163875.8659 | 179.9709 | 745.5354 | 0 | 0.0025 | 149627.8644 | 61520.4636
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 461851000000 | 300846.149 | 03-JAN-11:09 | 62886.42 | 35805.575 | 43041.154 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 154782.852 | 0 | 0
February | 417196000000 | 296908.391 | 27-FEB-11:20 | 62886.42 | 35805.575 | 43041.154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155175.242 | 0 | 0
March | 460949000000 | 300264.382 | 09-MAR-11:20 | 62886.42 | 35805.575 | 43041.154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158531.233 | 0 | 0
April | 431092000000 | 299626.497 | 14-APR-10:20 | 62886.42 | 35805.575 | 43041.154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157893.348 | 0 | 0
May | 454570000000 | 320379.138 | 30-MAY-17:10 | 41924.28 | 31827.177 | 43041.154 | 0 | 5104.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198482.226 | 0 | 0
June | 487816000000 | 346216.623 | 21-JUN-17:10 | 41924.28 | 31827.177 | 43041.154 | 0 | 10561.509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218862.503 | 0 | 0
July | 527230000000 | 346177.597 | 11-JUL-17:10 | 41924.28 | 31827.177 | 43041.154 | 0 | 11583.765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 217801.221 | 0 | 0
August | 509039000000 | 344534.239 | 15-AUG-17:10 | 41924.28 | 31827.177 | 43041.154 | 0 | 11598.539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216143.088 | 0 | 0
September | 449245000000 | 314747.896 | 01-SEP-17:10 | 41924.28 | 31827.177 | 43041.154 | 0 | 1579.079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196376.206 | 0 | 0
October | 451754000000 | 306398.761 | 02-OCT-10:20 | 62886.42 | 35805.575 | 43041.154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164665.613 | 0 | 0
November | 445961000000 | 297470.38 | 14-NOV-18:10 | 41924.28 | 31827.177 | 43041.154 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 176347.621 | 0 | 0
December | 462868000000 | 301652.943 | 18-DEC-11:09 | 62886.42 | 35805.575 | 43041.154 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 155589.647 | 0 | 0
Annual Sum or Average | 5559570000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 417196000000 | 296908.391 |  | 41924.28 | 31827.177 | 43041.154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154782.852 | 0 | 0
Maximum of Months | 527230000000 | 346216.623 |  | 62886.42 | 35805.575 | 43041.154 | 0 | 11598.539 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 218862.503 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 137561.62 | 35294.79 | 0 | 172856.42
Cost per Total Building Area ($/m2) | 32.9 | 8.44 | 0 | 41.35
Cost per Net Conditioned Building Area ($/m2) | 32.9 | 8.44 | 0 | 41.35

## Picture
DOE Commercial Building Benchmark - Super Market
Sales
Bakery
Deli
Produce
Office
DryStorage

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 112 | 5840
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 112 | 5840
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | 11.3 | 72.2 | 3764.71
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | 9.9
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 5.8
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0 | 0 | 7.6 | 49 | 2555
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | 7.6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 3.4
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | 13.9 | 91.6 | 4776.29
|  |  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15 | 12.3
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.15 | 0.15 | 9.8
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.22 | 0.64 | 0.74 | 0.68 | 0.68 | 0.71 | 0.72 | 0.72 | 0.73 | 0.68 | 0.68 | 0.58 | 0.54 | 0 | 0 | 0 | 8.44 | 52.69 | 2747.41
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.21 | 0.56 | 0.66 | 0.68 | 0.68 | 0.69 | 0.7 | 0.69 | 0.66 | 0.58 | 0.47 | 0.43 | 0.43 | 0.08 | 0 | 0 | 7.61
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.13 | 0.35 | 0.37 | 0.37 | 0.39 | 0.41 | 0.38 | 0.34 | 0.03 | 0 | 0 | 0 | 0 | 0 | 2.88
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0.23 | 0.13 | 0.08 | 6.62 | 44.59 | 2325.05
|  |  | Sat, WinterDesign | 0.11 | 0.1 | 0.08 | 0.06 | 0.06 | 0.06 | 0.07 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0.16 | 0.13 | 6.9
|  |  | Sun, Hol, Other | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07 | 0.1 | 0.12 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.1 | 0.06 | 4.59
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
INFIL_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8 | 56 | 2920
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16 | 115.5 | 6022.5
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19.5
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | WD, WinterDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8 | 3225.6 | 168192
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8
|  |  | Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624 | 4368 | 227760
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 112 | 5840
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
Deli Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Deli Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Deli Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Deli Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Deli_Case:1_ MULTIDECKDIARYANDDELICASE_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Deli_Case:1_ MULTIDECKDIARYANDDELICASE_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Deli_Case:1_ MULTIDECKDIARYANDDELICASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 595 | 31025
Deli_Case:1_ MULTIDECKDIARYANDDELICASE_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2 | 10.4 | 72.8 | 3796
Deli_Case:2_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Deli_Case:2_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Deli_Case:2_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Deli_Case:2_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Sales_Case:1_MEATDISPLAYCASE_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Sales_Case:1_MEATDISPLAYCASE_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Sales_Case:1_MEATDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 595 | 31025
Sales_Case:2_ MULTIDECKDIARYANDDELICASE_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Sales_Case:2_ MULTIDECKDIARYANDDELICASE_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Sales_Case:2_ MULTIDECKDIARYANDDELICASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 595 | 31025
Sales_Case:2_ MULTIDECKDIARYANDDELICASE_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2 | 10.4 | 72.8 | 3796
Sales_Case:3_GLASSDOORFROZENFOOD_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57 | 3.97 | 206.83
Sales_Case:3_GLASSDOORFROZENFOOD_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73 | 5.13 | 267.67
Sales_Case:3_GLASSDOORFROZENFOOD_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 595 | 31025
Sales_Case:3_GLASSDOORFROZENFOOD_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2 | 10.4 | 72.8 | 3796
Sales_Case:4_OPENWELLICECREAMDISPLAYCASE_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Sales_Case:4_OPENWELLICECREAMDISPLAYCASE_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Sales_Case:4_OPENWELLICECREAMDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 595 | 31025
Sales_Case:4_OPENWELLICECREAMDISPLAYCASE_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2 | 10.4 | 72.8 | 3796
Sales_Case:5_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Sales_Case:5_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Sales_Case:5_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Sales_Case:5_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Sales_Case:6_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Sales_Case:6_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Sales_Case:6_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Sales_Case:6_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Sales_Case:7_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Sales_Case:7_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Sales_Case:7_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Sales_Case:7_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Produce_Case:1_ MULTIDECKDIARYANDDELICASE_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Produce_Case:1_ MULTIDECKDIARYANDDELICASE_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Produce_Case:1_ MULTIDECKDIARYANDDELICASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 595 | 31025
Produce_Case:1_ MULTIDECKDIARYANDDELICASE_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2 | 10.4 | 72.8 | 3796
Bakery Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Bakery Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Bakery Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Bakery Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Bakery_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Bakery_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Bakery_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Bakery_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720