## BuildingSummary
Building Summary Warehouse new construction version 1.1_3.1
|  | Value | Data Source
Program
| Building Name | Warehouse
| Available Fuel Types | gas, electricity
| Principal Building Activity | Nonrefrigerated warehouse
Form
| Total Floor Area (m2) | 4835.13 | Liu, B, R.E. Jarnagin, W. Jiang, and K. Gowri. (2007). Technical Support Document: The Development of the Advanced Energy Design Guide for Small Warehouse and Self-Storage Buildings. PNNL-17056. Richland, WA: Pacific Northwest National Laboratory
| Building Shape | Rectangle
| Aspect Ratio | 0.45
| Number of Floors | 1
Window Fraction (Window to Wall Ratio)
| South | 0.0286
| East | 0
| North | 0
| West | 0.0076
| Total | 0.0058
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | Bulk storage, fine storage, office
| Floor to Ceiling Height (m) | 8.53
| Floor to Floor Height (m) | 8.53
| Roof type | Metal building roof | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Metal building wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1977.67
| Net Dimensions - Total Area (m2) | 1324.84
| Wall to Skin Ratio | 0.35192
Roof
| Construction Type | Metal building roof | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 4598.25
| Net Dimensions - Total Area (m2) | 4598.25
| Roof to Skin Ratio | 0.64808
Window Dimensions (m2)
| South | 11.15
| East | 0
| North | 0
| West | 6.51
| Total Area (m2) | 17.66
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 8in slab-on-grade
| Dimensions - Total Area (m2) | 4598.25
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 539.71
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 9670.26
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.21 | See Benchmark Technical Report
HVAC
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | PACU | 2003 CBECS
| Fan Control | SZ CAV | 2003 CBECS
Service Water Heating
| SWH Type | n/a
| Fuel | n/a
| Thermal Efficiency (%) | n/a
| Temperature Setpoint (ºC ) | n/a
| Water Consumption (m3 ) | n/a

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Office | Yes | 1 | 236.88 | 1010.76 | 4.267 | 149.56 | 17.66 | 47.376 | 5 | 11.836 | 8.074 | 0 | 0 | 2.5 | 0.3 | 83.564 | 0 | 0.16104
FineStorage | Yes | 1 | 1393.41 | 10880.57 | 8.534 | 760.8 | 0 | 0 | 0 | 15.064 | 0 | 0 | 0 | 0 | 0.3 | 418.023 | 0 | 0.21548
BulkStorage | Yes | 1 | 3204.84 | 27350.07 | 8.534 | 1586.63 | 0 | 0 | 0 | 9.684 | 2.559 | 0 | 0 | 0 | 0.3 | 961.452 | 0 | 0.19067
Total Conditioned Zones |  |  | 4835.13 | 39241.4 |  | 2496.99 | 17.66 |  | 5
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report
[5] Liu, B, R.E. Jarnagin, W. Jiang, and K. Gowri. (2007). Technical Support Document: The Development of the Advanced Energy Design Guide for Small Warehouse and Self-Storage Buildings. PNNL-17056. Richland, WA: Pacific Northwest National Laboratory

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7A | 8A
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fabric
Exterior walls
| Construction Type | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall
| R-value (m2·K / W) | 1.5601 | 1.5601 | 1.5601 | 1.5601 | 1.5601 | 1.5601 | 1.5601 | 1.5601 | 1.5601 | 1.5601 | 1.5601 | 1.5601 | 1.5601 | 1.5601 | 3.0864 | 3.0864
Roof
| Construction Type | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof
| R-value (m2·K / W) | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 3.5971
Window
| U-Factor (W / m2·K) | 6.49 | 6.49 | 6.49 | 3.18 | 3.18 | 3.18 | 6.49 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 2.58
| SHGC | 0.25 | 0.25 | 0.25 | 0.402 | 0.402 | 0.402 | 0.61 | 0.402 | 0.402 | 0.402 | 0.501 | 0.501 | 0.501 | 0.501 | 0.501 | 0.504
| Visible transmittance | 0.25 | 0.25 | 0.25 | 0.495 | 0.495 | 0.495 | 0.61 | 0.495 | 0.495 | 0.495 | 0.622 | 0.622 | 0.622 | 0.622 | 0.49 | 0.49
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade
| R-value (m2·K / W) | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809
HVAC
HVAC Sizing
Air Conditioning (kW)
| FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | 18.9967 | 17.4095 | 15.2573 | 16.3302 | 11.4439 | 14.0643 | 9.1867 | 15.6032 | 13.4992 | 9.6228 | 13.1667 | 12.7563 | 12.8775 | 14.4112 | 11.0546 | 13.2078
| FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | 68.0943 | 71.3484 | 70.7645 | 61.1601 | 25.7046 | 60.9918 | 17.5762 | 57.1694 | 45.3174 | 27.8713 | 77.9041 | 57.7137 | 88.8213 | 72.6565 | 89.6706 | 128.8913
Heating (kW)
| BULKSTORAGE UNIT HEATER COIL | 39.3476 | 39.2032 | 37.8007 | 37.9092 | 39.2079 | 36.3558 | 39.3336 | 39.1382 | 32.3667 | 38.791 | 71.651 | 47.3298 | 114.7125 | 110.5176 | 119.32 | 154.4094
| FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | 5.8159 | 11.1556 | 9.84 | 12.6569 | 7.6264 | 11.2739 | 9.4513 | 14.2973 | 13.226 | 11.851 | 17.9608 | 16.5124 | 20.0603 | 19.8889 | 17.459 | 21.8284
| FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | 13.4868 | 44.3665 | 30.6797 | 62.114 | 16.1805 | 46.4056 | 28.3228 | 77.0975 | 65.4292 | 53.9326 | 111.4072 | 96.6671 | 130.878 | 128.4829 | 131.5003 | 175.476
HVAC Efficiency
Air Conditioning (COP)
| FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | 3.76 | 3.81 | 4.04 | 3.84 | 4.05 | 4.03 | 4.04 | 3.81 | 4.04 | 4.05 | 3.99 | 4.03 | 4.04 | 4.03 | 4.06 | 4.04
| FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | 3.2 | 3.15 | 3.99 | 3.25 | 3.73 | 4.33 | 4.03 | 3.23 | 3.47 | 3.67 | 3.14 | 3.47 | 3.63 | 4.18 | 3.64 | 3.51
Heating Efficiency (%)
| BULKSTORAGE UNIT HEATER COIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78 | 0.8 | 0.8 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
HVAC Control - Economizer
| FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| BULKSTORAGE UNIT HEATERFAN | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 1.14 | 0.8 | 2.12 | 2.32 | 2.23 | 2.68
| FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | 0.88 | 0.85 | 0.92 | 0.82 | 0.69 | 0.85 | 0.55 | 0.77 | 0.82 | 0.58 | 0.77 | 0.77 | 0.78 | 0.87 | 0.67 | 0.8
| FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | 2.76 | 3.09 | 3.86 | 2.75 | 1.53 | 3.63 | 1.06 | 2.5 | 2.74 | 1.56 | 3.33 | 3.49 | 3.96 | 4.39 | 4.04 | 5.19
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.091926 | 0.12079 | 0.11289 | 0.10414 | 0.13544 | 0.10328 | 0.15154 | 0.081451 | 0.037834 | 0.077494 | 0.053717 | 0.037836 | 0.065482 | 0.080944 | 0.064225 | 0.10661
| Total Cost ($/m2) | 4.26 | 5.52 | 5.31 | 4.61 | 5.85 | 4.75 | 6.53 | 3.6 | 1.66 | 3.35 | 2.37 | 1.66 | 2.94 | 3.61 | 2.88 | 4.94
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.0115 | 0.0080607 | 0.0080702 | 0.009345 | 0.0086678 | 0.0075518 | 0.0088122 | 0.0096304 | 0.0068114 | 0.008478 | 0.0082182 | 0.0068385 | 0.0079253 | 0.0079091 | 0.0078931 | 0.0041056
| Total Cost ($/m2) | 0 | 0.06 | 0.04 | 0.2 | 0.01 | 0.09 | 0.06 | 0.47 | 0.25 | 0.24 | 0.65 | 0.44 | 1.03 | 0.82 | 1.15 | 1.3
Total Utility Costs
| Cost Intensity ($/m2) | 4.26 | 5.58 | 5.35 | 4.81 | 5.86 | 4.84 | 6.59 | 4.07 | 1.91 | 3.59 | 3.02 | 2.1 | 3.97 | 4.43 | 4.03 | 6.24
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 13825 | 10747.2222 | 13455.5556 | 4294.4444 | 688.8889 | 8675 | 102.7778 | 3425 | 2236.1111 | 119.4444 | 1930.5556 | 955.5556 | 1183.3333 | 386.1111 | 175 | 22.2222
| Interior Lighting | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778
| Exterior Lighting | 26769.4444 | 26761.1111 | 26755.5556 | 26750 | 26730.5556 | 26725 | 26738.8889 | 26722.2222 | 26733.3333 | 26680.5556 | 26727.7778 | 26711.1111 | 26708.3333 | 26702.7778 | 26688.8889 | 26525
| Interior Equipment | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 3055.5556 | 3161.1111 | 6791.6667 | 2736.1111 | 1086.1111 | 6402.7778 | 1141.6667 | 3319.4444 | 3258.3333 | 1936.1111 | 4191.6667 | 3963.8889 | 8861.1111 | 8044.4444 | 9752.7778 | 17141.6667
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 224061.1111 | 221077.7778 | 227411.1111 | 214194.4444 | 208916.6667 | 222213.8889 | 208394.4444 | 213877.7778 | 212636.1111 | 209147.2222 | 213261.1111 | 212041.6667 | 217166.6667 | 215541.6667 | 217025 | 224100
Gas (MJ)
| Heating | 200 | 34900 | 21660 | 102260 | 5930 | 59730 | 31890 | 234870 | 177550 | 135620 | 384800 | 309080 | 626090 | 502850 | 704790 | 1529160
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 200 | 34900 | 21660 | 102260 | 5930 | 59730 | 31890 | 234870 | 177550 | 135620 | 384800 | 309080 | 626090 | 502850 | 704790 | 1529160
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 806820 | 830790 | 840340 | 873360 | 758030 | 859710 | 782110 | 1004830 | 943040 | 888540 | 1152530 | 1072430 | 1407880 | 1278800 | 1486080 | 2335920
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 10.2934 | 8.0019 | 10.0183 | 3.1974 | 0.51291 | 6.459 | 0.076523 | 2.5501 | 1.6649 | 0.088932 | 1.4374 | 0.71146 | 0.88105 | 0.28748 | 0.1303 | 0.016546
| Interior Lighting (elec) | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271
| Exterior Lighting (elec) | 19.9312 | 19.925 | 19.9209 | 19.9167 | 19.9023 | 19.8981 | 19.9085 | 19.8961 | 19.9043 | 19.865 | 19.9002 | 19.8878 | 19.8857 | 19.8816 | 19.8712 | 19.7492
| Interior Equipment (elec) | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 2.275 | 2.3536 | 5.0567 | 2.0372 | 0.80866 | 4.7672 | 0.85003 | 2.4715 | 2.426 | 1.4415 | 3.1209 | 2.9513 | 6.5975 | 5.9895 | 7.2614 | 12.7628
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 166.8249 | 164.6036 | 169.3191 | 159.4786 | 155.5491 | 165.4495 | 155.1603 | 159.2429 | 158.3184 | 155.7207 | 158.7837 | 157.8758 | 161.6916 | 160.4817 | 161.5861 | 166.8538
Gas (MJ/m2)
| Heating (gas) | 0.041364 | 7.218 | 4.4797 | 21.1494 | 1.2264 | 12.3533 | 6.5955 | 48.5757 | 36.7208 | 28.0489 | 79.5842 | 63.9238 | 129.4877 | 103.9993 | 145.7644 | 316.2604
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0.041364 | 7.218 | 4.4797 | 21.1494 | 1.2264 | 12.3533 | 6.5955 | 48.5757 | 36.7208 | 28.0489 | 79.5842 | 63.9238 | 129.4877 | 103.9993 | 145.7644 | 316.2604
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 166.8662 | 171.8237 | 173.7988 | 180.628 | 156.7755 | 177.8049 | 161.7557 | 207.8186 | 195.0392 | 183.7676 | 238.3659 | 221.7996 | 291.1773 | 264.481 | 307.3506 | 483.1142
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 62.9146 | 62.0792 | 60.504 | 60.5855 | 64.6402 | 64.8836 | 64.7399 | 65.1939 | 60.4343 | 64.9572 | 66.7889 | 66.3349 | 69.7734 | 68.7959 | 69.2818 | 73.6268
| Feb | 66.5288 | 60.0337 | 60.2053 | 61.1945 | 59.11 | 59.1073 | 58.9256 | 60.4773 | 59.9299 | 59.2993 | 65.334 | 61.2802 | 63.9755 | 64.4419 | 64.9139 | 73.3385
| Mar | 68.7013 | 59.7891 | 64.0862 | 59.3435 | 59.3061 | 59.2209 | 58.8072 | 59.7007 | 59.8071 | 59.2684 | 59.8223 | 60.3391 | 61.5841 | 61.9351 | 63.1064 | 65.4194
| Apr | 72.8827 | 67.0572 | 69.1527 | 60.0504 | 59.4354 | 67.1439 | 59.127 | 59.1659 | 59.3074 | 58.9835 | 58.9686 | 59.5541 | 59.6777 | 60.3595 | 61.4141 | 62.1835
| May | 78.3913 | 79.1615 | 79.2045 | 69.8775 | 59.5234 | 75.2932 | 59.1181 | 60.0034 | 64.5763 | 59.2012 | 59.9243 | 59.6596 | 59.9121 | 59.0468 | 59.4947 | 58.8744
| Jun | 81.7684 | 80.1499 | 90.2669 | 76.0238 | 59.6395 | 84.9928 | 59.3796 | 77.359 | 73.8848 | 59.6243 | 74.6515 | 67.7181 | 75.0182 | 69.1673 | 59.711 | 59.2357
| Jul | 79.3998 | 82.1792 | 88.6112 | 82.7584 | 63.3397 | 84.4495 | 61.0263 | 81.2454 | 74.4401 | 62.8963 | 78.6686 | 73.4617 | 72.0741 | 70.5675 | 67.9253 | 59.3367
| Aug | 80.2171 | 81.692 | 90.0881 | 75.8764 | 65.7158 | 83.2438 | 59.4078 | 80.0165 | 74.4038 | 60.9356 | 76.2775 | 72.4228 | 72.5849 | 65.5313 | 61.4123 | 59.1411
| Sep | 77.2686 | 78.2378 | 81.5807 | 71.4677 | 64.9029 | 82.0546 | 63.6994 | 68.8253 | 64.6003 | 59.8613 | 64.8812 | 63.212 | 60.3389 | 59.6564 | 59.2681 | 60.0633
| Oct | 75.0653 | 70.3736 | 69.0866 | 60.1347 | 65.3177 | 65.904 | 59.3607 | 60.1286 | 59.466 | 64.7491 | 65.1032 | 64.7401 | 64.7938 | 59.972 | 65.3268 | 68.6373
| Nov | 69.163 | 60.2378 | 59.9263 | 59.389 | 65.0954 | 64.6928 | 64.6785 | 64.7901 | 64.7222 | 65.1203 | 65.0727 | 65.3803 | 67.0235 | 65.9768 | 67.7589 | 69.8912
| Dec | 64.5662 | 59.8038 | 60.8699 | 60.6864 | 64.9492 | 64.7856 | 64.7164 | 65.4892 | 65.4194 | 65.2232 | 65.8188 | 66.9181 | 67.8553 | 69.2922 | 68.0506 | 72.7266
Time of Peak Electrical Demand
| Jan | 25-JAN-15:39 | 11-JAN-09:09 | 20-JAN-09:09 | 02-JAN-09:09 | 02-JAN-16:00 | 10-JAN-16:00 | 02-JAN-16:00 | 10-JAN-16:00 | 04-JAN-09:09 | 02-JAN-16:00 | 27-JAN-16:00 | 05-JAN-16:00 | 04-JAN-16:00 | 06-JAN-16:00 | 09-JAN-16:00 | 13-JAN-09:09
| Feb | 23-FEB-13:00 | 17-FEB-09:09 | 23-FEB-09:09 | 10-FEB-09:09 | 13-FEB-15:09 | 03-FEB-09:09 | 15-FEB-15:00 | 08-FEB-09:09 | 06-FEB-09:09 | 15-FEB-09:09 | 01-FEB-16:00 | 15-FEB-09:09 | 03-FEB-09:09 | 27-FEB-09:09 | 01-FEB-09:09 | 03-FEB-09:09
| Mar | 13-MAR-15:00 | 28-MAR-14:00 | 17-MAR-15:00 | 13-MAR-08:09 | 31-MAR-14:00 | 03-MAR-09:09 | 16-MAR-08:09 | 31-MAR-08:09 | 29-MAR-08:09 | 20-MAR-08:09 | 03-MAR-09:09 | 02-MAR-09:09 | 13-MAR-08:09 | 03-MAR-09:09 | 07-MAR-09:09 | 14-MAR-08:09
| Apr | 03-APR-15:39 | 21-APR-14:00 | 28-APR-15:00 | 14-APR-15:00 | 11-APR-15:00 | 21-APR-15:00 | 13-APR-14:00 | 05-APR-15:00 | 21-APR-15:00 | 11-APR-08:09 | 21-APR-08:09 | 04-APR-08:09 | 04-APR-08:09 | 04-APR-08:09 | 03-APR-08:09 | 10-APR-08:09
| May | 24-MAY-14:00 | 18-MAY-15:50 | 30-MAY-15:00 | 15-MAY-15:39 | 30-MAY-14:00 | 31-MAY-15:00 | 17-MAY-14:39 | 15-MAY-14:00 | 31-MAY-15:00 | 04-MAY-14:00 | 05-MAY-13:00 | 23-MAY-15:00 | 15-MAY-14:00 | 12-MAY-08:09 | 01-MAY-08:09 | 01-MAY-08:09
| Jun | 28-JUN-14:00 | 13-JUN-15:00 | 28-JUN-15:00 | 19-JUN-15:30 | 30-JUN-14:00 | 27-JUN-15:00 | 16-JUN-14:00 | 30-JUN-15:00 | 29-JUN-15:00 | 28-JUN-14:00 | 08-JUN-12:00 | 28-JUN-13:00 | 30-JUN-15:30 | 30-JUN-14:00 | 14-JUN-14:00 | 21-JUN-15:00
| Jul | 13-JUL-15:00 | 05-JUL-15:00 | 19-JUL-15:00 | 03-JUL-15:00 | 10-JUL-15:00 | 24-JUL-15:00 | 03-JUL-14:00 | 25-JUL-13:39 | 03-JUL-15:00 | 24-JUL-15:39 | 03-JUL-14:00 | 17-JUL-15:00 | 13-JUL-15:00 | 21-JUL-15:00 | 06-JUL-15:00 | 12-JUL-15:00
| Aug | 21-AUG-15:30 | 31-AUG-13:00 | 01-AUG-15:00 | 17-AUG-13:00 | 08-AUG-15:09 | 04-AUG-15:00 | 15-AUG-13:30 | 04-AUG-15:30 | 01-AUG-15:50 | 07-AUG-15:00 | 04-AUG-15:00 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-15:00 | 14-AUG-15:30 | 15-AUG-14:50
| Sep | 11-SEP-14:00 | 15-SEP-14:00 | 08-SEP-15:00 | 11-SEP-13:00 | 25-SEP-13:39 | 01-SEP-14:00 | 28-SEP-15:00 | 08-SEP-15:00 | 14-SEP-15:00 | 01-SEP-15:00 | 05-SEP-14:00 | 01-SEP-15:00 | 14-SEP-14:00 | 01-SEP-15:00 | 07-SEP-14:00 | 29-SEP-08:09
| Oct | 06-OCT-14:00 | 06-OCT-15:00 | 02-OCT-15:00 | 02-OCT-14:00 | 31-OCT-16:00 | 04-OCT-14:00 | 13-OCT-14:00 | 03-OCT-14:00 | 13-OCT-14:00 | 30-OCT-16:00 | 31-OCT-16:49 | 30-OCT-16:00 | 31-OCT-16:00 | 16-OCT-08:09 | 31-OCT-16:00 | 27-OCT-08:09
| Nov | 01-NOV-14:20 | 03-NOV-14:39 | 13-NOV-15:00 | 15-NOV-09:09 | 20-NOV-16:49 | 09-NOV-16:40 | 22-NOV-16:00 | 20-NOV-16:00 | 20-NOV-16:00 | 29-NOV-16:00 | 27-NOV-16:00 | 17-NOV-16:00 | 27-NOV-16:00 | 29-NOV-16:00 | 24-NOV-16:00 | 09-NOV-09:09
| Dec | 13-DEC-15:50 | 19-DEC-15:30 | 26-DEC-09:09 | 22-DEC-09:09 | 19-DEC-16:49 | 26-DEC-16:00 | 27-DEC-16:00 | 20-DEC-16:00 | 28-DEC-16:00 | 13-DEC-16:19 | 14-DEC-16:00 | 01-DEC-16:00 | 29-DEC-16:00 | 11-DEC-16:00 | 20-DEC-16:00 | 29-DEC-09:09
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emissions
| Carbon Equivalent (kg) | 61452.1755 | 74372.6204 | 69040.3495 | 67823.386 | 24522.1246 | 76024.4642 | 24929.3106 | 61951.6735 | 90063.5045 | 17678.4848 | 120638.7173 | 92191.9982 | 85624.209 | 87835.0155 | 86995.7627 | 90633.8049
| CO2 (kg) | 142297.8944 | 186861.3358 | 162572.0193 | 155074.4973 | 65493.3786 | 180625.7375 | 66683.2097 | 141667.5022 | 211646.784 | 43251.2018 | 282384.1613 | 217932.4674 | 203988.6151 | 209400.9205 | 207979.1286 | 237632.8301
| NOX (kg) | 250.9484 | 244.8729 | 273.8903 | 293.9977 | 56.0637 | 293.9349 | 57.1524 | 269.8942 | 363.5104 | 64.5555 | 495.8878 | 368.7369 | 342.332 | 348.9865 | 345.8541 | 270.2275
| SO2 (kg) | 959.069 | 1054.5547 | 914.4703 | 751.8456 | 607.9253 | 1222.3717 | 606.4122 | 780.8068 | 928.5907 | 161.6894 | 1437.3099 | 926.0246 | 512.7128 | 575.6585 | 512.4052 | 1141.1696
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0044 | 0.003 | 0.0025 | 0.0028 | 0.0003 | 0.0023 | 0.0003 | 0.0032 | 0.0036 | 0.0006 | 0.0044 | 0.0036 | 0.0038 | 0.004 | 0.0038 | 0.004
| Water for Electricity (m3) | 118.6979 | 359.7209 | 6755.1 | 1337.34 | 3668.12 | 6096.22 | 3658.94 | 48.5586 | 965.5417 | 2136.8 | 330.8613 | 962.8367 | 336.9191 | 13653.3 | 336.703 | 228.9587

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 806.82 | 166.87 | 166.87
Net Site Energy | 806.82 | 166.87 | 166.87
Total Source Energy | 2675.77 | 553.4 | 553.4
Net Source Energy | 2675.77 | 553.4 | 553.4
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 0.2 | 0 | 0 | 0 | 0
Cooling | 49.77 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 545.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 96.37 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 11 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 806.62 | 0.2 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 11.8401 | 47.39 | 8.07
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 15.06 |  | 0
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 9.68 |  | 2.56
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.37 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.37 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
OFFICE_WALL_SOUTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 180 | 90 | S
OFFICE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 0 | 90 | N
OFFICE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 236.88 | 0 | 180
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS | 0.8 | 0.641 | 0.71 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.3 | 3.242 | 6.3 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_WEST_1 | EXT-WALLS | 0.8 | 0.641 | 0.71 | 182.07 | 270 | 90 | W
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOFS | 0.3 | 0.369 | 0.4 | 1393.41 | 0 | 0
BULKSTORAGE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOFS | 0.3 | 0.369 | 0.4 | 3204.84 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW_SOUTH | 5.58 | 5.58 | 6.49 | 0.25 | 0.25 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW_SOUTH | 5.58 | 5.58 | 6.49 | 0.25 | 0.25 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW_WEST | 3.25 | 3.25 | 6.49 | 0.25 | 0.25 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW_WEST | 3.25 | 3.25 | 6.49 | 0.25 | 0.25 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 6.49 | 0.25 | 0.25
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 6.49 | 0.25 | 0.25
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18996.68 | 13564.26 | 5432.42 | 0.71 | 3.76
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 68094.29 | 46133.33 | 21960.95 | 0.68 | 3.2
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 39347.64 | 0.8
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 5815.87 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13486.79 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.88 | 1006.42 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.76 | 3016.13 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 11398.0069 | 20.0951 | 76.7755 | 0 | 0.0003 | 9502.0111 | 4921.7156
February | 10316.5447 | 18.1932 | 69.5289 | 0 | 0.0003 | 8605.1462 | 4455.2182
March | 11977.799 | 21.1231 | 80.7265 | 0 | 0.0004 | 9991.0063 | 5172.6533
April | 11131.3637 | 19.6313 | 75.0294 | 0 | 0.0003 | 9285.9173 | 4807.2145
May | 12386.5407 | 21.845 | 83.4898 | 0 | 0.0004 | 10333.0011 | 5349.2779
June | 12779.4555 | 22.5379 | 86.1382 | 0 | 0.0004 | 10660.7754 | 5518.9629
July | 12574.783 | 22.177 | 84.7586 | 0 | 0.0004 | 10490.0351 | 5430.5726
August | 13478.8659 | 23.7714 | 90.8524 | 0 | 0.0004 | 11244.2319 | 5821.0118
September | 11796.8914 | 20.8051 | 79.5153 | 0 | 0.0004 | 9841.1086 | 5094.6307
October | 11892.2498 | 20.9732 | 80.1581 | 0 | 0.0004 | 9920.6577 | 5135.8124
November | 11430.9625 | 20.1597 | 77.0488 | 0 | 0.0004 | 9535.8463 | 4936.5999
December | 11134.4315 | 19.6364 | 75.0475 | 0 | 0.0003 | 9288.1481 | 4808.5056
Annual Sum or Average | 142297.8944 | 250.9484 | 959.069 | 0 | 0.0044 | 118697.8851 | 61452.1755
Minimum of Months | 10316.5447 | 18.1932 | 69.5289 | 0 | 0.0003 | 8605.1462 | 4455.2182
Maximum of Months | 13478.8659 | 23.7714 | 90.8524 | 0 | 0.0004 | 11244.2319 | 5821.0118
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 64571400000 | 62914.6 | 25-JAN-15:39 | 49331.035 | 9104.406 | 788.156 | 0 | 3691.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 58476800000 | 66528.778 | 23-FEB-13:00 | 49331.035 | 9104.406 | 1261.527 | 0 | 6831.809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 67894400000 | 68701.335 | 13-MAR-15:00 | 49331.035 | 9104.406 | 1528.922 | 0 | 8736.971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 63103000000 | 72882.748 | 03-APR-15:39 | 49331.035 | 9104.406 | 2099.692 | 0 | 12347.614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 70218500000 | 78391.304 | 24-MAY-14:00 | 49331.035 | 9104.406 | 2716.257 | 0 | 17239.605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 72445900000 | 81768.419 | 28-JUN-14:00 | 49331.035 | 9104.406 | 3134.044 | 0 | 20198.933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 71285600000 | 79399.77 | 13-JUL-15:00 | 49331.035 | 9104.406 | 2910.754 | 0 | 18053.575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 76410800000 | 80217.145 | 21-AUG-15:30 | 49331.035 | 9104.406 | 2960.147 | 0 | 18821.557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 66875800000 | 77268.631 | 11-SEP-14:00 | 49331.035 | 9104.406 | 2628.46 | 0 | 16204.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 67416400000 | 75065.326 | 06-OCT-14:00 | 49331.035 | 9104.406 | 2379.391 | 0 | 14250.493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 64801400000 | 69163.003 | 01-NOV-14:20 | 49331.035 | 9104.406 | 1618.846 | 0 | 9108.715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 63118100000 | 64566.246 | 13-DEC-15:50 | 49331.035 | 9104.406 | 996.645 | 0 | 5134.159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 806618000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 58476800000 | 62914.6 |  | 49331.035 | 9104.406 | 788.156 | 0 | 3691.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 76410800000 | 81768.419 |  | 49331.035 | 9104.406 | 3134.044 | 0 | 20198.933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 20596.93 | 2.3 | 0 | 20599.22
Cost per Total Building Area ($/m2) | 4.26 | 0 | 0 | 4.26
Cost per Net Conditioned Building Area ($/m2) | 4.26 | 0 | 0 | 4.26

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 830.79 | 171.82 | 171.82
Net Site Energy | 830.79 | 171.82 | 171.82
Total Source Energy | 38.11 | 7.88 | 7.88
Net Source Energy | 38.11 | 7.88 | 7.88
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 34.9 | 0 | 0 | 0 | 0
Cooling | 38.69 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 545.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 96.34 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 11.38 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 795.88 | 34.9 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 11.8401 | 47.39 | 8.07
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 15.06 |  | 0
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 9.68 |  | 2.56
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.37 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.37 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
OFFICE_WALL_SOUTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 180 | 90 | S
OFFICE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 0 | 90 | N
OFFICE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 236.88 | 0 | 180
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS | 0.8 | 0.641 | 0.71 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.3 | 3.242 | 6.3 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_WEST_1 | EXT-WALLS | 0.8 | 0.641 | 0.71 | 182.07 | 270 | 90 | W
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOFS | 0.3 | 0.369 | 0.4 | 1393.41 | 0 | 0
BULKSTORAGE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOFS | 0.3 | 0.369 | 0.4 | 3204.84 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW_SOUTH | 5.58 | 5.58 | 6.49 | 0.25 | 0.25 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW_SOUTH | 5.58 | 5.58 | 6.49 | 0.25 | 0.25 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW_WEST | 3.25 | 3.25 | 6.49 | 0.25 | 0.25 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW_WEST | 3.25 | 3.25 | 6.49 | 0.25 | 0.25 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 6.49 | 0.25 | 0.25
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 6.49 | 0.25 | 0.25
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17409.46 | 12690.97 | 4718.49 | 0.73 | 3.81
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 71348.36 | 49547.04 | 21801.32 | 0.69 | 3.15
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 39203.23 | 0.8
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11155.59 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 44366.5 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.85 | 971.01 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 3.09 | 3377.54 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 15834.8778 | 20.5144 | 86.0522 | 0 | 0.0002 | 29352.395 | 6271.9518
February | 13954.4026 | 18.1603 | 76.9838 | 0 | 0.0002 | 26259.5223 | 5537.7149
March | 15574.7248 | 20.44 | 88.3166 | 0 | 0.0002 | 30125.9562 | 6202.7605
April | 14105.3845 | 18.5383 | 80.359 | 0 | 0.0002 | 27411.6153 | 5621.0283
May | 15763.7407 | 20.7199 | 89.8356 | 0 | 0.0003 | 30644.238 | 6282.153
June | 16811.6605 | 22.0974 | 95.8084 | 0 | 0.0003 | 32681.651 | 6699.7769
July | 16957.9595 | 22.2897 | 96.6421 | 0 | 0.0003 | 32966.0545 | 6758.08
August | 17723.1854 | 23.2955 | 101.0031 | 0 | 0.0003 | 34453.6438 | 7063.0375
September | 15144.4093 | 19.9059 | 86.3068 | 0 | 0.0002 | 29440.5362 | 6035.3446
October | 15048.5254 | 19.7791 | 85.7485 | 0 | 0.0002 | 29250.0747 | 5997.0234
November | 14725.7135 | 19.3451 | 83.7733 | 0 | 0.0002 | 28576.2479 | 5867.1289
December | 15216.752 | 19.7873 | 83.7252 | 0 | 0.0002 | 28558.9919 | 6036.6207
Annual Sum or Average | 186861.3358 | 244.8729 | 1054.5547 | 0 | 0.003 | 359720.9267 | 74372.6204
Minimum of Months | 13954.4026 | 18.1603 | 76.9838 | 0 | 0.0002 | 26259.5223 | 5537.7149
Maximum of Months | 17723.1854 | 23.2955 | 101.0031 | 0 | 0.0003 | 34453.6438 | 7063.0375
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 64942200000 | 62079.213 | 11-JAN-09:09 | 49331.035 | 9104.406 | 3643.771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 58099200000 | 60033.668 | 17-FEB-09:09 | 49331.035 | 9104.406 | 1598.226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 66653700000 | 59789.07 | 28-MAR-14:00 | 49331.035 | 9104.406 | 326.77 | 0 | 1026.858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 60648300000 | 67057.194 | 21-APR-14:00 | 49331.035 | 9104.406 | 1364.845 | 0 | 7256.907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 67800400000 | 79161.527 | 18-MAY-15:50 | 49331.035 | 9104.406 | 2961.867 | 0 | 17764.218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 72308200000 | 80149.861 | 13-JUN-15:00 | 49331.035 | 9104.406 | 3044.305 | 0 | 18670.115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 72937500000 | 82179.157 | 05-JUL-15:00 | 49331.035 | 9104.406 | 3316.202 | 0 | 20427.514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 76228800000 | 81691.978 | 31-AUG-13:00 | 49331.035 | 9104.406 | 3218.099 | 0 | 20038.437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 65137200000 | 78237.83 | 15-SEP-14:00 | 49331.035 | 9104.406 | 2848.943 | 0 | 16953.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 64715800000 | 70373.574 | 06-OCT-15:00 | 49331.035 | 9104.406 | 1794.86 | 0 | 10143.272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 63225000000 | 60237.833 | 03-NOV-14:39 | 49331.035 | 9104.406 | 409.004 | 0 | 1393.387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 63186800000 | 59803.777 | 19-DEC-15:30 | 49331.035 | 9104.406 | 324.99 | 0 | 1043.345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 795883000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 58099200000 | 59789.07 |  | 49331.035 | 9104.406 | 324.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 76228800000 | 82179.157 |  | 49331.035 | 9104.406 | 3643.771 | 0 | 20427.514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 26703.94 | 281.32 | 0 | 26985.26
Cost per Total Building Area ($/m2) | 5.52 | 0.06 | 0 | 5.58
Cost per Net Conditioned Building Area ($/m2) | 5.52 | 0.06 | 0 | 5.58

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 840.34 | 173.8 | 173.8
Net Site Energy | 840.34 | 173.8 | 173.8
Total Source Energy | 2613.14 | 540.45 | 540.45
Net Source Energy | 2613.14 | 540.45 | 540.45
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 21.66 | 0 | 0 | 0 | 0
Cooling | 48.44 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 545.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 96.32 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 24.45 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 818.68 | 21.66 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 11.8401 | 47.39 | 8.07
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 15.06 |  | 0
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 9.68 |  | 2.56
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.37 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.37 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
OFFICE_WALL_SOUTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 180 | 90 | S
OFFICE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 0 | 90 | N
OFFICE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 236.88 | 0 | 180
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS | 0.8 | 0.641 | 0.71 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.3 | 3.242 | 6.3 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_WEST_1 | EXT-WALLS | 0.8 | 0.641 | 0.71 | 182.07 | 270 | 90 | W
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOFS | 0.3 | 0.369 | 0.4 | 1393.41 | 0 | 0
BULKSTORAGE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOFS | 0.3 | 0.369 | 0.4 | 3204.84 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW_SOUTH | 5.58 | 5.58 | 6.49 | 0.25 | 0.25 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW_SOUTH | 5.58 | 5.58 | 6.49 | 0.25 | 0.25 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW_WEST | 3.25 | 3.25 | 6.49 | 0.25 | 0.25 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW_WEST | 3.25 | 3.25 | 6.49 | 0.25 | 0.25 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 6.49 | 0.25 | 0.25
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 6.49 | 0.25 | 0.25
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15257.33 | 12185.35 | 3071.98 | 0.8 | 4.04
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 70764.48 | 54014.59 | 16749.89 | 0.76 | 3.99
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 37800.65 | 0.8
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 9840.04 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 30679.72 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.92 | 1049.99 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.86 | 7369.94 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 13105.5485 | 21.9191 | 72.5599 | 0 | 0.0002 | 535985.3678 | 5549.4041
February | 11742.1818 | 19.6484 | 65.0802 | 0 | 0.0002 | 480734.6618 | 4973.0609
March | 13196.4759 | 22.2741 | 74.5314 | 0 | 0.0002 | 550558.1547 | 5608.4273
April | 11987.1876 | 20.2567 | 67.8727 | 0 | 0.0002 | 501371.9559 | 5096.879
May | 13595.7326 | 22.9789 | 77.0099 | 0 | 0.0002 | 568868.029 | 5781.234
June | 15638.9594 | 26.4324 | 88.5838 | 0 | 0.0002 | 654363.722 | 6650.0704
July | 15406.1009 | 26.0388 | 87.2648 | 0 | 0.0002 | 644620.4809 | 6551.0532
August | 15990.3215 | 27.0262 | 90.574 | 0 | 0.0002 | 669065.3787 | 6799.4782
September | 13540.7495 | 22.8861 | 76.6989 | 0 | 0.0002 | 566570.641 | 5757.8599
October | 12697.6803 | 21.4597 | 71.9133 | 0 | 0.0002 | 531220.0118 | 5399.2243
November | 12504.0973 | 21.1059 | 70.6242 | 0 | 0.0002 | 521696.3483 | 5314.2162
December | 13166.9841 | 21.8639 | 71.7572 | 0 | 0.0002 | 530047.578 | 5559.4419
Annual Sum or Average | 162572.0193 | 273.8903 | 914.4703 | 0 | 0.0025 | 6755100 | 69040.3495
Minimum of Months | 11742.1818 | 19.6484 | 65.0802 | 0 | 0.0002 | 480734.6618 | 4973.0609
Maximum of Months | 15990.3215 | 27.0262 | 90.574 | 0 | 0.0002 | 669065.3787 | 6799.4782
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 64958300000 | 60503.98 | 20-JAN-09:09 | 49331.035 | 9104.406 | 2068.539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 58262200000 | 60205.336 | 23-FEB-09:09 | 49331.035 | 9104.406 | 1769.894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 66724400000 | 64086.24 | 17-MAR-15:00 | 49331.035 | 9104.406 | 1651.106 | 0 | 3999.693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 60763400000 | 69152.685 | 28-APR-15:00 | 49331.035 | 9104.406 | 3203.43 | 0 | 7513.813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 68943500000 | 79204.532 | 30-MAY-15:00 | 49331.035 | 9104.406 | 5877.114 | 0 | 14891.977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 79305100000 | 90266.942 | 28-JUN-15:00 | 49331.035 | 9104.406 | 8372.918 | 0 | 23458.583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 78124200000 | 88611.154 | 19-JUL-15:00 | 49331.035 | 9104.406 | 7961.377 | 0 | 22214.335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 81086800000 | 90088.091 | 01-AUG-15:00 | 49331.035 | 9104.406 | 8342.677 | 0 | 23309.972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 68665100000 | 81580.672 | 08-SEP-15:00 | 49331.035 | 9104.406 | 6314.428 | 0 | 16830.803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 64380800000 | 69086.594 | 02-OCT-15:00 | 49331.035 | 9104.406 | 3114.915 | 0 | 7536.237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 63226600000 | 59926.319 | 13-NOV-15:00 | 49331.035 | 9104.406 | 413.369 | 0 | 1077.508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 64238700000 | 60869.886 | 26-DEC-09:09 | 49331.035 | 9104.406 | 2434.444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 818679000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 58262200000 | 59926.319 |  | 49331.035 | 9104.406 | 413.369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 81086800000 | 90266.942 |  | 49331.035 | 9104.406 | 8372.918 | 0 | 23458.583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 25671.79 | 174.8 | 0 | 25846.59
Cost per Total Building Area ($/m2) | 5.31 | 0.04 | 0 | 5.35
Cost per Net Conditioned Building Area ($/m2) | 5.31 | 0.04 | 0 | 5.35

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 873.36 | 180.63 | 180.63
Net Site Energy | 873.36 | 180.63 | 180.63
Total Source Energy | 2705.63 | 559.58 | 559.58
Net Source Energy | 2705.63 | 559.58 | 559.58
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 102.26 | 0 | 0 | 0 | 0
Cooling | 15.46 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 545.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 96.3 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 9.85 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 771.1 | 102.26 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 11.8401 | 47.39 | 8.07
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 15.06 |  | 0
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 9.68 |  | 2.56
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.37 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.37 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
OFFICE_WALL_SOUTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 180 | 90 | S
OFFICE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 0 | 90 | N
OFFICE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 236.88 | 0 | 180
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS | 0.8 | 0.641 | 0.71 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.3 | 3.242 | 6.3 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_WEST_1 | EXT-WALLS | 0.8 | 0.641 | 0.71 | 182.07 | 270 | 90 | W
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOFS | 0.3 | 0.369 | 0.4 | 1393.41 | 0 | 0
BULKSTORAGE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOFS | 0.3 | 0.369 | 0.4 | 3204.84 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW_SOUTH | 5.58 | 5.58 | 3.18 | 0.402 | 0.495 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW_SOUTH | 5.58 | 5.58 | 3.18 | 0.402 | 0.495 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW_WEST | 3.25 | 3.25 | 3.18 | 0.402 | 0.495 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW_WEST | 3.25 | 3.25 | 3.18 | 0.402 | 0.495 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 3.18 | 0.402 | 0.495
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16330.17 | 12047.56 | 4282.61 | 0.74 | 3.84
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 61160.09 | 43109.96 | 18050.14 | 0.7 | 3.25
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 37909.17 | 0.8
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 12656.85 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 62114.01 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.82 | 937.65 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.75 | 3009.89 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 14585.1197 | 26.2818 | 64.0002 | 0 | 0.0002 | 113826.9993 | 6252.4859
February | 12826.0999 | 23.3126 | 57.264 | 0 | 0.0002 | 101848.3304 | 5516.9208
March | 13198.792 | 25.2309 | 65.0109 | 0 | 0.0002 | 115639.2936 | 5791.8284
April | 11758.5968 | 22.6049 | 58.5403 | 0 | 0.0002 | 104130.7043 | 5171.5876
May | 12512.8186 | 24.1616 | 62.8185 | 0 | 0.0002 | 111741.7778 | 5513.1643
June | 12919.4009 | 24.9473 | 64.8631 | 0 | 0.0002 | 115378.6987 | 5692.3691
July | 12805.2433 | 24.7269 | 64.29 | 0 | 0.0002 | 114359.1968 | 5642.0706
August | 13636.0512 | 26.3312 | 68.4611 | 0 | 0.0002 | 121778.855 | 6008.1298
September | 12087.8939 | 23.3417 | 60.6884 | 0 | 0.0002 | 107952.7973 | 5326.0019
October | 12367.6927 | 23.8551 | 61.9614 | 0 | 0.0002 | 110216.8059 | 5446.799
November | 12675.1381 | 24.0925 | 61.7582 | 0 | 0.0002 | 109852.3131 | 5549.3548
December | 13701.6503 | 25.1113 | 62.1895 | 0 | 0.0002 | 110610.8322 | 5912.6738
Annual Sum or Average | 155074.4973 | 293.9977 | 751.8456 | 0 | 0.0028 | 1337340 | 67823.386
Minimum of Months | 11758.5968 | 22.6049 | 57.264 | 0 | 0.0002 | 101848.3304 | 5171.5876
Maximum of Months | 14585.1197 | 26.3312 | 68.4611 | 0 | 0.0002 | 121778.855 | 6252.4859
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 65631600000 | 60585.471 | 02-JAN-09:09 | 49331.035 | 9104.406 | 2150.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 58724800000 | 61194.533 | 10-FEB-09:09 | 49331.035 | 9104.406 | 2759.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 66676500000 | 59343.451 | 13-MAR-08:09 | 49331.035 | 9104.406 | 908.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 60040800000 | 60050.376 | 14-APR-15:00 | 49331.035 | 9104.406 | 382.537 | 0 | 1232.397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 64429300000 | 69877.476 | 15-MAY-15:39 | 49331.035 | 9104.406 | 1850.859 | 0 | 9591.175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 66526300000 | 76023.816 | 19-JUN-15:30 | 49331.035 | 9104.406 | 2663.037 | 0 | 14925.337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 65938400000 | 82758.41 | 03-JUL-15:00 | 49331.035 | 9104.406 | 3528.134 | 0 | 20794.835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 70216500000 | 75876.421 | 17-AUG-13:00 | 49331.035 | 9104.406 | 2663.064 | 0 | 14777.916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 62244600000 | 71467.663 | 11-SEP-13:00 | 49331.035 | 9104.406 | 2087.899 | 0 | 10944.323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 63550000000 | 60134.666 | 02-OCT-14:00 | 49331.035 | 9104.406 | 407.993 | 0 | 1291.231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 63339800000 | 59388.962 | 15-NOV-09:09 | 49331.035 | 9104.406 | 953.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 63777200000 | 60686.371 | 22-DEC-09:09 | 49331.035 | 9104.406 | 2250.929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 771096000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 58724800000 | 59343.451 |  | 49331.035 | 9104.406 | 382.537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 70216500000 | 82758.41 |  | 49331.035 | 9104.406 | 3528.134 | 0 | 20794.835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 22305.44 | 955.62 | 0 | 23261.06
Cost per Total Building Area ($/m2) | 4.61 | 0.2 | 0 | 4.81
Cost per Net Conditioned Building Area ($/m2) | 4.61 | 0.2 | 0 | 4.81

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 758.03 | 156.78 | 156.78
Net Site Energy | 758.03 | 156.78 | 156.78
Total Source Energy | 2334.23 | 482.76 | 482.76
Net Source Energy | 2334.23 | 482.76 | 482.76
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 5.93 | 0 | 0 | 0 | 0
Cooling | 2.48 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 545.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 96.23 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 3.91 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 752.1 | 5.93 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 11.8401 | 47.39 | 8.07
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 15.06 |  | 0
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 9.68 |  | 2.56
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.37 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.37 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
OFFICE_WALL_SOUTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 180 | 90 | S
OFFICE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 0 | 90 | N
OFFICE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 236.88 | 0 | 180
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS | 0.8 | 0.641 | 0.71 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.3 | 3.242 | 6.3 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_WEST_1 | EXT-WALLS | 0.8 | 0.641 | 0.71 | 182.07 | 270 | 90 | W
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOFS | 0.3 | 0.369 | 0.4 | 1393.41 | 0 | 0
BULKSTORAGE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOFS | 0.3 | 0.369 | 0.4 | 3204.84 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW_SOUTH | 5.58 | 5.58 | 3.18 | 0.402 | 0.495 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW_SOUTH | 5.58 | 5.58 | 3.18 | 0.402 | 0.495 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW_WEST | 3.25 | 3.25 | 3.18 | 0.402 | 0.495 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW_WEST | 3.25 | 3.25 | 3.18 | 0.402 | 0.495 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 3.18 | 0.402 | 0.495
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 11443.92 | 9139.75 | 2304.17 | 0.8 | 4.05
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 25704.6 | 20413.64 | 5290.96 | 0.79 | 3.73
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 39207.88 | 0.8
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 7626.44 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 16180.49 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.69 | 801.88 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.53 | 1677.45 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 5643.1824 | 4.8328 | 51.9988 | 0 | 0 | 313750.313 | 2111.7611
February | 5052.3786 | 4.3264 | 46.6331 | 0 | 0 | 281375.1366 | 1890.9125
March | 5819.9244 | 4.9832 | 53.7979 | 0 | 0 | 324606.2652 | 2178.4208
April | 5222.2843 | 4.4707 | 48.4227 | 0 | 0 | 292173.7917 | 1955.177
May | 5516.6502 | 4.7216 | 51.3364 | 0 | 0 | 309755.6061 | 2065.9473
June | 5417.2888 | 4.6362 | 50.4919 | 0 | 0 | 304660.1878 | 2028.9816
July | 5238.868 | 4.4833 | 48.8586 | 0 | 0 | 294805.2542 | 1962.2468
August | 5760.2532 | 4.9295 | 53.7212 | 0 | 0 | 324145.0082 | 2157.5345
September | 5282.5425 | 4.5207 | 49.2659 | 0 | 0 | 297262.9365 | 1978.6053
October | 5527.8779 | 4.7307 | 51.5383 | 0 | 0 | 310973.8581 | 2070.4491
November | 5496.9623 | 4.7054 | 51.0432 | 0 | 0 | 307985.8822 | 2058.2387
December | 5515.1658 | 4.7232 | 50.8174 | 0 | 0 | 306621.9878 | 2063.8499
Annual Sum or Average | 65493.3786 | 56.0637 | 607.9253 | 0 | 0.0003 | 3668120 | 24522.1246
Minimum of Months | 5052.3786 | 4.3264 | 46.6331 | 0 | 0 | 281375.1366 | 1890.9125
Maximum of Months | 5819.9244 | 4.9832 | 53.7979 | 0 | 0 | 324606.2652 | 2178.4208
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 64330600000 | 64640.186 | 02-JAN-16:00 | 49331.035 | 9104.406 | 80.12 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 57692500000 | 59110.002 | 13-FEB-15:09 | 49331.035 | 9104.406 | 235.411 | 0 | 439.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 66556500000 | 59306.14 | 31-MAR-14:00 | 49331.035 | 9104.406 | 284.219 | 0 | 586.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 59906600000 | 59435.354 | 11-APR-15:00 | 49331.035 | 9104.406 | 297.688 | 0 | 702.225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 63511500000 | 59523.374 | 30-MAY-14:00 | 49331.035 | 9104.406 | 332.127 | 0 | 755.805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 62466800000 | 59639.515 | 30-JUN-14:00 | 49331.035 | 9104.406 | 359.027 | 0 | 845.047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 60446200000 | 63339.674 | 10-JUL-15:00 | 49331.035 | 9104.406 | 1157.433 | 0 | 3746.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 66461900000 | 65715.801 | 08-AUG-15:09 | 49331.035 | 9104.406 | 1664.563 | 0 | 5615.797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 60950100000 | 64902.876 | 25-SEP-13:39 | 49331.035 | 9104.406 | 1489.04 | 0 | 4978.394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 63761300000 | 65317.697 | 31-OCT-16:00 | 49331.035 | 9104.406 | 259.406 | 0 | 498.225 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 63148700000 | 65095.397 | 20-NOV-16:49 | 49331.035 | 9104.406 | 198.078 | 0 | 337.252 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 62869000000 | 64949.203 | 19-DEC-16:49 | 49331.035 | 9104.406 | 161.857 | 0 | 227.28 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 752102000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 57692500000 | 59110.002 |  | 49331.035 | 9104.406 | 80.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 66556500000 | 65715.801 |  | 49331.035 | 9104.406 | 1664.563 | 0 | 5615.797 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 28295.45 | 51.4 | 0 | 28346.85
Cost per Total Building Area ($/m2) | 5.85 | 0.01 | 0 | 5.86
Cost per Net Conditioned Building Area ($/m2) | 5.85 | 0.01 | 0 | 5.86

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 859.71 | 177.8 | 177.8
Net Site Energy | 859.71 | 177.8 | 177.8
Total Source Energy | 2926.73 | 605.3 | 605.3
Net Source Energy | 2926.73 | 605.3 | 605.3
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 59.73 | 0 | 0 | 0 | 0
Cooling | 31.23 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 545.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 96.21 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 23.05 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 799.97 | 59.73 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 11.8401 | 47.39 | 8.07
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 15.06 |  | 0
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 9.68 |  | 2.56
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.37 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.37 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
OFFICE_WALL_SOUTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 180 | 90 | S
OFFICE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 0 | 90 | N
OFFICE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 236.88 | 0 | 180
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS | 0.8 | 0.641 | 0.71 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.3 | 3.242 | 6.3 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_WEST_1 | EXT-WALLS | 0.8 | 0.641 | 0.71 | 182.07 | 270 | 90 | W
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOFS | 0.3 | 0.369 | 0.4 | 1393.41 | 0 | 0
BULKSTORAGE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOFS | 0.3 | 0.369 | 0.4 | 3204.84 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW_SOUTH | 5.58 | 5.58 | 3.18 | 0.402 | 0.495 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW_SOUTH | 5.58 | 5.58 | 3.18 | 0.402 | 0.495 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW_WEST | 3.25 | 3.25 | 3.18 | 0.402 | 0.495 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW_WEST | 3.25 | 3.25 | 3.18 | 0.402 | 0.495 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 3.18 | 0.402 | 0.495
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14064.26 | 11232.5 | 2831.77 | 0.8 | 4.03
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 60991.83 | 48378.9 | 12612.93 | 0.79 | 4.33
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 36355.77 | 0.8
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11273.88 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 46405.63 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.85 | 967.88 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.63 | 6923.74 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 16176.3736 | 25.5802 | 102.4805 | 0 | 0.0002 | 511064.9689 | 6731.2367
February | 13224.2495 | 21.4664 | 88.9907 | 0 | 0.0002 | 443813.2214 | 5560.4526
March | 15245.3896 | 24.7453 | 102.5731 | 0 | 0.0002 | 511551.3182 | 6410.0845
April | 13348.2689 | 21.8772 | 91.7941 | 0 | 0.0002 | 457802.0696 | 5634.3715
May | 14524.3014 | 23.816 | 99.9877 | 0 | 0.0002 | 498665.86 | 6131.9544
June | 16332.7533 | 26.7845 | 112.4671 | 0 | 0.0002 | 560904.2145 | 6895.786
July | 16385.9734 | 26.8718 | 112.8336 | 0 | 0.0002 | 562731.9116 | 6918.2558
August | 17157.0869 | 28.1364 | 118.1434 | 0 | 0.0002 | 589213.7184 | 7243.8245
September | 14407.0716 | 23.6266 | 99.2069 | 0 | 0.0002 | 494771.8861 | 6082.7517
October | 14220.1147 | 23.312 | 97.8446 | 0 | 0.0002 | 487977.6827 | 6002.9894
November | 14252.9164 | 23.2443 | 96.9287 | 0 | 0.0002 | 483405.536 | 6004.2126
December | 15351.2384 | 24.4741 | 99.1213 | 0 | 0.0002 | 494320.5887 | 6408.5443
Annual Sum or Average | 180625.7375 | 293.9349 | 1222.3717 | 0 | 0.0023 | 6096220 | 76024.4642
Minimum of Months | 13224.2495 | 21.4664 | 88.9907 | 0 | 0.0002 | 443813.2214 | 5560.4526
Maximum of Months | 17157.0869 | 28.1364 | 118.1434 | 0 | 0.0002 | 589213.7184 | 7243.8245
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 67064000000 | 64883.569 | 10-JAN-16:00 | 49331.035 | 9104.406 | 323.503 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 58239000000 | 59107.266 | 03-FEB-09:09 | 49331.035 | 9104.406 | 671.824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 67127800000 | 59220.927 | 03-MAR-09:09 | 49331.035 | 9104.406 | 785.485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 60074600000 | 67143.863 | 21-APR-15:00 | 49331.035 | 9104.406 | 2809.036 | 0 | 5899.386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 65436900000 | 75293.213 | 31-MAY-15:00 | 49331.035 | 9104.406 | 5353.124 | 0 | 11504.648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 73604100000 | 84992.802 | 27-JUN-15:00 | 49331.035 | 9104.406 | 7906.33 | 0 | 18651.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 73844000000 | 84449.525 | 24-JUL-15:00 | 49331.035 | 9104.406 | 7829.661 | 0 | 18184.423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 77319000000 | 83243.777 | 04-AUG-15:00 | 49331.035 | 9104.406 | 7424.732 | 0 | 17383.603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 64926000000 | 82054.636 | 01-SEP-14:00 | 49331.035 | 9104.406 | 7216.604 | 0 | 16402.591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 64034400000 | 65903.998 | 04-OCT-14:00 | 49331.035 | 9104.406 | 2384.357 | 0 | 5084.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 63434400000 | 64692.779 | 09-NOV-16:40 | 49331.035 | 9104.406 | 93.91 | 0 | 38.802 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 64866700000 | 64785.603 | 26-DEC-16:00 | 49331.035 | 9104.406 | 225.537 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 799971000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 58239000000 | 59107.266 |  | 49331.035 | 9104.406 | 93.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 77319000000 | 84992.802 |  | 49331.035 | 9104.406 | 7906.33 | 0 | 18651.03 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 22950.8 | 451.07 | 0 | 23401.87
Cost per Total Building Area ($/m2) | 4.75 | 0.09 | 0 | 4.84
Cost per Net Conditioned Building Area ($/m2) | 4.75 | 0.09 | 0 | 4.84

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 782.11 | 161.76 | 161.76
Net Site Energy | 782.11 | 161.76 | 161.76
Total Source Energy | 2356.76 | 487.42 | 487.42
Net Source Energy | 2356.76 | 487.42 | 487.42
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 31.89 | 0 | 0 | 0 | 0
Cooling | 0.37 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 545.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 96.26 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 4.11 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 750.22 | 31.89 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 11.8401 | 47.39 | 8.07
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 15.06 |  | 0
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 9.68 |  | 2.56
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.37 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.37 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
OFFICE_WALL_SOUTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 180 | 90 | S
OFFICE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 0 | 90 | N
OFFICE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 236.88 | 0 | 180
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS | 0.8 | 0.641 | 0.71 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.3 | 3.242 | 6.3 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_WEST_1 | EXT-WALLS | 0.8 | 0.641 | 0.71 | 182.07 | 270 | 90 | W
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOFS | 0.3 | 0.369 | 0.4 | 1393.41 | 0 | 0
BULKSTORAGE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOFS | 0.3 | 0.369 | 0.4 | 3204.84 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW_SOUTH | 5.58 | 5.58 | 6.49 | 0.61 | 0.61 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW_SOUTH | 5.58 | 5.58 | 6.49 | 0.61 | 0.61 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW_WEST | 3.25 | 3.25 | 6.49 | 0.61 | 0.61 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW_WEST | 3.25 | 3.25 | 6.49 | 0.61 | 0.61 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 6.49 | 0.61 | 0.61
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 6.49 | 0.61 | 0.61
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 9186.67 | 7336.98 | 1849.69 | 0.8 | 4.04
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17576.2 | 14037.33 | 3538.88 | 0.8 | 4.03
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 39333.64 | 0.8
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 9451.3 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 28322.77 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.55 | 643.71 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.06 | 1209.57 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 6209.37 | 5.3446 | 52.4034 | 0 | 0 | 316175.5467 | 2308.9541
February | 5118.0661 | 4.3855 | 46.7329 | 0 | 0 | 281975.8769 | 1913.9516
March | 5936.4497 | 5.0887 | 53.8472 | 0 | 0 | 324900.202 | 2218.9008
April | 5280.3324 | 4.5237 | 48.3648 | 0 | 0 | 291822.5023 | 1975.0909
May | 5546.1082 | 4.7495 | 51.1457 | 0 | 0 | 308603.2545 | 2075.5609
June | 5428.2225 | 4.6474 | 50.2469 | 0 | 0 | 303180.6867 | 2032.0183
July | 5204.9371 | 4.4556 | 48.298 | 0 | 0 | 291421.6652 | 1948.7928
August | 5704.1121 | 4.8832 | 52.8863 | 0 | 0 | 319106.5122 | 2135.5568
September | 5257.8446 | 4.5008 | 48.8141 | 0 | 0 | 294535.6385 | 1968.6786
October | 5556.8432 | 4.7579 | 51.3814 | 0 | 0 | 310025.8499 | 2079.9954
November | 5580.8447 | 4.781 | 51.1498 | 0 | 0 | 308626.7691 | 2087.5957
December | 5860.079 | 5.0345 | 51.1418 | 0 | 0 | 308569.8086 | 2184.2148
Annual Sum or Average | 66683.2097 | 57.1524 | 606.4122 | 0 | 0.0003 | 3658940 | 24929.3106
Minimum of Months | 5118.0661 | 4.3855 | 46.7329 | 0 | 0 | 281975.8769 | 1913.9516
Maximum of Months | 6209.37 | 5.3446 | 53.8472 | 0 | 0 | 324900.202 | 2308.9541
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 64827900000 | 64739.91 | 02-JAN-16:00 | 49331.035 | 9104.406 | 179.844 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 57815600000 | 58925.622 | 15-FEB-15:00 | 49331.035 | 9104.406 | 184.578 | 0 | 305.602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 66616700000 | 58807.232 | 16-MAR-08:09 | 49331.035 | 9104.406 | 371.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 59834600000 | 59127.034 | 13-APR-14:00 | 49331.035 | 9104.406 | 238.615 | 0 | 452.977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 63275300000 | 59118.098 | 17-MAY-14:39 | 49331.035 | 9104.406 | 230.735 | 0 | 451.922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 62163400000 | 59379.582 | 16-JUN-14:00 | 49331.035 | 9104.406 | 294.356 | 0 | 649.785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 59752400000 | 61026.275 | 03-JUL-14:00 | 49331.035 | 9104.406 | 683.011 | 0 | 1907.823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 65428800000 | 59407.85 | 15-AUG-13:30 | 49331.035 | 9104.406 | 299.637 | 0 | 672.772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 60390900000 | 63699.445 | 28-SEP-15:00 | 49331.035 | 9104.406 | 1247.908 | 0 | 4016.095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 63566900000 | 59360.71 | 13-OCT-14:00 | 49331.035 | 9104.406 | 291.986 | 0 | 633.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 63280100000 | 64678.482 | 22-NOV-16:00 | 49331.035 | 9104.406 | 118.416 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 63268400000 | 64716.42 | 27-DEC-16:00 | 49331.035 | 9104.406 | 156.353 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 750221000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 57815600000 | 58807.232 |  | 49331.035 | 9104.406 | 118.416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 66616700000 | 64739.91 |  | 49331.035 | 9104.406 | 1247.908 | 0 | 4016.095 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 31580.88 | 281.02 | 0 | 31861.9
Cost per Total Building Area ($/m2) | 6.53 | 0.06 | 0 | 6.59
Cost per Net Conditioned Building Area ($/m2) | 6.53 | 0.06 | 0 | 6.59

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1004.83 | 207.82 | 207.82
Net Site Energy | 1004.83 | 207.82 | 207.82
Total Source Energy | 3009.87 | 622.5 | 622.5
Net Source Energy | 3009.87 | 622.5 | 622.5
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 234.87 | 0 | 0 | 0 | 0
Cooling | 12.33 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 545.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 96.2 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 11.95 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 769.96 | 234.87 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 11.8401 | 47.39 | 8.07
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 15.06 |  | 0
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 9.68 |  | 2.56
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.37 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.37 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
OFFICE_WALL_SOUTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 180 | 90 | S
OFFICE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 0 | 90 | N
OFFICE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 236.88 | 0 | 180
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS | 0.8 | 0.641 | 0.71 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.3 | 3.242 | 6.3 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_WEST_1 | EXT-WALLS | 0.8 | 0.641 | 0.71 | 182.07 | 270 | 90 | W
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOFS | 0.3 | 0.369 | 0.4 | 1393.41 | 0 | 0
BULKSTORAGE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOFS | 0.3 | 0.369 | 0.4 | 3204.84 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW_SOUTH | 5.58 | 5.58 | 3.18 | 0.402 | 0.495 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW_SOUTH | 5.58 | 5.58 | 3.18 | 0.402 | 0.495 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW_WEST | 3.25 | 3.25 | 3.18 | 0.402 | 0.495 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW_WEST | 3.25 | 3.25 | 3.18 | 0.402 | 0.495 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 3.18 | 0.402 | 0.495
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15603.18 | 11394.21 | 4208.97 | 0.73 | 3.81
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 57169.45 | 39825.97 | 17343.48 | 0.7 | 3.23
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 39138.15 | 0.8
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 14297.26 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 77097.46 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.77 | 874 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.5 | 2728.84 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 15331.4104 | 26.1826 | 67.7936 | 0 | 0.0003 | 4215.1321 | 6427.8237
February | 12760.0763 | 22.4742 | 60.1937 | 0 | 0.0002 | 3742.871 | 5412.2041
March | 12363.6904 | 23.5437 | 68.0844 | 0 | 0.0003 | 4234.1816 | 5405.7119
April | 10283.2024 | 20.3197 | 60.7011 | 0 | 0.0002 | 3775.2476 | 4563.5282
May | 10667.9267 | 21.2941 | 64.1549 | 0 | 0.0003 | 3990.1202 | 4753.8507
June | 10963.3617 | 21.9202 | 66.1321 | 0 | 0.0003 | 4113.1039 | 4888.8234
July | 10841.9222 | 21.6774 | 65.3998 | 0 | 0.0003 | 4067.559 | 4834.6747
August | 11855.2993 | 23.7035 | 71.5126 | 0 | 0.0003 | 4447.7472 | 5286.564
September | 10254.603 | 20.4998 | 61.8389 | 0 | 0.0002 | 3846.0863 | 4572.4747
October | 10931.8271 | 21.619 | 64.6273 | 0 | 0.0003 | 4019.4421 | 4852.9918
November | 11630.9834 | 22.265 | 64.6926 | 0 | 0.0003 | 4023.2862 | 5096.0046
December | 13783.1992 | 24.3949 | 65.6758 | 0 | 0.0003 | 4083.7974 | 5857.0217
Annual Sum or Average | 141667.5022 | 269.8942 | 780.8068 | 0 | 0.0032 | 48558.5746 | 61951.6735
Minimum of Months | 10254.603 | 20.3197 | 60.1937 | 0 | 0.0002 | 3742.871 | 4563.5282
Maximum of Months | 15331.4104 | 26.1826 | 71.5126 | 0 | 0.0003 | 4447.7472 | 6427.8237
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 66836800000 | 65193.86 | 10-JAN-16:00 | 49331.035 | 9104.406 | 633.794 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 59348500000 | 60477.323 | 08-FEB-09:09 | 49331.035 | 9104.406 | 2041.881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 67138900000 | 59700.675 | 31-MAR-08:09 | 49331.035 | 9104.406 | 1265.233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 59861900000 | 59165.95 | 05-APR-15:00 | 49331.035 | 9104.406 | 211.977 | 0 | 518.531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 63269000000 | 60003.36 | 15-MAY-14:00 | 49331.035 | 9104.406 | 365.273 | 0 | 1202.645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 65219000000 | 77358.97 | 30-JUN-15:00 | 49331.035 | 9104.406 | 2736.928 | 0 | 16186.601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 64496900000 | 81245.422 | 25-JUL-13:39 | 49331.035 | 9104.406 | 3249.952 | 0 | 19560.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 70525300000 | 80016.527 | 04-AUG-15:30 | 49331.035 | 9104.406 | 3077.581 | 0 | 18503.504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 60985100000 | 68825.339 | 08-SEP-15:00 | 49331.035 | 9104.406 | 1615.417 | 0 | 8774.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 63733900000 | 60128.605 | 03-OCT-14:00 | 49331.035 | 9104.406 | 391.235 | 0 | 1301.929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 63794900000 | 64790.07 | 20-NOV-16:00 | 49331.035 | 9104.406 | 230.004 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 64754300000 | 65489.214 | 20-DEC-16:00 | 49331.035 | 9104.406 | 929.148 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 769964000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 59348500000 | 59165.95 |  | 49331.035 | 9104.406 | 211.977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 70525300000 | 81245.422 |  | 49331.035 | 9104.406 | 3249.952 | 0 | 19560.029 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 17420.58 | 2261.89 | 0 | 19682.47
Cost per Total Building Area ($/m2) | 3.6 | 0.47 | 0 | 4.07
Cost per Net Conditioned Building Area ($/m2) | 3.6 | 0.47 | 0 | 4.07

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 943.04 | 195.04 | 195.04
Net Site Energy | 943.04 | 195.04 | 195.04
Total Source Energy | 2733.79 | 565.4 | 565.4
Net Source Energy | 2733.79 | 565.4 | 565.4
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 177.55 | 0 | 0 | 0 | 0
Cooling | 8.05 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 545.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 96.24 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 11.73 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 765.49 | 177.55 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 11.8401 | 47.39 | 8.07
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 15.06 |  | 0
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 9.68 |  | 2.56
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.37 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.37 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
OFFICE_WALL_SOUTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 180 | 90 | S
OFFICE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 0 | 90 | N
OFFICE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 236.88 | 0 | 180
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS | 0.8 | 0.641 | 0.71 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.3 | 3.242 | 6.3 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_WEST_1 | EXT-WALLS | 0.8 | 0.641 | 0.71 | 182.07 | 270 | 90 | W
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOFS | 0.3 | 0.369 | 0.4 | 1393.41 | 0 | 0
BULKSTORAGE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOFS | 0.3 | 0.369 | 0.4 | 3204.84 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW_SOUTH | 5.58 | 5.58 | 3.18 | 0.402 | 0.495 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW_SOUTH | 5.58 | 5.58 | 3.18 | 0.402 | 0.495 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW_WEST | 3.25 | 3.25 | 3.18 | 0.402 | 0.495 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW_WEST | 3.25 | 3.25 | 3.18 | 0.402 | 0.495 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 3.18 | 0.402 | 0.495
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13499.18 | 10781.19 | 2717.99 | 0.8 | 4.04
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 45317.39 | 36192.98 | 9124.42 | 0.8 | 3.47
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 32366.69 | 0.8
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13225.97 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 65429.25 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.82 | 929 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.74 | 2993.94 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 19989.8342 | 32.9461 | 80.1969 | 0 | 0.0003 | 83379.0214 | 8370.3536
February | 17071.2408 | 28.6563 | 71.3048 | 0 | 0.0003 | 74137.8463 | 7199.3004
March | 18757.5932 | 32.0774 | 81.5436 | 0 | 0.0003 | 84787.5204 | 7968.3737
April | 16052.8058 | 27.9994 | 72.7487 | 0 | 0.0003 | 75646.3794 | 6873.064
May | 16856.332 | 29.5583 | 77.2418 | 0 | 0.0003 | 80319.41 | 7232.53
June | 17046.5369 | 29.9084 | 78.203 | 0 | 0.0003 | 81319.0637 | 7315.7659
July | 16936.625 | 29.716 | 77.7009 | 0 | 0.0003 | 80796.9895 | 7268.6348
August | 17976.9362 | 31.5412 | 82.4736 | 0 | 0.0003 | 85759.8446 | 7715.1017
September | 16106.5508 | 28.259 | 73.8898 | 0 | 0.0003 | 76833.9937 | 6912.3409
October | 17009.4291 | 29.6817 | 77.1583 | 0 | 0.0003 | 80231.7006 | 7283.9926
November | 18042.6675 | 30.6905 | 77.5467 | 0 | 0.0003 | 80630.4639 | 7648.5563
December | 19800.2325 | 32.4759 | 78.5826 | 0 | 0.0003 | 81699.493 | 8275.4906
Annual Sum or Average | 211646.784 | 363.5104 | 928.5907 | 0 | 0.0036 | 965541.7266 | 90063.5045
Minimum of Months | 16052.8058 | 27.9994 | 71.3048 | 0 | 0.0003 | 74137.8463 | 6873.064
Maximum of Months | 19989.8342 | 32.9461 | 82.4736 | 0 | 0.0003 | 85759.8446 | 8370.3536
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 66103900000 | 60434.318 | 04-JAN-09:09 | 49331.035 | 9104.406 | 1998.877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 58777400000 | 59929.869 | 06-FEB-09:09 | 49331.035 | 9104.406 | 1494.427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 67220600000 | 59807.09 | 29-MAR-08:09 | 49331.035 | 9104.406 | 1371.648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 59973400000 | 59307.416 | 21-APR-15:00 | 49331.035 | 9104.406 | 278.438 | 0 | 593.536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 63678200000 | 64576.314 | 31-MAY-15:00 | 49331.035 | 9104.406 | 1357.715 | 0 | 4783.157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 64470700000 | 73884.752 | 29-JUN-15:00 | 49331.035 | 9104.406 | 3131.744 | 0 | 12317.566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 64056800000 | 74440.067 | 03-JUL-15:00 | 49331.035 | 9104.406 | 3199.828 | 0 | 12804.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 67991400000 | 74403.76 | 01-AUG-15:50 | 49331.035 | 9104.406 | 3187.808 | 0 | 12780.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 60914900000 | 64600.348 | 14-SEP-15:00 | 49331.035 | 9104.406 | 1382.848 | 0 | 4782.059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 63608700000 | 59466.048 | 13-OCT-14:00 | 49331.035 | 9104.406 | 319.324 | 0 | 711.283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 63924800000 | 64722.191 | 20-NOV-16:00 | 49331.035 | 9104.406 | 162.125 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 64772300000 | 65419.383 | 28-DEC-16:00 | 49331.035 | 9104.406 | 859.317 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 765493000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 58777400000 | 59307.416 |  | 49331.035 | 9104.406 | 162.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 67991400000 | 74440.067 |  | 49331.035 | 9104.406 | 3199.828 | 0 | 12804.798 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 8044.8 | 1209.36 | 0 | 9254.16
Cost per Total Building Area ($/m2) | 1.66 | 0.25 | 0 | 1.91
Cost per Net Conditioned Building Area ($/m2) | 1.66 | 0.25 | 0 | 1.91

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 888.54 | 183.77 | 183.77
Net Site Energy | 888.54 | 183.77 | 183.77
Total Source Energy | 1459.69 | 301.89 | 301.89
Net Source Energy | 1459.69 | 301.89 | 301.89
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 135.62 | 0 | 0 | 0 | 0
Cooling | 0.43 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 545.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 96.05 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 6.97 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 752.93 | 135.62 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 11.8401 | 47.39 | 8.07
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 15.06 |  | 0
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 9.68 |  | 2.56
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.37 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.37 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
OFFICE_WALL_SOUTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 180 | 90 | S
OFFICE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 0 | 90 | N
OFFICE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 236.88 | 0 | 180
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS | 0.8 | 0.641 | 0.71 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.3 | 3.242 | 6.3 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_WEST_1 | EXT-WALLS | 0.8 | 0.641 | 0.71 | 182.07 | 270 | 90 | W
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOFS | 0.3 | 0.369 | 0.4 | 1393.41 | 0 | 0
BULKSTORAGE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOFS | 0.3 | 0.369 | 0.4 | 3204.84 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW_SOUTH | 5.58 | 5.58 | 3.18 | 0.402 | 0.495 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW_SOUTH | 5.58 | 5.58 | 3.18 | 0.402 | 0.495 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW_WEST | 3.25 | 3.25 | 3.18 | 0.402 | 0.495 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW_WEST | 3.25 | 3.25 | 3.18 | 0.402 | 0.495 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 3.18 | 0.402 | 0.495
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 9622.85 | 7685.34 | 1937.51 | 0.8 | 4.05
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27871.31 | 21513.3 | 6358.01 | 0.77 | 3.67
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 38791.02 | 0.8
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11851.01 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 53932.63 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.58 | 674.27 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.56 | 1707.24 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 4972.0733 | 6.7348 | 14.2053 | 0 | 0.0001 | 187649.7882 | 1958.7756
February | 3732.467 | 5.3575 | 12.5904 | 0 | 0.0001 | 166363.7601 | 1502.7453
March | 4195.4852 | 6.063 | 14.4135 | 0 | 0.0001 | 190458.4315 | 1693.545
April | 3255.3865 | 4.9609 | 12.821 | 0 | 0.0001 | 169447.404 | 1341.5281
May | 3094.095 | 4.9145 | 13.4591 | 0 | 0.0001 | 177902.9249 | 1296.42
June | 2984.7899 | 4.7707 | 13.1742 | 0 | 0.0001 | 174139.4978 | 1253.8173
July | 2851.4118 | 4.5745 | 12.6938 | 0 | 0 | 167791.6317 | 1199.6066
August | 3135.2019 | 5.0337 | 13.9822 | 0 | 0.0001 | 184822.9227 | 1319.4193
September | 2935.3403 | 4.6871 | 12.9267 | 0 | 0.0001 | 170868.5314 | 1232.5559
October | 3255.919 | 5.1002 | 13.7074 | 0 | 0.0001 | 181177.2615 | 1356.5805
November | 3999.4245 | 5.7904 | 13.8083 | 0 | 0.0001 | 182461.8621 | 1615.549
December | 4839.6073 | 6.568 | 13.9075 | 0 | 0.0001 | 183717.3357 | 1907.9422
Annual Sum or Average | 43251.2018 | 64.5555 | 161.6894 | 0 | 0.0006 | 2136800 | 17678.4848
Minimum of Months | 2851.4118 | 4.5745 | 12.5904 | 0 | 0 | 166363.7601 | 1199.6066
Maximum of Months | 4972.0733 | 6.7348 | 14.4135 | 0 | 0.0001 | 190458.4315 | 1958.7756
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 66120400000 | 64957.187 | 02-JAN-16:00 | 49331.035 | 9104.406 | 397.121 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 58620100000 | 59299.309 | 15-FEB-09:09 | 49331.035 | 9104.406 | 863.867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 67110100000 | 59268.434 | 20-MAR-08:09 | 49331.035 | 9104.406 | 832.992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 59706600000 | 58983.513 | 11-APR-08:09 | 49331.035 | 9104.406 | 548.071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 62686000000 | 59201.22 | 04-MAY-14:00 | 49331.035 | 9104.406 | 252.094 | 0 | 513.684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 61359900000 | 59624.31 | 28-JUN-14:00 | 49331.035 | 9104.406 | 351.341 | 0 | 837.527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 59123200000 | 62896.319 | 24-JUL-15:39 | 49331.035 | 9104.406 | 1001.708 | 0 | 3459.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 65124400000 | 60935.635 | 07-AUG-15:00 | 49331.035 | 9104.406 | 625.287 | 0 | 1874.907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 60207400000 | 59861.266 | 01-SEP-15:00 | 49331.035 | 9104.406 | 398.943 | 0 | 1026.881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 63839800000 | 64749.121 | 30-OCT-16:00 | 49331.035 | 9104.406 | 189.055 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 64292400000 | 65120.265 | 29-NOV-16:00 | 49331.035 | 9104.406 | 560.198 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 64734800000 | 65223.215 | 13-DEC-16:19 | 49331.035 | 9104.406 | 663.149 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 752925000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 58620100000 | 58983.513 |  | 49331.035 | 9104.406 | 189.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 67110100000 | 65223.215 |  | 49331.035 | 9104.406 | 1001.708 | 0 | 3459.17 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 16207.68 | 1149.78 | 0 | 17357.46
Cost per Total Building Area ($/m2) | 3.35 | 0.24 | 0 | 3.59
Cost per Net Conditioned Building Area ($/m2) | 3.35 | 0.24 | 0 | 3.59

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1152.53 | 238.37 | 238.37
Net Site Energy | 1152.53 | 238.37 | 238.37
Total Source Energy | 3142.6 | 649.95 | 649.95
Net Source Energy | 3142.6 | 649.95 | 649.95
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 384.8 | 0 | 0 | 0 | 0
Cooling | 6.95 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 545.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 96.22 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 15.09 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 767.74 | 384.8 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 11.8401 | 47.39 | 8.07
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 15.06 |  | 0
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 9.68 |  | 2.56
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.37 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.37 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
OFFICE_WALL_SOUTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 180 | 90 | S
OFFICE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 0 | 90 | N
OFFICE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 236.88 | 0 | 180
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS | 0.8 | 0.641 | 0.71 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.3 | 3.242 | 6.3 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_WEST_1 | EXT-WALLS | 0.8 | 0.641 | 0.71 | 182.07 | 270 | 90 | W
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOFS | 0.3 | 0.369 | 0.4 | 1393.41 | 0 | 0
BULKSTORAGE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOFS | 0.3 | 0.369 | 0.4 | 3204.84 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW_SOUTH | 5.58 | 5.58 | 3.18 | 0.501 | 0.622 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW_SOUTH | 5.58 | 5.58 | 3.18 | 0.501 | 0.622 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW_WEST | 3.25 | 3.25 | 3.18 | 0.501 | 0.622 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW_WEST | 3.25 | 3.25 | 3.18 | 0.501 | 0.622 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 3.18 | 0.501 | 0.622
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 3.18 | 0.501 | 0.622
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13166.74 | 10344.71 | 2822.03 | 0.79 | 3.99
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 77904.1 | 53840.05 | 24064.05 | 0.69 | 3.14
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 71651.03 | 0.8
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 17960.8 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 111407.18 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 1.14 | 105.9 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.77 | 874.11 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 3.33 | 3641.24 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 29185.1428 | 47.6675 | 127.0658 | 0 | 0.0004 | 29244.8886 | 12125.6779
February | 24408.5125 | 40.8778 | 112.3351 | 0 | 0.0003 | 25856.1823 | 10237.8529
March | 25766.0725 | 44.5877 | 127.1939 | 0 | 0.0004 | 29278.4572 | 10944.6017
April | 21104.5165 | 37.8717 | 112.2791 | 0 | 0.0003 | 25847.1875 | 9093.6599
May | 21643.347 | 39.3482 | 118.2007 | 0 | 0.0004 | 27211.0698 | 9374.56
June | 21782.4274 | 39.6623 | 119.3276 | 0 | 0.0004 | 27470.5618 | 9440.6589
July | 21606.7982 | 39.3437 | 118.3726 | 0 | 0.0004 | 27250.719 | 9364.6542
August | 22951.8665 | 41.7927 | 125.7402 | 0 | 0.0004 | 28946.8083 | 9947.6009
September | 20713.4359 | 37.708 | 113.4247 | 0 | 0.0003 | 26111.6337 | 8976.6038
October | 22132.5262 | 39.9921 | 119.4011 | 0 | 0.0004 | 27487.0952 | 9562.9786
November | 23742.4602 | 41.6468 | 120.5666 | 0 | 0.0004 | 27753.7321 | 10138.6601
December | 27347.0554 | 45.3893 | 123.4025 | 0 | 0.0004 | 28402.9396 | 11431.2082
Annual Sum or Average | 282384.1613 | 495.8878 | 1437.3099 | 0 | 0.0044 | 330861.2752 | 120638.7173
Minimum of Months | 20713.4359 | 37.708 | 112.2791 | 0 | 0.0003 | 25847.1875 | 8976.6038
Maximum of Months | 29185.1428 | 47.6675 | 127.1939 | 0 | 0.0004 | 29278.4572 | 12125.6779
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 67860600000 | 66788.919 | 27-JAN-16:00 | 49331.035 | 9104.406 | 2228.853 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 59997300000 | 65333.972 | 01-FEB-16:00 | 49331.035 | 9104.406 | 773.906 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 67938500000 | 59822.278 | 03-MAR-09:09 | 49331.035 | 9104.406 | 1386.836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 59976500000 | 58968.644 | 21-APR-08:09 | 49331.035 | 9104.406 | 533.202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 63141200000 | 59924.307 | 05-MAY-13:00 | 49331.035 | 9104.406 | 397.875 | 0 | 1090.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 63743400000 | 74651.518 | 08-JUN-12:00 | 49331.035 | 9104.406 | 2409.739 | 0 | 13806.337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 63233200000 | 78668.639 | 03-JUL-14:00 | 49331.035 | 9104.406 | 2933.349 | 0 | 17299.848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 67168900000 | 76277.471 | 04-AUG-15:00 | 49331.035 | 9104.406 | 2698.91 | 0 | 15143.119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 60590100000 | 64881.156 | 05-SEP-14:00 | 49331.035 | 9104.406 | 1126.435 | 0 | 5319.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 63781700000 | 65103.201 | 31-OCT-16:49 | 49331.035 | 9104.406 | 189.268 | 0 | 353.867 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 64400400000 | 65072.701 | 27-NOV-16:00 | 49331.035 | 9104.406 | 512.635 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 65906900000 | 65818.808 | 14-DEC-16:00 | 49331.035 | 9104.406 | 1258.742 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 767739000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 59976500000 | 58968.644 |  | 49331.035 | 9104.406 | 189.268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 67938500000 | 78668.639 |  | 49331.035 | 9104.406 | 2933.349 | 0 | 17299.848 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 11455.66 | 3162.36 | 0 | 14618.01
Cost per Total Building Area ($/m2) | 2.37 | 0.65 | 0 | 3.02
Cost per Net Conditioned Building Area ($/m2) | 2.37 | 0.65 | 0 | 3.02

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1072.43 | 221.8 | 221.8
Net Site Energy | 1072.43 | 221.8 | 221.8
Total Source Energy | 2870.31 | 593.64 | 593.64
Net Source Energy | 2870.31 | 593.64 | 593.64
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 309.08 | 0 | 0 | 0 | 0
Cooling | 3.44 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 545.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 96.16 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 14.27 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 763.35 | 309.08 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 11.8401 | 47.39 | 8.07
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 15.06 |  | 0
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 9.68 |  | 2.56
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.37 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.37 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
OFFICE_WALL_SOUTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 180 | 90 | S
OFFICE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 0 | 90 | N
OFFICE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 236.88 | 0 | 180
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS | 0.8 | 0.641 | 0.71 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.3 | 3.242 | 6.3 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_WEST_1 | EXT-WALLS | 0.8 | 0.641 | 0.71 | 182.07 | 270 | 90 | W
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOFS | 0.3 | 0.369 | 0.4 | 1393.41 | 0 | 0
BULKSTORAGE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOFS | 0.3 | 0.369 | 0.4 | 3204.84 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW_SOUTH | 5.58 | 5.58 | 3.18 | 0.501 | 0.622 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW_SOUTH | 5.58 | 5.58 | 3.18 | 0.501 | 0.622 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW_WEST | 3.25 | 3.25 | 3.18 | 0.501 | 0.622 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW_WEST | 3.25 | 3.25 | 3.18 | 0.501 | 0.622 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 3.18 | 0.501 | 0.622
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 3.18 | 0.501 | 0.622
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12756.3 | 10187.89 | 2568.41 | 0.8 | 4.03
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 57713.72 | 46093.36 | 11620.35 | 0.8 | 3.47
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 47329.75 | 0.8
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 16512.42 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 96667.06 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.77 | 877.87 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 3.49 | 3812.91 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 21715.0616 | 34.7372 | 81.4226 | 0 | 0.0003 | 84645.7132 | 8989.5363
February | 18547.6046 | 30.1893 | 72.355 | 0 | 0.0003 | 75223.2272 | 7729.1906
March | 19889.1606 | 33.2353 | 82.2564 | 0 | 0.0003 | 85523.4899 | 8372.8412
April | 16521.8985 | 28.4601 | 72.9395 | 0 | 0.0003 | 75842.5016 | 7038.8393
May | 16898.5492 | 29.5036 | 76.7385 | 0 | 0.0003 | 79795.3214 | 7238.0183
June | 16493.6569 | 28.9194 | 75.5639 | 0 | 0.0003 | 78574.7332 | 7076.6292
July | 16278.1411 | 28.5606 | 74.6797 | 0 | 0.0003 | 77655.36 | 6986.0303
August | 17671.9952 | 31.0057 | 81.0721 | 0 | 0.0003 | 84302.4832 | 7584.1855
September | 16018.8325 | 28.0696 | 73.295 | 0 | 0.0003 | 76215.2625 | 6871.2088
October | 17336.9842 | 30.0358 | 77.4668 | 0 | 0.0003 | 80551.1456 | 7402.9263
November | 19070.081 | 31.7837 | 78.4202 | 0 | 0.0003 | 81534.376 | 8019.898
December | 21490.5019 | 34.2365 | 79.8147 | 0 | 0.0003 | 82973.117 | 8882.6944
Annual Sum or Average | 217932.4674 | 368.7369 | 926.0246 | 0 | 0.0036 | 962836.7308 | 92191.9982
Minimum of Months | 16018.8325 | 28.0696 | 72.355 | 0 | 0.0003 | 75223.2272 | 6871.2088
Maximum of Months | 21715.0616 | 34.7372 | 82.2564 | 0 | 0.0003 | 85523.4899 | 8989.5363
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 67108100000 | 66334.936 | 05-JAN-16:00 | 49331.035 | 9104.406 | 1774.87 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 59637900000 | 61280.23 | 15-FEB-09:09 | 49331.035 | 9104.406 | 2844.789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 67804100000 | 60339.057 | 02-MAR-09:09 | 49331.035 | 9104.406 | 1903.615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 60128800000 | 59554.122 | 04-APR-08:09 | 49331.035 | 9104.406 | 1118.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 63262700000 | 59659.573 | 23-MAY-15:00 | 49331.035 | 9104.406 | 356.595 | 0 | 867.536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 62295000000 | 67718.11 | 28-JUN-13:00 | 49331.035 | 9104.406 | 1951.928 | 0 | 7330.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 61566100000 | 73461.68 | 17-JUL-15:00 | 49331.035 | 9104.406 | 3048.549 | 0 | 11977.689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 66836000000 | 72422.801 | 30-AUG-13:00 | 49331.035 | 9104.406 | 2797.3 | 0 | 11190.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 60424400000 | 63212.022 | 01-SEP-15:00 | 49331.035 | 9104.406 | 1093.395 | 0 | 3683.185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 63861900000 | 64740.052 | 30-OCT-16:00 | 49331.035 | 9104.406 | 106.906 | 0 | 73.08 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 64641400000 | 65380.33 | 17-NOV-16:00 | 49331.035 | 9104.406 | 820.264 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 65782100000 | 66918.077 | 01-DEC-16:00 | 49331.035 | 9104.406 | 2358.011 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 763349000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 59637900000 | 59554.122 |  | 49331.035 | 9104.406 | 106.906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 67804100000 | 73461.68 |  | 49331.035 | 9104.406 | 3048.549 | 0 | 11977.689 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 8022.8 | 2113.64 | 0 | 10136.44
Cost per Total Building Area ($/m2) | 1.66 | 0.44 | 0 | 2.1
Cost per Net Conditioned Building Area ($/m2) | 1.66 | 0.44 | 0 | 2.1

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1407.88 | 291.18 | 291.18
Net Site Energy | 1407.88 | 291.18 | 291.18
Total Source Energy | 3370.72 | 697.13 | 697.13
Net Source Energy | 3370.72 | 697.13 | 697.13
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 626.09 | 0 | 0 | 0 | 0
Cooling | 4.26 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 545.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 96.15 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 31.9 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 781.8 | 626.09 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 11.8401 | 47.39 | 8.07
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 15.06 |  | 0
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 9.68 |  | 2.56
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.37 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.37 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
OFFICE_WALL_SOUTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 180 | 90 | S
OFFICE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 0 | 90 | N
OFFICE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 236.88 | 0 | 180
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS | 0.8 | 0.641 | 0.71 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.3 | 3.242 | 6.3 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_WEST_1 | EXT-WALLS | 0.8 | 0.641 | 0.71 | 182.07 | 270 | 90 | W
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOFS | 0.3 | 0.369 | 0.4 | 1393.41 | 0 | 0
BULKSTORAGE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOFS | 0.3 | 0.369 | 0.4 | 3204.84 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW_SOUTH | 5.58 | 5.58 | 3.18 | 0.501 | 0.622 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW_SOUTH | 5.58 | 5.58 | 3.18 | 0.501 | 0.622 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW_WEST | 3.25 | 3.25 | 3.18 | 0.501 | 0.622 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW_WEST | 3.25 | 3.25 | 3.18 | 0.501 | 0.622 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 3.18 | 0.501 | 0.622
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 3.18 | 0.501 | 0.622
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12877.53 | 10270.37 | 2607.16 | 0.8 | 4.04
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 88821.33 | 62378.73 | 26442.6 | 0.7 | 3.63
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 114712.46 | 0.8
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20060.32 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 130878 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 2.12 | 197.29 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.78 | 883.53 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 3.96 | 7427.74 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 26731.8623 | 39.0111 | 48.1399 | 0 | 0.0004 | 31608.5237 | 10661.5031
February | 20385.9278 | 31.2994 | 41.7566 | 0 | 0.0003 | 27426.7578 | 8278.6374
March | 18488.8265 | 30.7586 | 45.5939 | 0 | 0.0003 | 29959.9493 | 7734.95
April | 13920.2185 | 24.737 | 39.4688 | 0 | 0.0003 | 25942.2029 | 5974.56
May | 13863.3156 | 25.24 | 41.2744 | 0 | 0.0003 | 27131.3005 | 6007.8761
June | 13852.6253 | 25.2765 | 41.4249 | 0 | 0.0003 | 27230.469 | 6008.5971
July | 13410.1133 | 24.4708 | 40.1073 | 0 | 0.0003 | 26364.3159 | 5816.822
August | 14629.9189 | 26.6969 | 43.7563 | 0 | 0.0003 | 28762.9813 | 6345.9529
September | 13236.2368 | 24.1269 | 39.5007 | 0 | 0.0003 | 25965.5094 | 5738.8611
October | 14760.6967 | 26.3141 | 42.1239 | 0 | 0.0003 | 27687.6534 | 6343.2781
November | 17575.4544 | 29.3047 | 43.5551 | 0 | 0.0003 | 28620.5493 | 7359.1042
December | 23133.419 | 35.096 | 46.011 | 0 | 0.0004 | 30218.8692 | 9354.0671
Annual Sum or Average | 203988.6151 | 342.332 | 512.7128 | 0 | 0.0038 | 336919.0818 | 85624.209
Minimum of Months | 13236.2368 | 24.1269 | 39.4688 | 0 | 0.0003 | 25942.2029 | 5738.8611
Maximum of Months | 26731.8623 | 39.0111 | 48.1399 | 0 | 0.0004 | 31608.5237 | 10661.5031
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 73345200000 | 69773.432 | 04-JAN-16:00 | 49331.035 | 9104.406 | 5213.366 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 63641700000 | 63975.531 | 03-FEB-09:09 | 49331.035 | 9104.406 | 5540.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 69519800000 | 61584.073 | 13-MAR-08:09 | 49331.035 | 9104.406 | 3148.632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 60196900000 | 59677.66 | 04-APR-08:09 | 49331.035 | 9104.406 | 1242.219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 62956100000 | 59912.123 | 15-MAY-14:00 | 49331.035 | 9104.406 | 405.331 | 0 | 1071.351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 63186300000 | 75018.194 | 30-JUN-15:30 | 49331.035 | 9104.406 | 3920.434 | 0 | 12662.318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 61176400000 | 72074.086 | 13-JUL-15:00 | 49331.035 | 9104.406 | 3281.052 | 0 | 10357.592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 66742300000 | 72584.87 | 25-AUG-15:00 | 49331.035 | 9104.406 | 3421.286 | 0 | 10728.142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 60251000000 | 60338.916 | 14-SEP-14:00 | 49331.035 | 9104.406 | 504.897 | 0 | 1398.578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 64247100000 | 64793.812 | 31-OCT-16:00 | 49331.035 | 9104.406 | 233.746 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 66411800000 | 67023.536 | 27-NOV-16:00 | 49331.035 | 9104.406 | 2463.47 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 70120600000 | 67855.316 | 29-DEC-16:00 | 49331.035 | 9104.406 | 3295.249 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 781795000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 60196900000 | 59677.66 |  | 49331.035 | 9104.406 | 233.746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 73345200000 | 75018.194 |  | 49331.035 | 9104.406 | 5540.089 | 0 | 12662.318 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 14220.49 | 4961.94 | 0 | 19182.42
Cost per Total Building Area ($/m2) | 2.94 | 1.03 | 0 | 3.97
Cost per Net Conditioned Building Area ($/m2) | 2.94 | 1.03 | 0 | 3.97

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1278.8 | 264.48 | 264.48
Net Site Energy | 1278.8 | 264.48 | 264.48
Total Source Energy | 3246.32 | 671.4 | 671.4
Net Source Energy | 3246.32 | 671.4 | 671.4
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 502.85 | 0 | 0 | 0 | 0
Cooling | 1.39 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 545.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 96.13 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 28.96 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 775.95 | 502.85 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 11.8401 | 47.39 | 8.07
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 15.06 |  | 0
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 9.68 |  | 2.56
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.37 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.37 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
OFFICE_WALL_SOUTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 180 | 90 | S
OFFICE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 0 | 90 | N
OFFICE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 236.88 | 0 | 180
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS | 0.8 | 0.641 | 0.71 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.3 | 3.242 | 6.3 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_WEST_1 | EXT-WALLS | 0.8 | 0.641 | 0.71 | 182.07 | 270 | 90 | W
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 39.02 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOFS | 0.3 | 0.369 | 0.4 | 1393.41 | 0 | 0
BULKSTORAGE_WALL_EAST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS | 0.8 | 0.641 | 0.71 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS | 0.8 | 0.641 | 0.71 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOFS | 0.3 | 0.369 | 0.4 | 3204.84 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW_SOUTH | 5.58 | 5.58 | 3.18 | 0.501 | 0.622 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW_SOUTH | 5.58 | 5.58 | 3.18 | 0.501 | 0.622 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW_WEST | 3.25 | 3.25 | 3.18 | 0.501 | 0.622 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW_WEST | 3.25 | 3.25 | 3.18 | 0.501 | 0.622 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 3.18 | 0.501 | 0.622
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 3.18 | 0.501 | 0.622
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14411.2 | 11509.58 | 2901.62 | 0.8 | 4.03
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 72656.48 | 58027.48 | 14629 | 0.8 | 4.18
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 110517.59 | 0.8
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 19888.88 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 128482.94 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 2.32 | 215.63 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.87 | 991.76 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 4.39 | 8234.05 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 24483.2361 | 36.9791 | 53.4748 | 0 | 0.0004 | 1267690 | 9900.0112
February | 19738.613 | 30.802 | 46.6888 | 0 | 0.0003 | 1107020 | 8077.0877
March | 18856.578 | 31.2816 | 51.3148 | 0 | 0.0004 | 1217050 | 7895.5664
April | 15389.8914 | 26.3819 | 44.9593 | 0 | 0.0003 | 1066450 | 6526.2901
May | 15099.3935 | 26.5879 | 46.6569 | 0 | 0.0003 | 1106830 | 6471.1579
June | 14654.9324 | 25.9718 | 45.8856 | 0 | 0.0003 | 1088550 | 6296.7676
July | 14184.2396 | 25.1769 | 44.554 | 0 | 0.0003 | 1056970 | 6098.3237
August | 15440.4832 | 27.3998 | 48.4749 | 0 | 0.0003 | 1149990 | 6637.7597
September | 14320.6405 | 25.336 | 44.6824 | 0 | 0.0003 | 1060000 | 6148.9477
October | 16047.0573 | 27.781 | 47.8651 | 0 | 0.0003 | 1135420 | 6831.3232
November | 18330.7935 | 30.2576 | 49.3353 | 0 | 0.0003 | 1170080 | 7660.7468
December | 22855.0621 | 35.0309 | 51.7664 | 0 | 0.0004 | 1227290 | 9291.0333
Annual Sum or Average | 209400.9205 | 348.9865 | 575.6585 | 0 | 0.004 | 13653300 | 87835.0155
Minimum of Months | 14184.2396 | 25.1769 | 44.554 | 0 | 0.0003 | 1056970 | 6098.3237
Maximum of Months | 24483.2361 | 36.9791 | 53.4748 | 0 | 0.0004 | 1267690 | 9900.0112
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 72045800000 | 68795.911 | 06-JAN-16:00 | 49331.035 | 9104.406 | 4235.845 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 62914600000 | 64441.878 | 27-FEB-09:09 | 49331.035 | 9104.406 | 6006.436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 69167900000 | 61935.102 | 03-MAR-09:09 | 49331.035 | 9104.406 | 3499.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 60609100000 | 60359.504 | 04-APR-08:09 | 49331.035 | 9104.406 | 1924.062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 62903700000 | 59046.811 | 12-MAY-08:09 | 49331.035 | 9104.406 | 611.369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 61865100000 | 69167.272 | 30-JUN-14:00 | 49331.035 | 9104.406 | 3301.559 | 0 | 7430.271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 60070000000 | 70567.539 | 21-JUL-15:00 | 49331.035 | 9104.406 | 3791.663 | 0 | 8340.434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 65356400000 | 65531.346 | 09-AUG-15:00 | 49331.035 | 9104.406 | 2205.644 | 0 | 4890.261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 60242500000 | 59656.351 | 01-SEP-15:00 | 49331.035 | 9104.406 | 352.093 | 0 | 868.816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 64528700000 | 59972.03 | 16-OCT-08:09 | 49331.035 | 9104.406 | 1536.589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 66498300000 | 65976.76 | 29-NOV-16:00 | 49331.035 | 9104.406 | 1416.694 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 69750000000 | 69292.162 | 11-DEC-16:00 | 49331.035 | 9104.406 | 4732.095 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 775952000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 60070000000 | 59046.811 |  | 49331.035 | 9104.406 | 352.093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 72045800000 | 70567.539 |  | 49331.035 | 9104.406 | 6006.436 | 0 | 8340.434 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 17446.85 | 3977.11 | 0 | 21423.96
Cost per Total Building Area ($/m2) | 3.61 | 0.82 | 0 | 4.43
Cost per Net Conditioned Building Area ($/m2) | 3.61 | 0.82 | 0 | 4.43

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1486.08 | 307.35 | 307.35
Net Site Energy | 1486.08 | 307.35 | 307.35
Total Source Energy | 3454.94 | 714.55 | 714.55
Net Source Energy | 3454.94 | 714.55 | 714.55
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 704.79 | 0 | 0 | 0 | 0
Cooling | 0.63 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 545.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 96.08 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 35.11 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 781.29 | 704.79 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 11.8401 | 47.39 | 8.07
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 15.06 |  | 0
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 9.68 |  | 2.56
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.37 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.37 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
OFFICE_WALL_SOUTH | EXT-WALLS | 0.8 | 0.324 | 0.34 | 110.54 | 180 | 90 | S
OFFICE_WALL_EAST | EXT-WALLS | 0.8 | 0.324 | 0.34 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS | 0.8 | 0.324 | 0.34 | 110.54 | 0 | 90 | N
OFFICE_WALL_WEST | EXT-WALLS | 0.8 | 0.324 | 0.34 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 236.88 | 0 | 180
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS | 0.8 | 0.324 | 0.34 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_EAST | EXT-WALLS | 0.8 | 0.324 | 0.34 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.3 | 3.242 | 6.3 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_WEST_1 | EXT-WALLS | 0.8 | 0.324 | 0.34 | 182.07 | 270 | 90 | W
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS | 0.8 | 0.324 | 0.34 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS | 0.8 | 0.324 | 0.34 | 39.02 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOFS | 0.3 | 0.369 | 0.4 | 1393.41 | 0 | 0
BULKSTORAGE_WALL_EAST | EXT-WALLS | 0.8 | 0.324 | 0.34 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS | 0.8 | 0.324 | 0.34 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS | 0.8 | 0.324 | 0.34 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOFS | 0.3 | 0.369 | 0.4 | 3204.84 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW_SOUTH | 5.58 | 5.58 | 3.18 | 0.501 | 0.49 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW_SOUTH | 5.58 | 5.58 | 3.18 | 0.501 | 0.49 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW_WEST | 3.25 | 3.25 | 3.18 | 0.501 | 0.49 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW_WEST | 3.25 | 3.25 | 3.18 | 0.501 | 0.49 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 3.18 | 0.501 | 0.49
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 3.18 | 0.501 | 0.49
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 11054.56 | 8828.78 | 2225.78 | 0.8 | 4.06
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 89670.63 | 63211.37 | 26459.26 | 0.7 | 3.64
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 119320.03 | 0.8
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 17458.96 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 131500.32 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 2.23 | 207.49 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.67 | 774.59 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 4.04 | 7571.57 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 25612.334 | 37.9502 | 47.9894 | 0 | 0.0004 | 31513.2264 | 10269.7664
February | 21731.2857 | 32.687 | 42.3046 | 0 | 0.0003 | 27783.0102 | 8760.1713
March | 20105.1958 | 32.4819 | 46.4355 | 0 | 0.0003 | 30508.647 | 8318.865
April | 14894.9876 | 25.7712 | 39.9596 | 0 | 0.0003 | 26262.0391 | 6326.2032
May | 14135.9618 | 25.4869 | 41.2738 | 0 | 0.0003 | 27130.0112 | 6102.1862
June | 13499.7454 | 24.6111 | 40.2998 | 0 | 0.0003 | 26490.7697 | 5853.4826
July | 13051.311 | 23.8126 | 39.023 | 0 | 0.0003 | 25651.5601 | 5660.8588
August | 14293.7006 | 26.0689 | 42.7035 | 0 | 0.0003 | 28070.8889 | 6198.7277
September | 13352.1137 | 24.2285 | 39.4895 | 0 | 0.0003 | 25957.7166 | 5778.6207
October | 15150.5485 | 26.7445 | 42.3747 | 0 | 0.0003 | 27851.4928 | 6485.5167
November | 18522.1225 | 30.3368 | 44.1223 | 0 | 0.0003 | 28990.8259 | 7703.2698
December | 23629.8221 | 35.6745 | 46.4296 | 0 | 0.0004 | 30492.8292 | 9538.0943
Annual Sum or Average | 207979.1286 | 345.8541 | 512.4052 | 0 | 0.0038 | 336703.017 | 86995.7627
Minimum of Months | 13051.311 | 23.8126 | 39.023 | 0 | 0.0003 | 25651.5601 | 5660.8588
Maximum of Months | 25612.334 | 37.9502 | 47.9894 | 0 | 0.0004 | 31513.2264 | 10269.7664
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 73124100000 | 69281.807 | 09-JAN-16:00 | 49331.035 | 9104.406 | 4721.74 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 64468400000 | 64913.891 | 01-FEB-09:09 | 49331.035 | 9104.406 | 6478.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 70793000000 | 63106.359 | 07-MAR-09:09 | 49331.035 | 9104.406 | 4670.917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 60939100000 | 61414.066 | 03-APR-08:09 | 49331.035 | 9104.406 | 2978.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 62953100000 | 59494.719 | 01-MAY-08:09 | 49331.035 | 9104.406 | 1059.277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 61469800000 | 59711.022 | 14-JUN-14:00 | 49331.035 | 9104.406 | 364.516 | 0 | 911.064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 59522500000 | 67925.323 | 06-JUL-15:00 | 49331.035 | 9104.406 | 2355.279 | 0 | 7134.603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 65136400000 | 61412.313 | 14-AUG-15:30 | 49331.035 | 9104.406 | 797.343 | 0 | 2179.528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 60232900000 | 59268.078 | 07-SEP-14:00 | 49331.035 | 9104.406 | 264.268 | 0 | 568.368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 64627300000 | 65326.793 | 31-OCT-16:00 | 49331.035 | 9104.406 | 766.727 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 67271000000 | 67758.859 | 24-NOV-16:00 | 49331.035 | 9104.406 | 3198.793 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 70756300000 | 68050.647 | 20-DEC-16:00 | 49331.035 | 9104.406 | 3490.581 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 781294000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 59522500000 | 59268.078 |  | 49331.035 | 9104.406 | 264.268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 73124100000 | 69281.807 |  | 49331.035 | 9104.406 | 6478.45 | 0 | 7134.603 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 13938.4 | 5562.95 | 0 | 19501.35
Cost per Total Building Area ($/m2) | 2.88 | 1.15 | 0 | 4.03
Cost per Net Conditioned Building Area ($/m2) | 2.88 | 1.15 | 0 | 4.03

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2335.92 | 483.11 | 483.11
Net Site Energy | 2335.92 | 483.11 | 483.11
Total Source Energy | 4551.59 | 941.36 | 941.36
Net Source Energy | 4551.59 | 941.36 | 941.36
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1529.16 | 0 | 0 | 0 | 0
Cooling | 0.08 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 545.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 95.49 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 61.71 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 806.76 | 1529.16 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 11.8401 | 47.39 | 8.07
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 15.06 |  | 0
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 9.68 |  | 2.56
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.37 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 11.3363 | 967.37 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
OFFICE_WALL_SOUTH | EXT-WALLS | 0.8 | 0.324 | 0.34 | 110.54 | 180 | 90 | S
OFFICE_WALL_EAST | EXT-WALLS | 0.8 | 0.324 | 0.34 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS | 0.8 | 0.324 | 0.34 | 110.54 | 0 | 90 | N
OFFICE_WALL_WEST | EXT-WALLS | 0.8 | 0.324 | 0.34 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 236.88 | 0 | 180
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS | 0.8 | 0.324 | 0.34 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_EAST | EXT-WALLS | 0.8 | 0.324 | 0.34 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.3 | 3.242 | 6.3 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_WEST_1 | EXT-WALLS | 0.8 | 0.324 | 0.34 | 182.07 | 270 | 90 | W
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS | 0.8 | 0.324 | 0.34 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS | 0.8 | 0.324 | 0.34 | 39.02 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOFS | 0.3 | 0.278 | 0.29 | 1393.41 | 0 | 0
BULKSTORAGE_WALL_EAST | EXT-WALLS | 0.8 | 0.324 | 0.34 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS | 0.8 | 0.324 | 0.34 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS | 0.8 | 0.324 | 0.34 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.45 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOFS | 0.3 | 0.278 | 0.29 | 3204.84 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW_SOUTH | 5.58 | 5.58 | 2.58 | 0.504 | 0.49 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW_SOUTH | 5.58 | 5.58 | 2.58 | 0.504 | 0.49 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW_WEST | 3.25 | 3.25 | 2.58 | 0.504 | 0.49 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW_WEST | 3.25 | 3.25 | 2.58 | 0.504 | 0.49 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 2.58 | 0.504 | 0.49
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 2.58 | 0.504 | 0.49
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13207.75 | 10548.44 | 2659.31 | 0.8 | 4.04
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 128891.27 | 87141.22 | 41750.05 | 0.68 | 3.51
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 154409.39 | 0.8
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21828.43 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 175476 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 2.68 | 249.11 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.8 | 908.94 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 5.19 | 9737.23 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 35356.8618 | 37.5583 | 114.3882 | 0 | 0.0004 | 22938.378 | 13077.6763
February | 29424.8129 | 31.4478 | 99.1893 | 0 | 0.0004 | 19891.8065 | 10912.9192
March | 23713.559 | 26.5403 | 104.9669 | 0 | 0.0004 | 21058.1234 | 8978.8679
April | 15298.2899 | 18.0438 | 87.0047 | 0 | 0.0003 | 17459.1154 | 5934.3937
May | 12160.8605 | 15.1329 | 85.6804 | 0 | 0.0003 | 17196.3775 | 4838.8529
June | 11414.2918 | 14.285 | 82.1187 | 0 | 0.0003 | 16481.7761 | 4554.2823
July | 11014.9981 | 13.7931 | 79.4078 | 0 | 0.0003 | 15937.6906 | 4396.1542
August | 12504.7777 | 15.6398 | 89.7548 | 0 | 0.0003 | 18014.348 | 4987.8444
September | 12609.3015 | 15.5337 | 85.5498 | 0 | 0.0003 | 17169.6685 | 4993.0879
October | 17599.6108 | 20.6017 | 96.8198 | 0 | 0.0003 | 19428.0973 | 6803.0292
November | 25624.0003 | 28.2908 | 105.3145 | 0 | 0.0004 | 21125.9823 | 9642.59
December | 30911.4658 | 33.3604 | 110.9747 | 0 | 0.0004 | 22257.3566 | 11514.107
Annual Sum or Average | 237632.8301 | 270.2275 | 1141.1696 | 0 | 0.004 | 228958.7202 | 90633.8049
Minimum of Months | 11014.9981 | 13.7931 | 79.4078 | 0 | 0.0003 | 15937.6906 | 4396.1542
Maximum of Months | 35356.8618 | 37.5583 | 114.3882 | 0 | 0.0004 | 22938.378 | 13077.6763
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 80825900000 | 73626.828 | 13-JAN-09:09 | 49331.035 | 9104.406 | 9066.762 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 70090900000 | 73338.512 | 03-FEB-09:09 | 49331.035 | 9104.406 | 8778.446 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 74200600000 | 65419.443 | 14-MAR-08:09 | 49331.035 | 9104.406 | 6984.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 61519100000 | 62183.454 | 10-APR-08:09 | 49331.035 | 9104.406 | 3748.012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 60593300000 | 58874.353 | 01-MAY-08:09 | 49331.035 | 9104.406 | 438.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 58075300000 | 59235.653 | 21-JUN-15:00 | 49331.035 | 9104.406 | 253.972 | 0 | 546.239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 56158200000 | 59336.736 | 12-JUL-15:00 | 49331.035 | 9104.406 | 285.21 | 0 | 616.085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 63475500000 | 59141.092 | 15-AUG-14:50 | 49331.035 | 9104.406 | 230.846 | 0 | 474.804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 60499200000 | 60063.286 | 29-SEP-08:09 | 49331.035 | 9104.406 | 1627.844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 68457000000 | 68637.331 | 27-OCT-08:09 | 49331.035 | 9104.406 | 4077.264 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 74439700000 | 69891.197 | 09-NOV-09:09 | 49331.035 | 9104.406 | 5331.131 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 78426200000 | 72726.642 | 29-DEC-09:09 | 49331.035 | 9104.406 | 8166.576 | 0 | 0 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 806761000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 56158200000 | 58874.353 |  | 49331.035 | 9104.406 | 230.846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 80825900000 | 73626.828 |  | 49331.035 | 9104.406 | 9066.762 | 0 | 616.085 | 6124.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 23892.34 | 6278.08 | 0 | 30170.42
Cost per Total Building Area ($/m2) | 4.94 | 1.3 | 0 | 6.24
Cost per Net Conditioned Building Area ($/m2) | 4.94 | 1.3 | 0 | 6.24

## Picture
DOE Commercial Building Benchmark - Warehouse

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 64 | 3337.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 64 | 3337.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 9.8 | 54.22 | 2827.19
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.24 | 0.24 | 0.24 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.82
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.7 | 0.9 | 0.9 | 0.9 | 0.5 | 0.85 | 0.85 | 0.85 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8 | 35.2 | 1835.43
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 10.1 | 56.3 | 2935.64
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.4
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 3.5 | 182.5
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INFIL_SCH | Fraction | Through 12/31 | WD, SummerDesign | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
|  |  | Sat | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
|  |  | Sat | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.07 | 0.07 | 0.1 | 0.3 | 0.36 | 0.36 | 0.46 | 0.57 | 0.43 | 0.38 | 0.4 | 0.3 | 0.18 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 4.29 | 22.88 | 1193.03
|  |  | Sat, WinterDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.06 | 0.12 | 0.12 | 0.17 | 0.04 | 0.04 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.91
|  |  | Sun, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.04 | 0.04 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.52
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 432.5 | 2956 | 154134.29
|  |  | SummerDesign | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 372
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Sat | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 421.5
|  |  | Sun, Hol, Other | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 372
HTGSETP_FineStorage_SCH | Temperature | Through 12/31 | All | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 372 | 2604 | 135780
HTGSETP_BulkStorage_SCH | Temperature | Through 12/31 | All | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 172.8 | 1209.6 | 63072
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 660 | 4692 | 244654.29
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 672
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
CLGSETP_FineStorage_SCH | Temperature | Through 12/31 | All | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 640.8 | 4485.6 | 233892
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 58 | 3024.29
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
|  | Through 9/30 | All | [24 empty] | 24 | 168 | bar: 1 to 24
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -240 | -1680 | -87600
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600