## Calculations (English Units)
About the Solar Hot Water System Size and Life Cycle Costs spreadsheet:
This tool calculates solar hot water system sizing and life cycle costs given site-specific inputs. Two scenarios can be evaluated in parallel, depending on the solar fraction(s) of interest (solar fraction is the fraction of load met by solar). • In Scenario 1, the default solar fraction is calculated given the solar resource data (columns D-E). • In Scenario 2, a user can specify their desired solar fraction (columns G-H). Cells requiring user inputs are highlighted and color-coded by data type, and additional tabs provide relevant data for reference. There is a tab for calculations in English units and another tab for calculations in metric units. • If using the metric version and fuel cost is given in English $/therm, divide by 29.3 kWh/therm to get fuel cost in $/kWh. • If using the English version and fuel cost is given in metric $/kWh, multiply by 29.3 kWh/therm to get fuel cost in $/therm. Other conversion factors may be found on the Unit Conversions tab. Check https://www.energy.gov/femp/articles/solar-hot-water-system-calculator for the most up-to-date version of this spreadsheet. See the instructions below for more details.
Instructions:
1. Input a desired solar fraction to be evaluated in cell H12.
2. Estimate the building's Daily Hot Water Use (row 15). Refer to the 'Hot Water Use' tab for benchmark values for gallons per person per day by building type. Multiply the reference value by the number of building occupants.
3. Input the following data in the Hot Water Use Information section (rows 15-20): • Daily Hot Water Use (gallons per day; use the estimate from Step 2 above) • Cold incoming water temperature (F) • Hot water delivery temperature (F) • Cost of electricity or fuel ($/therm) used for water heating (see row 2 on how to convert $/kWh to $/therm) • Thermal efficiency of the heating system (refer to 'Hot Water Use' tab)
4. Input the solar resource data (rows 25-26; maximum and average daily solar Btu/ft2/day) using the 'Resource Data' tab. Use the values corresponding to the nearest City and State.
5. Using the calculated system size(s) shown in row 28, identify the approximate unit cost(s) in $/ft2 using the 'Cost Data' tab.
6. Input the unit cost(s) into row 35 to calculate the economic results. If the Savings to Investment Ratio in row 40 is greater than 1, the project is cost effective according to federal criteria in 10 CFR 436.*
* https://www.ecfr.gov/current/title-10/chapter-II/subchapter-D/part-436
|  | Scenario 1: Calculate solar fraction using solar resource data. |  | Scenario 2: Input desired solar fraction.
|  |  |  | Solar fraction=fraction of load met by solar | 30%
|  |  | English Units |  | English Units
Hot Water Use Information
Vdaily | Daily Hot Water Use (volume/day) | 1000 | gallons/day | 1000 | gallons/day
Tcold | Cold Incoming Water Temperature | 60 | F | 60 | F
Thot | Hot Water Delivery Temperature | 140 | F | 140 | F
Qload | Equation: Building Hot Water Energy Requirement | 6.664 | therms/day | 6.664 | therms/day
cfuel | Cost of Electricity or Fuel ($/therm) Used for Water Heating | 5.28 | $/therm | 5.28 | $/therm
η heating | Thermal Efficiency of Conventional Heating System | 0.93 |  | 0.93
Stipulated Design Values: These are reasonable default values for the efficiency of the solar water heater (annual average) and the fraction of solar heat that can be used. These inputs may be changed.
η solar | Efficiency of Solar Water Heater | 0.3 |  | 0.3
% Utilization | Fraction of delivered heat that can be used. | 0.9 |  | 0.9
Solar Resource Data
IC,max | Maximum daily solar insolation on tilt=latitude. | 1934.3123 | Btu/ft2/day | 1934.3123 | Btu/ft2/day
IC,ave | Average daily solar insolation on tilt=latitude. | 1744.052 | Btu/ft2/day | 1744.052 | Btu/ft2/day
Calculated Energy Results: The following rows show the calculated system size (ft2) and energy delivery.
AC | Equation: Area of Solar Collector | 1148.384 | ft2 | 344.5152 | ft2
Qload | Equation: Annual Energy to Heat Water | 2432.36 | therms/year | 2432.36 | therms/year
Qsolar | Equation: Annual Solar Heat Delivery | 1973.8003 | therms/year | 592.1401 | therms/year
SF | Equation: Fraction of Load Provided by Solar | 0.81148 |  | 0.24344
Qsavings | Equation: Annual Savings in Heating Fuel | 2122.3659 | therms/year | 636.7098 | therms/year
Qpump | Equation: Annual Parasitic Pump Energy | 14.3017 | therms/year | 4.2905 | therms/year
Economic Results
Cunit | Unit Cost of Solar Water System | 150 | $/ft2 | 225 | $/ft2
Cinitial | Equation: Initial Cost of Solar Heating System | 172257.6058 |  | 77515.9226
Csavings | Equation: Annual Energy Cost Savings Energy Cost times (Qsavings minus Qpump) | 11130.579 |  | 3339.1737
CO&M | Annual Operation & Maintenance Cost 0.5% of initial cost per year | 861.288 |  | 387.5796
SPB (Simple Payback Period, years) | Equation: Simple Payback Period (years) | 16.7741 |  | 26.2624
SIR (Savings-to-Investment Ratio) | Equation: Savings-to-Investment Ratio | 1.0373 |  | 0.66254

## Calculations (Metric Units)
About the Solar Hot Water System Size and Life Cycle Costs spreadsheet:
This tool calculates solar hot water system sizing and life cycle costs given site-specific inputs. Two scenarios can be evaluated in parallel, depending on the solar fraction(s) of interest (solar fraction is the fraction of load met by solar). • In Scenario 1, the default solar fraction is calculated given the solar resource data (columns D-E). • In Scenario 2, a user can specify their desired solar fraction (columns G-H). Cells requiring user inputs are highlighted and color-coded by data type, and additional tabs provide relevant data for reference. There is a tab for calculations in English units and another tab for calculations in Metric units. • If using the metric version and fuel cost is given in English $/therm, divide by 29.3 kWh/therm to get fuel cost in $/kWh. • If using the English version and fuel cost is given in metric $/kWh, multiply by 29.3 kWh/therm to get fuel cost in $/therm. Other conversion factors may be found on the Unit Conversions tab. Check https://www.energy.gov/femp/articles/solar-hot-water-system-calculator for the most up-to-date version of this spreadsheet. See the instructions below for more details.
Instructions:
1. Input a desired solar fraction to be evaluated in cell H12.
2. Estimate the building's Daily Hot Water Use (row 15). Refer to the 'Hot Water Use' tab for benchmark values for liters per person per day by building type. Multiply the reference value by the number of building occupants.
3. Input the following data in the Hot Water Use Information section (rows 15-20): • Daily Hot Water Use (liters per day; use the estimate from Step 2 above) • Cold incoming water temperature (C) • Hot water delivery temperature (C) • Cost of electricity or fuel ($/kWh) used for water heating (see row 2 on how to convert $/therm to $/kWh) • Thermal efficiency of the heating system (refer to 'Hot Water Use' tab)
4. Input the solar resource data (rows 25-26; maximum and average daily solar kWh/m2/day) using the 'Resource Data' tab. Use the values corresponding to the nearest City and State.
5. Using the calculated system size(s) shown in row 28, identify the approximate unit cost(s) in $/m2 using the 'Cost Data' tab.
6. Input the unit cost(s) into row 35 to calculate the economic results. If the Savings to Investment Ratio in row 40 is greater than 1, the project is cost effective according to federal criteria in 10 CFR 436.*
* https://www.ecfr.gov/current/title-10/chapter-II/subchapter-D/part-436
|  | Scenario 1: Calculate solar fraction using solar resource data. |  | Scenario 2: Input desired solar fraction.
|  |  |  | Solar fraction=fraction of load met by solar | 30%
|  |  | Metric Units |  | Metric Units
Hot Water Use Information |  | Scenario 1 |  | Scenario 2
Vdaily | Daily Hot Water Use (volume/day) | 3785 | liters/day | 3785 | liters/day
Tcold | Cold Incoming Water Temperature | 15 | C | 15 | C
Thot | Hot Water Delivery Temperature | 60 | C | 60 | C
Qload | Equation: Building Hot Water Energy Requirement | 198.7693 | kWh/day | 198.7693 | kWh/day
cfuel | Cost of Electricity ($/kWh) or Fuel ($/therm) Used for Water Heating | 0.18 | $/kWh | 0.18 | $/kWh
η heating | Thermal Efficiency of Conventional Heating System | 0.93 |  | 0.98
Stipulated Design Values: These are reasonable default values for the efficiency of the solar water heater (annual average) and the fraction of solar heat that can be used. These inputs may be changed. |  | Scenario 1 |  | Scenario 2
η solar | Efficiency of Solar Water Heater | 0.3 |  | 0.3
% Utilization | Fraction of delivered heat that can be used. | 0.9 |  | 0.9
Solar Resource Data |  | Scenario 1 |  | Scenario 2
IC,max | Maximum daily solar insolation on tilt=latitude. | 6.1 | kWh/m2/day | 6.1 | kWh/m2/day
IC,ave | Average daily solar insolation on tilt=latitude. | 5.5 | kWh/m2/day | 5.5 | kWh/m2/day
Calculated Energy Results: The following rows show the calculated system size (m2) and energy delivery. |  | Scenario 1 |  | Scenario 2
AC | Equation: Area of Solar Collector | 108.6171 | m2 | 32.5851 | m2
Qload | Equation: Annual Energy to Heat Water | 72550.7854 | kWh/year | 72550.7854 | kWh/year
Qsolar | Equation: Annual Solar Heat Delivery | 58873.1783 | kWh/year | 17661.9535 | kWh/year
SF | Equation: Fraction of Load Provided by Solar | 0.81148 |  | 0.24344
Qsavings | Equation: Annual Savings in Heating Fuel | 63304.4928 | kWh/year | 18022.4015 | kWh/year
Qpump | Equation: Annual Parasitic Pump Energy | 396.4524 | kWh/year | 118.9357 | kWh/year
Economic Results |  | Scenario 1 |  | Scenario 2
Cunit | Unit Cost of Solar Hot Water System | 1500 | $/m2 | 2225 | $/m2
Cinitial | Equation: Initial Cost of Solar Heating System | 162925.6352 |  | 72501.9077
Csavings | Equation: Annual Energy Cost Savings Energy Cost times (Qsavings minus Qpump) | 11323.4473 |  | 3222.6238
CO&M | Annual Operation & Maintenance Cost 0.5% of initial cost per year | 814.6282 |  | 362.5095
SPB (Simple Payback Period, years) | Equation: Simple Payback Period (years) | 15.5037 |  | 25.3493
SIR (Savings-to-Investment Ratio) | Equation: Savings-to-Investment Ratio | 1.1223 |  | 0.68641

## Unit Conversions
Volume | 0.2642 | gallons/liter
Temperature | C=(F-32)*5/9
F=(C*9/5)+32
Mass | 2.2 | lbs/kg
Energy | 3412 | Btu/kWh
Area | 10.76 | ft2/m2
Energy Cost | 29.3083 | ($/therm)/($/kWh)
Solar Resource | 317.1004 | (Btu/ft2/day)/(kWh/m2/day)
Unit Cost | 0.092937 | ($/ft2)/($/m2)

## Hot Water Use
From https://www.nrel.gov/docs/fy11osti/50118.pdf
| Metric Units | English Units
Building Type | Estimated Hot Water Use Liters/Person/Day | Estimated Hot Water Use Gallons/Person/Day
House | 59.803 | 15.8
Hotel/Motel | 75.7 | 20
Hospital | 196.82 | 52
Office | 4.1635 | 1.1
Restaurant | 9.084 | 2.4
School | 1.8925 | 0.5
School with Showers | 7.1915 | 1.9
Federal gas water heater performance requirements
Energy factor of 0.67 or higher
Annual energy use of 242 therms/year or less for a 50-gallon tank
Tankless energy factor of 0.82 or higher
Federal electric water heater performance requirements
Energy factor of 0.93 or higher
Annual energy use of 4,721 kWh/yr or less for a 60+-gallon tank

## Resource Data
|  | Metric Units |  | English Units
STATE/COUNTRY | CITY | Ic,max | Ic,ave | Ic,max | Ic,ave
|  | kWh/m2/day | kWh/m2/day | Btu/ft2/day | Btu/ft2/day
Alabama | Huntsville | 5.7 | 4.8 | 1807.4721 | 1522.0818
Alaska | Anchorage | 4.6 | 3 | 1458.6617 | 951.3011
Alaska | Juneau | 4.5 | 1.1 | 1426.9517 | 348.8104
Arizona | Chandler | 6.9 | 5.4 | 2187.9926 | 1712.342
Arizona | Flagstaff | 6.7 | 4.9 | 2124.5725 | 1553.7918
Arizona | Mesa | 6.8 | 6.1 | 2156.2825 | 1934.3123
Arizona | Phoenix | 7.5 | 6.5 | 2378.2528 | 2061.1524
Arizona | Scottsdale | 7 | 6 | 2219.7026 | 1902.6022 | L
Arizona | Tucson | 7.3 | 6.5 | 2314.8327 | 2061.1524
California | Bakersfield | 7.3 | 5.7 | 2314.8327 | 1807.4721
California | Chula Vista | 6.6 | 5.5 | 2092.8625 | 1744.052
California | Fresno | 7.3 | 5.7 | 2314.8327 | 1807.4721
California | Inyokern | 7.2 | 6.3 | 2283.1227 | 1997.7323
California | Lancaster | 7.1 | 6 | 2251.4126 | 1902.6022
California | Long Beach | 6.3 | 5.6 | 1997.7323 | 1775.7621
California | Modesto | 7 | 5.1 | 2219.7026 | 1617.2119
California | Ontario | 6.2 | 5 | 1966.0223 | 1585.5019
California | Oxnard | 6.1 | 5.3 | 1934.3123 | 1680.632
California | Palmdale | 7.1 | 6.1 | 2251.4126 | 1934.3123
California | Riverside | 6.3 | 5.1 | 1997.7323 | 1617.2119
California | Sacramento | 7.2 | 5.5 | 2283.1227 | 1744.052
California | San Diego | 6.5 | 5.7 | 2061.1524 | 1807.4721
California | San Francisco | 6.8 | 5.4 | 2156.2825 | 1712.342
California | Santa Rosa | 6.9 | 5.3 | 2187.9926 | 1680.632
California | Stockton | 7.1 | 5.1 | 2251.4126 | 1617.2119
California | Truckee | 7 | 5.1 | 2219.7026 | 1617.2119
Colorado | Eagle | 6.4 | 5.5 | 2029.4424 | 1744.052
Colorado | Alamosa | 6.8 | 6.3 | 2156.2825 | 1997.7323
Colorado | Denver | 6.1 | 5.5 | 1934.3123 | 1744.052
Colorado | Fort Collins | 6.4 | 5.1 | 2029.4424 | 1617.2119
Colorado | La Junta | 6.7 | 5.2 | 2124.5725 | 1648.9219
Connecticut | Hartford | 5.4 | 4.4 | 1712.342 | 1395.2416
Delaware | Wilmington | 5.6 | 4.6 | 1775.7621 | 1458.6617
Florida | Jacksonville | 6 | 5 | 1902.6022 | 1585.5019
Florida | Miami | 6.1 | 5.2 | 1934.3123 | 1648.9219
Florida | Tampa | 6.3 | 5.3 | 1997.7323 | 1680.632
Florida | Orlando | 5.8 | 4.8 | 1839.1822 | 1522.0818
Florida | Key West | 6.4 | 5.5 | 2029.4424 | 1744.052
Florida | Fort Lauderdale | 5.9 | 5 | 1870.8922 | 1585.5019
Georgia | Atlanta | 5.8 | 5.1 | 1839.1822 | 1617.2119
Hawaii | Hilo | 5.2 | 4.8 | 1648.9219 | 1522.0818
Hawaii | Honolulu | 6.2 | 5.7 | 1966.0223 | 1807.4721
Idaho | Boise | 7 | 5.1 | 2219.7026 | 1617.2119
Illinois | Aurora | 5.3 | 3.8 | 1680.632 | 1204.9814
Illinois | Joliet | 5.5 | 4.1 | 1744.052 | 1300.1115
Illinois | Chicago | 5.7 | 4.4 | 1807.4721 | 1395.2416
Indiana | Fort Wayne | 5.6 | 4.3 | 1775.7621 | 1363.5316
Kansas | Overland Park | 5.8 | 4.5 | 1839.1822 | 1426.9517
Kansas | Wichita | 6.3 | 5.2 | 1997.7323 | 1648.9219
Kentucky | Lexington-Fayette | 5.6 | 4.5 | 1775.7621 | 1426.9517
Louisiana | Shreveport | 6 | 5.1 | 1902.6022 | 1617.2119
Louisiana | New Orleans | 5.7 | 5 | 1807.4721 | 1585.5019
Maine | Bangor | 5 | 3.7 | 1585.5019 | 1173.2714
Maryland | Baltimore | 5.6 | 4.6 | 1775.7621 | 1458.6617
Massacheusettes | Boston | 5.6 | 4.6 | 1775.7621 | 1458.6617
Michigan | Houghton | 5.6 | 4.1 | 1775.7621 | 1300.1115
Michigan | Detroit | 5.6 | 4.2 | 1775.7621 | 1331.8216
Minnesota | Duluth | 5.6 | 4.4 | 1775.7621 | 1395.2416
Mississippi | Natchez | 5.4 | 4.6 | 1712.342 | 1458.6617
Montana | Billings | 6.5 | 5 | 2061.1524 | 1585.5019
Montana | Kalispell | 6.2 | 4.1 | 1966.0223 | 1300.1115
Missouri | St. Louis | 5.9 | 4.8 | 1870.8922 | 1522.0818
Nebraska | Omaha | 6 | 4.9 | 1902.6022 | 1553.7918
Nebraska | Lincoln | 5.7 | 4.3 | 1807.4721 | 1363.5316
Nevada | Las Vegas | 7.4 | 6.5 | 2346.5428 | 2061.1524
Nevada | Reno | 7.1 | 5.8 | 2251.4126 | 1839.1822
New Hampshire | Concord | 5.6 | 4.6 | 1775.7621 | 1458.6617
New Jersey | Newwark | 5.4 | 4.5 | 1712.342 | 1426.9517
New Mexico | Albuquerque | 7.2 | 6.4 | 2283.1227 | 2029.4424
New Mexico | Las Cruces | 7.1 | 6.5 | 2251.4126 | 2061.1524
New York | Albany | 5.5 | 4.3 | 1744.052 | 1363.5316
New York | Buffalo | 5.5 | 4.1 | 1744.052 | 1300.1115
New York | New York | 5.6 | 4.6 | 1775.7621 | 1458.6617
North Carolina | Charlotte | 5.7 | 5 | 1807.4721 | 1585.5019
North Carolina | Raleigh | 5.7 | 4.7 | 1807.4721 | 1490.3717
North Carolina | Greensboro | 5.7 | 5 | 1807.4721 | 1585.5019
North Dakota | Fargo | 6 | 4.6 | 1902.6022 | 1458.6617
Ohio | Columbus | 5.4 | 4.2 | 1712.342 | 1331.8216
Oklahoma | Oklahoma City | 6.3 | 5.4 | 1997.7323 | 1712.342
Oregon | Portland | 5.8 | 3.9 | 1839.1822 | 1236.6914
Oregon | Salem | 6.1 | 4.1 | 1934.3123 | 1300.1115
Pennsylvania | Philadelphia | 5.5 | 4.6 | 1744.052 | 1458.6617
Rhode Island | Providence | 5.5 | 4.5 | 1744.052 | 1426.9517
South Carolina | Columbia | 5.9 | 5.1 | 1870.8922 | 1617.2119
South Dakota | Sioux Falls | 6.1 | 4.8 | 1934.3123 | 1522.0818
Tennessee | Memphis | 6 | 5 | 1902.6022 | 1585.5019
Texas | Amarillo | 6.4 | 5.8 | 2029.4424 | 1839.1822
Texas | Arlington | 6.2 | 4.8 | 1966.0223 | 1522.0818
Texas | Brownsville | 5.9 | 5 | 1870.8922 | 1585.5019
Texas | Dallas/Fort Worth | 6.4 | 5.4 | 2029.4424 | 1712.342
Texas | El Paso | 7.3 | 6.5 | 2314.8327 | 2061.1524
Texas | Houston | 5.5 | 4.8 | 1744.052 | 1522.0818
Texas | Laredo | 6.2 | 5 | 1966.0223 | 1585.5019
Texas | Lubbock | 6.3 | 5.8 | 1997.7323 | 1839.1822
Texas | San Antonio | 6.3 | 5.4 | 1997.7323 | 1712.342
Utah | Salt Lake City | 6.7 | 5.3 | 2124.5725 | 1680.632
Utah | Provo | 6.9 | 5 | 2187.9926 | 1585.5019
Vermont | Burlington | 5.6 | 4.3 | 1775.7621 | 1363.5316
Virginia | Richmond | 5.6 | 4.8 | 1775.7621 | 1522.0818
Virginia | Chesapeake | 5.4 | 4.5 | 1712.342 | 1426.9517
Virginia | Norfolk | 5.6 | 4.8 | 1775.7621 | 1522.0818
Washington | Yakima | 6.7 | 4.8 | 2124.5725 | 1522.0818
Washington | Seattle | 5.7 | 3.7 | 1807.4721 | 1173.2714
West Virginia | Huntington | 5.4 | 4.3 | 1712.342 | 1363.5316
Wisconsin | Madison | 5.8 | 4.5 | 1839.1822 | 1426.9517
Wyoming | Cheyenne | 6.1 | 5.3 | 1934.3123 | 1680.632
Wyoming | Dubois | 6.2 | 4.8 | 1966.0223 | 1522.0818
Australia | Canberra | 6.6 | 5.2 | 2092.8625 | 1648.9219
Austria | Vienna | 4.8 | 3.6 | 1522.0818 | 1141.5613
Azerbaijan | Baku | 5.5 | 4.2 | 1744.052 | 1331.8216
Bahamas | Nassau | 6.6 | 5.8 | 2092.8625 | 1839.1822
Bangladesh | Chittagong | 5.8 | 4.9 | 1839.1822 | 1553.7918
Bangladesh | Dhaka | 6 | 5 | 1902.6022 | 1585.5019
Belarus | Minsk | 4.6 | 2.9 | 1458.6617 | 919.5911
Belgium | Antwerp | 4.6 | 3.2 | 1458.6617 | 1014.7212
Belize | San Ignacio | 6.1 | 5.1 | 1934.3123 | 1617.2119
Bhutan | Thimpu | 5.6 | 5.2 | 1775.7621 | 1648.9219
Bolivia | Santa Cruz | 5.2 | 4.8 | 1648.9219 | 1522.0818
Bosnia | Sarajevo | 5.3 | 3.8 | 1680.632 | 1204.9814
Brazil | Rio de Janeiro | 5.7 | 4.9 | 1807.4721 | 1553.7918
Brazil | Brasília | 6.2 | 5.5 | 1966.0223 | 1744.052
Canada | Edmonton | 5.9 | 4.8 | 1870.8922 | 1522.0818
Canada | Montreal | 4.8 | 3.9 | 1522.0818 | 1236.6914
Canada | Saskatoon | 5.9 | 5.2 | 1870.8922 | 1648.9219
Canada | Toronto | 5.5 | 3.9 | 1744.052 | 1236.6914
Canada | Vancouver | 5.6 | 3.6 | 1775.7621 | 1141.5613
Canada | Winnipeg | 5.7 | 4.6 | 1807.4721 | 1458.6617
Canada | Yellowknife | 5.5 | 3.2 | 1744.052 | 1014.7212
Chile | Punta Arenas | 5.1 | 3.4 | 1617.2119 | 1078.1413
Chile | Santiago | 5.9 | 4 | 1870.8922 | 1268.4015
China | Baotou Neimongol | 6.3 | 5.5 | 1997.7323 | 1744.052
China | Beihai Guangxi | 4.6 | 4.2 | 1458.6617 | 1331.8216
China | Beijing | 5 | 4.3 | 1585.5019 | 1363.5316
China | Changsha Hunan | 4.8 | 3.2 | 1522.0818 | 1014.7212
China | Chengdu Sichuan | 3.4 | 2.5 | 1078.1413 | 792.7509
China | Chungking | 3.6 | 2.4 | 1141.5613 | 761.0409
China | Fuzhou Fujian | 4.9 | 3.4 | 1553.7918 | 1078.1413
China | Guangdong Tianjin | 5.9 | 5.1 | 1870.8922 | 1617.2119
China | Ganzhou Jiagxi | 4.9 | 3.7 | 1553.7918 | 1173.2714
China | Guiyang, Guizhou | 3.9 | 2.7 | 1236.6914 | 856.171
China | Haikou Hainan | 5.1 | 4.5 | 1617.2119 | 1426.9517
China | Harbin Heilongjiang | 5 | 4.3 | 1585.5019 | 1363.5316
China | Hefei Anhui | 4.3 | 3.7 | 1363.5316 | 1173.2714
China | Hong Kong | 4.9 | 4.1 | 1553.7918 | 1300.1115
China | Jilin Jilin | 5.8 | 5 | 1839.1822 | 1585.5019
China | Jinzhou Liaoning | 5.7 | 4.7 | 1807.4721 | 1490.3717
China | Kunming Yunan | 5.5 | 4.4 | 1744.052 | 1395.2416
China | Lanzhou Gansu | 5 | 4.2 | 1585.5019 | 1331.8216
China | Lhasa Tibet | 6.9 | 6.2 | 2187.9926 | 1966.0223
China | Tsingtao Shandong | 3.7 | 3.4 | 1173.2714 | 1078.1413
China | Shanghai | 4.4 | 3.6 | 1395.2416 | 1141.5613
China | Shenzhen Guangdong | 4.6 | 4 | 1458.6617 | 1268.4015
China | Shijiazhuang Hebei | 5.9 | 5 | 1870.8922 | 1585.5019
China | Suzhou Jiangsu | 4.6 | 4.1 | 1458.6617 | 1300.1115
China | Urumqi Xinjiang | 5.7 | 4.4 | 1807.4721 | 1395.2416
China | Wuhan Hubei | 4.4 | 3.3 | 1395.2416 | 1046.4312
China | Xian Shaanxi | 4.4 | 3.8 | 1395.2416 | 1204.9814
China | Xining Qinghai | 5.8 | 4.7 | 1839.1822 | 1490.3717
China | Yanchi Ningxia | 5.9 | 5.3 | 1870.8922 | 1680.632
China | Zhengzhou Henan | 5.3 | 4.2 | 1680.632 | 1331.8216
Columbia | Bogota | 5.2 | 4.3 | 1648.9219 | 1363.5316
England | Leeds | 4.1 | 2.9 | 1300.1115 | 919.5911
England | London | 4.1 | 2.8 | 1300.1115 | 887.881
Ethiopia | Addis Ababa | 5.9 | 5.1 | 1870.8922 | 1617.2119
Finland | Helsinki | 5.1 | 3.1 | 1617.2119 | 983.0112
France | Marseille | 6.4 | 4.9 | 2029.4424 | 1553.7918
France | Paris | 5 | 3.2 | 1585.5019 | 1014.7212
France | Lyon | 5.7 | 3.7 | 1807.4721 | 1173.2714
Georgia | Tbilisi | 5.5 | 4 | 1744.052 | 1268.4015
Germany | Frankfurt | 4.3 | 3.1 | 1363.5316 | 983.0112
Germany | Hamburg | 4.5 | 2.9 | 1426.9517 | 919.5911
Germany | Munich | 4.7 | 3.6 | 1490.3717 | 1141.5613
Iceland | Reykyavik | 4.1 | 2.6 | 1300.1115 | 824.461
India | Ahmadabad Gujarat | 7 | 5.9 | 2219.7026 | 1870.8922
India | Bangalore | 6.1 | 5.4 | 1934.3123 | 1712.342
India | Bhopal | 6.5 | 5.4 | 2061.1524 | 1712.342
India | Calcutta | 6.1 | 5.1 | 1934.3123 | 1617.2119
India | Chandigarh | 6.6 | 5.8 | 2092.8625 | 1839.1822
India | Delhi | 6.8 | 5.7 | 2156.2825 | 1807.4721
India | Dhera Dun Uttaranchal | 6.8 | 5.9 | 2156.2825 | 1870.8922
India | Gauhati Assam | 6.2 | 5.2 | 1966.0223 | 1648.9219
India | Goa | 6.8 | 5.7 | 2156.2825 | 1807.4721
India | Hyderabad | 6.6 | 5.2 | 2092.8625 | 1648.9219
India | Itanagar Arunchal | 4.9 | 4.3 | 1553.7918 | 1363.5316
India | Kargil Kashmir | 6.1 | 5.3 | 1934.3123 | 1680.632
India | Leh Ladakh | 6.5 | 5.6 | 2061.1524 | 1775.7621
India | Lucknow Uttar | 6.3 | 5.3 | 1997.7323 | 1680.632
India | Ludhiana Punjab | 6.6 | 5.8 | 2092.8625 | 1839.1822
India | Madras | 6.8 | 5.5 | 2156.2825 | 1744.052
India | Manali Himachal | 5.6 | 5 | 1775.7621 | 1585.5019
India | Mumbai | 6.6 | 5.4 | 2092.8625 | 1712.342
India | Patna Bihar | 6.9 | 5.6 | 2187.9926 | 1775.7621
India | Pune | 6.9 | 5.7 | 2187.9926 | 1807.4721
India | Shrinagar Kashmir | 6.4 | 4.9 | 2029.4424 | 1553.7918
Haikou Hainan | Trivandrum | 6.4 | 5.5 | 2029.4424 | 1744.052
Indonesia | Jakarta | 4.4 | 4 | 1395.2416 | 1268.4015
Indonesia | Palembang | 5 | 4.7 | 1585.5019 | 1490.3717
Iran | Shiraz | 6.7 | 5.9 | 2124.5725 | 1870.8922
Iran | Tabriz | 6.8 | 5.1 | 2156.2825 | 1617.2119
Iran | Tehran | 6.8 | 5.4 | 2156.2825 | 1712.342
Iraq | Baghdad | 6.4 | 5.5 | 2029.4424 | 1744.052
Iraq | Mosul | 5.6 | 4.4 | 1775.7621 | 1395.2416
Ireland | Dublin | 4.2 | 2.8 | 1331.8216 | 887.881
Israel | Haifa | 6.8 | 5.5 | 2156.2825 | 1744.052
Italy | Milan | 5.6 | 4.2 | 1775.7621 | 1331.8216
Italy | Palermo | 7.1 | 5.4 | 2251.4126 | 1712.342
Italy | Venice | 5.3 | 3.6 | 1680.632 | 1141.5613
Japan | Akita | 4.6 | 3.5 | 1458.6617 | 1109.8513
Japan | Nagasaki | 5.6 | 4.4 | 1775.7621 | 1395.2416
Japan | Sapporo | 4.6 | 3.8 | 1458.6617 | 1204.9814
Japan | Tokyo | 3.7 | 3.2 | 1173.2714 | 1014.7212
Japan | Yamagata | 4.6 | 3.6 | 1458.6617 | 1141.5613
Kazakhstan | Karaganda | 5.7 | 4.5 | 1807.4721 | 1426.9517
Kenya | Nairobi | 6.6 | 5.3 | 2092.8625 | 1680.632
Korea, N. | Pyongyang | 5 | 4.2 | 1585.5019 | 1331.8216
Mali | Bamako | 6.5 | 5.8 | 2061.1524 | 1839.1822
Mexico | Chihuahua | 6.9 | 6.3 | 2187.9926 | 1997.7323
Mexico | Merida | 6.2 | 5.5 | 1966.0223 | 1744.052
Mexico | Mexico City | 6.3 | 5.3 | 1997.7323 | 1680.632
Mexico | Monterey | 6.2 | 5.5 | 1966.0223 | 1744.052
Mongolia | Ulan Bator | 6 | 4.7 | 1902.6022 | 1490.3717
Morocco | Casablanca | 5.8 | 4.9 | 1839.1822 | 1553.7918
Mozambique | Maputo | 6.2 | 5.6 | 1966.0223 | 1775.7621
Myanmar | Mandalay | 6.5 | 5.4 | 2061.1524 | 1712.342
Myanmar | Yangon | 6.5 | 4.9 | 2061.1524 | 1553.7918
Nepal | Kathmandu | 6.9 | 5.8 | 2187.9926 | 1839.1822
Netherlands | Amsterdam | 4.9 | 3.2 | 1553.7918 | 1014.7212
New Zealand | Aukland | 6 | 4.5 | 1902.6022 | 1426.9517
Nicaragua | Managua | 6.8 | 5.9 | 2156.2825 | 1870.8922
Nigeria | Lagos | 5.6 | 4.8 | 1775.7621 | 1522.0818
Norway | Oslo | 4.8 | 3.3 | 1522.0818 | 1046.4312
Pakistan | Faisalabad | 6.2 | 5.5 | 1966.0223 | 1744.052
Pakistan | Gujranwala | 6.7 | 5.9 | 2124.5725 | 1870.8922
Pakistan | Hyderabad | 6.3 | 5.5 | 1997.7323 | 1744.052
Pakistan | Karachi | 6.1 | 5.7 | 1934.3123 | 1807.4721
Pakistan | Lahore | 5.8 | 5.1 | 1839.1822 | 1617.2119
Pakistan | Multan | 6 | 5.5 | 1902.6022 | 1744.052
Pakistan | Peshawar | 6.5 | 5.8 | 2061.1524 | 1839.1822
Pakistan | Quetta | 6.8 | 6 | 2156.2825 | 1902.6022
Paraguay | Asunción | 5.8 | 5.1 | 1839.1822 | 1617.2119
Peru | Lima | 7.1 | 5.4 | 2251.4126 | 1712.342
Philippines | Davao | 5.6 | 5 | 1775.7621 | 1585.5019
Poland | Warsaw | 4.7 | 2.9 | 1490.3717 | 919.5911
Russia | Grozny Chechnya | 5.3 | 4.2 | 1680.632 | 1331.8216
Russia | Moscow | 4.9 | 3.1 | 1553.7918 | 983.0112
Saudi Arabia | Jidda | 6.8 | 6.2 | 2156.2825 | 1966.0223
Scotland | Edinburgh | 4.2 | 2.9 | 1331.8216 | 919.5911
Senegal | Dakar | 6.8 | 5.8 | 2156.2825 | 1839.1822
Somalia | Mogadishu | 7.2 | 6.7 | 2283.1227 | 2124.5725
South Africa | Cape Town | 6.9 | 5.6 | 2187.9926 | 1775.7621
South Africa | Pretoria | 6.4 | 5.9 | 2029.4424 | 1870.8922
Spain | Barcelona | 6.2 | 5 | 1966.0223 | 1585.5019
Spain | Seville | 6.6 | 5.4 | 2092.8625 | 1712.342
Sweden | Linkoping | 4.8 | 3.4 | 1522.0818 | 1078.1413
Switzerland | Geneva | 5.3 | 3.6 | 1680.632 | 1141.5613
Syria | Aleppo | 6.8 | 5.2 | 2156.2825 | 1648.9219
Taiwan | Taipei | 4.6 | 3.7 | 1458.6617 | 1173.2714
Tajikistan | Dushanbe | 7.1 | 5.1 | 2251.4126 | 1617.2119
Tanzania | Dar es Salaam | 5.3 | 4.8 | 1680.632 | 1522.0818
Thailand | Bankok | 5.7 | 4.9 | 1807.4721 | 1553.7918
Tunisia | Sidi Bou Said | 6.6 | 5 | 2092.8625 | 1585.5019
Turkey | Antalya | 6.4 | 4.9 | 2029.4424 | 1553.7918
Turkey | Bursa | 6.1 | 4.3 | 1934.3123 | 1363.5316
Turkey | Istanbul | 6.6 | 4.5 | 2092.8625 | 1426.9517
Uganda | Kampala | 6.5 | 5.5 | 2061.1524 | 1744.052
Ukraine | Odessa | 5.5 | 3.7 | 1744.052 | 1173.2714
Venezuela | Caracas | 5 | 4.5 | 1585.5019 | 1426.9517
Virgin Islands | Charlotte Amalie | 7 | 6.3 | 2219.7026 | 1997.7323
Yemen | Sana'a | 5.3 | 4.6 | 1680.632 | 1458.6617

## Cost Data
Metric Units |  | English Units
Square Meters | $/m2 | Square Feet | $/ft2
9.2937 | 2445.7521 | 100 | 227.3004
18.5874 | 1951.0871 | 200 | 181.3278
46.4684 | 1447.2655 | 500 | 134.5042
92.9368 | 1154.5492 | 1000 | 107.3001
139.4052 | 1011.595 | 1500 | 94.0144
185.8736 | 921.0361 | 2000 | 85.5982
278.8104 | 806.9951 | 3000 | 74.9995